OPERATING PROCEDURE

MANUAL

Resource

Desk

- Introduction

## 1.1	Purpose

## 1.2	Scope

## 1.3	Roles/Responsibilities

- General

2.1	System Operator Responsibility and Authority

2.2	Communication

- Three-part Communication

- Hotline Call Communication

- VDIs to Master QSEs

- Monitor and Manage System Security

3.1	Compliance Monitoring

- Monitor Resource Status for Discrepancies

- Dynamically Scheduled Resource

3.2	QSE Request to Move Ancillary Services

3.3	Notifications for Diminishing Reserves

- Advisory

- Watch

3.4	Deploying Non-Spin for PRC < 2500 MW

3.5	System Failures

3.6	Responding to GTLs

- North to Houston Interface

- Rio Grande Valley Interface

3.7	Deploying Non-Spin for Local Congestion

- Decommitment Request

4.1	Approve/Reject Resource Decommitment Request

- Supplemental Ancillary Service Market

5.1	Supplemental Ancillary Service Market

- Procurement of Ancillary Services when DAM process is insufficient

- Increasing Amount of Ancillary Services for Extreme Cold Weather

- Increasing Amount of Ancillary Services for Other Reasons

- Replacement of Ancillary Service Due to Undeliverable or Failure to Provide

- Daily Reconfiguration SASM

5.2	SASM Failure/Timeline Deviation

- Failure of the SASM Software

- Timeline Deviation

- Manage Outages

6.1	Manage Resource Forced & Maintenance Outages

- Forced Outages

- Maintenance Outages

- Forced Derate

- Short-Notice Resource Outages

- Opportunity Outages

- Returning from Planned Outage Early

6.2	Forced Outage Detection

- Emergency Operation

7.1	Market Notices

- OCN

- Advisory

- Watch

- Emergency Notice

- Scripts

7.2	Implement EEA Levels

- Implement EEA Level 1

- Implement EEA Level 2

- Implement EEA Level 3

7.3	Restore EEA Levels

- Restore Firm Load

- Move from EEA Level 3 to EEA Level 2

- Move from EEA Level 2 to EEA Level 1

- Move from EEA Level 1 to EEA 0

- Recall Non-Spin and Cancel Watch

7.4	Restoration of Primary Control Center Functionality

- Communication Testing

8.1	Weekly Hotline Test

8.2	Monthly Testing of Satellite Phones

- Primary Control Center

- Alternate Control Center

- Perform Miscellaneous

9.1	Responding to Miscellaneous Issues

- Telemetry Issues that could affect SCED and/or LMPs

- Backup/Alternate Control Center Transfer

- QSE Issues

- Missing Data from MIS Postings

- Courtesy Hotline Calls for ERCOT Application Issues

- Power System Stabilizers (PSS) & Automatic Voltage Regulators (AVR)

# 1.	Introduction

## 1.1	Purpose

This procedure provides the System Operator assigned to the Resource Desk with detailed Procedures required for performing duties assigned to that position.

The Resource Desk shall monitor Ancillary Service levels to ensure QSEs are meeting their A/S obligations, execute a Supplemental Ancillary Service Market to procure additional/insufficient A/S as needed, deploy/recall A/S (Non-Spin, Load Resources providing RRS, etc.) as system conditions require or as instructed by the Shift Supervisor.  The Resource Desk Operator will also be responsible for various communication testing (Hotline, Satellite Phone, etc.), issuing market notifications and MIS postings using Notice Builder, compliance monitoring, Forced Outage Detection (Resources), monitoring and responding to telemetry issues, resolving Market Participant issues and questions, and assisting other desk Operators in the Control Room as needed.

## 1.2	Scope

The instructions contained in these procedures are limited to those required for the Resource Desk.  Instructions for other ERCOT Control Room Positions are contained in separate procedures, one for each position.  These Procedures do not imply that the duties contained herein are the only duties to be performed by this position.  The individual assigned to this position will be required to follow any other instructions and to perform any other duties as required or requested by appropriate ERCOT Supervision.  Although the steps within the procedures are numbered, the numbering is for indexing purposes and are not sequential in nature.  The system operator will determine the sequence of steps, exclude steps, or take any additional actions required to ensure system security based on the information and situational awareness available during both normal and emergency conditions.

## 1.3	Roles/Responsibilities

ERCOT System Operator, Resource Desk

The ERCOT System Operator – Resource Desk position represents the following NERC functional entities collectively for the ERCOT ISO at any time:

- Reliability Coordinator

- Balancing Authority

- Transmission Operator

- Interchange Coordinator

This representation includes the responsibility and clear decision making authority during normal and emergency conditions to direct and implement real-time actions to ensure the stable and reliable operation of the ERCOT Electric Grid.  These actions shall include shedding of firm load without obtaining approval from higher-level personnel.

# 2.	General

## 2.1	System Operator Responsibility and Authority

Procedure Purpose: To ensure the System Operators know their roles, responsibility and authority.

| Protocol Reference | 6.5.1.1 | 6.5.1.2(3) | 6.5.2 |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.5.2(1) |  |  |  |
| NERC Standard | EOP-002-3.1 R1 | IRO-001-1.1 R3 | PER-001-0 R1 | TOP-001-1 R1 |

| Version: 1 | Revision: 2 | Effective Date: May 1, 2012 |
| --- | --- | --- |

- English shall be used as the language for all communications between and among operating personnel responsible for the real-time generation control and operation of the interconnected Bulk Electric System.

The System Operator (SO) shall, in accordance with NERC Reliability Standards, have clear decision-making authority to act and to direct actions to be taken by Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities within its Reliability Coordination Area to preserve the integrity and reliability of the Bulk Electric System during both normal and emergency conditions.  These actions shall be taken without delay, but not longer than 30 minutes which may include the shedding of firm load without obtaining approval from higher-level personnel.  The ERCOT System Operator represents the following NERC functional entities collectively for the ERCOT ISO at any time:

- Reliability Coordinator.

- Balancing Authority

- Transmission Operator

- Interchange Coordinator

- The SO on duty is, in accordance with the ERCOT Protocols, Operating Guides, and NERC Reliability Standards, and acting as the Balancing Authority, Transmission Operator, Regional Reliability Coordinator, and Interchange Coordinator shall request and receive information required to continually monitor the operating conditions and request that individual Market Participants (MPs) make changes, which will assure the Security and Reliability of the ERCOT System.

- The SO issues Dispatch Instructions for the Real-Time Operation of Transmission Facilities to a TO, and to a QSE for the Real-Time Operation of a Resource.

- The SO shall, on an ERCOT-wide basis, coordinate the ERCOT System Restoration (Black Start) Plan.  The SO shall implement the Black Start Plan and shall direct the reconnection efforts of the islands, established by restoration activities.  The SO shall coordinate the mutual assistance activities of the ERCOT Participants during system restoration activities.

- The SO shall consider all equipment operating limits when issuing Dispatch Instructions except as stated in Protocol Section 6.5.9, Emergency Operations, if a Dispatch Instruction conflicts with a restriction that may be placed on equipment from time to time by a TO or a Generation Resource’s QSE to protect the integrity of equipment, ERCOT shall honor the restriction.

- The SO performs security analyses on a Day Ahead and Real-Time basis and ensures that all Forced Outages are entered into the Outage Scheduler. The SO shall obtain or arrange to provide Emergency Energy over the DC Tie(s) on behalf of ERCOT.

- The SO shall issue appropriate OCN’s, Advisories, Watches, and Emergency Notices, and coordinate the reduction or cancellation of clearances, re-dispatch of generation, and request, order, or take other action(s) that the SO determines necessary to maintain safe and reliable operating conditions on the ERCOT System in accordance with ERCOT Protocols, Operating Guides, and NERC Reliability Standards.  The SO will implement and terminate ERCOT Time Corrections, and will determine the need for and implement the operation of a Qualified Scheduling Entity (QSE) on Constant Frequency Control for loss of ERCOT’s Load Frequency Control System.

- As the Reliability Coordinator, ERCOT ISO shall comply with its Regional Reliability Plan which has been approved by the NERC Operating Committee.

The SPP DC-Tie processes, procedures, or plans that support or affect SPP shall be reviewed at least once every 3 years and updated if needed.  These would include any DC-Tie procedures, inadvertent energy procedures, and emergency procedures.

## 2.2	Communication

Procedure Purpose:  To ensure that three part communication is used for all directives and ensuring all QSEs receive Hotline calls.

| Protocol Reference | 6.5.7.8(4) | 6.5.7.8(6) |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | COM-002-2 R2 |  |  |  |

| Version: 1 | Revision: 2 | Effective Date: June 1, 2014 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ## Three-Part Communication |  |
| NERC | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall issue directives in a clear, concise, and definitive manner, shall ensure the recipient of the directive repeats the information back correctly; and shall acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| NOTE | A directive is an authoritative instruction or direction; specific order. |
| 1 | ERCOT ISO is the Reliability Coordinator, Transmission Operator, and Balancing Authority. When issuing a directive you shall use three-part communication: - Issue the directive - Receive a correct repeat back - Give an acknowledgement Failing to do any of the three parts is a NERC Reliability Standard violation. |
| 2 | Many scripts have been placed throughout these procedures as a reminder of three-part communication. However, a script cannot be provided for every scenario. Effective three-part communication skills are mandatory. |
| ## Hotline Call Communication |  |
| 1 | When making Hotline calls, verify that every QSE has answered. IF: - Not every QSE answered the Hotline; THEN: - Contact them using their OPX line or LD line to provide them with the message - Inquire why they were not on the Hotline call - Open a Help ticket if ERCOT’s Telecommunications department is needed to investigate. |
| LOG | Log all actions. |
| ## VDIs to Master QSEs |  |
| 1 | Direct VDIs to the Master QSE of a Generation Resource that has been split to function as two or more Split Generation Resources as deemed necessary by ERCOT to effectuate actions for the total Generation Resource for instances when electronic Dispatch Instructions are not feasible. |

## 3.	Monitor and Manage System Security

## 3.1	Compliance Monitoring

Procedure Purpose: To monitor QSE performance.

| Protocol Reference | 3.9(3)(4)&(5) | 3.9.1(10) | 3.9.2 (3)&(4) | 6.4.2.2(2) |
| --- | --- | --- | --- | --- |
|  | 6.4.2.5 | 6.4.5(2)(b) | 6.4.8.1(1) | 6.4.8.1.2 |
|  | 6.4.8.1.3 |  |  |  |
| Guide Reference | 2.1(1)(h) | 2.2.1(3)(c)(ii)&(iv) |  |  |
| NERC Standard | BAL-005-0-2b R2 |  |  |  |

| Version: 1 | Revision: 12 | Effective Date: August 1, 2014 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Monitor Resource Status for Discrepancies |  |
| Telemetered Status | REVIEW REFERENCE DISPLAY: Market Participation>Physical Market>Market Operator Data>Consistency Checks IF: - Discrepancy is identified between a COP and telemetered Resource Status; THEN: - Call the QSE representing Resource to determine the correct resource status and have them make the necessary correction. NOTE: It is not necessary to make calls for inconsistent telemetry/COP for quick start units. |
| LOG | Log all actions. |
| ON TEST | Review the list of “Approved Unit Tests” on the System Operations SharePoint; compare this list to the units showing a unit status of ONTEST. WHEN: - A unit with a status of ONTEST without an approved unit test exists; THEN: - Notify the QSE that they do not have an approved unit test and can not use the ONTEST status. |
| LOG | Log all actions. |
| ### Dynamically Scheduled Resource |  |
| NOTE | Each QSE may not have more than one DSR Load. |
| DSR | REVIEW REFERENCE DISPLAY: EMP Applications>Generation Area Status>Analyst Displays>Gen Monitoring Displays>Dynamic Schedules>Load Based IF: - A DSR load signal fails for any reason for > than one 15 minute Settlement Interval; THEN: - Notify the QSE and notify the Helpdesk to suspend validation of DSR Output Schedule. IF: - A DSR load signal fails for more than 10 consecutive hours; THEN: - Notify the Helpdesk to have DSR suspended until the signal is reliably restored. |
| NOTE | IF: - The signal failure is identified to be an ERCOT communication problem; THEN: - ERCOT will not suspend the QSE’s ability to use DSR. |
| LOG | Log all actions. |
| ### Monitor QSE Ancillary Service Obligations |  |
| A/S Difference in COP | REVIEW REFERENCE DISPLAY: Market Participation>Physical Market>SASM Market>AS Responsibility - QSE Market Participation>Physical Market>SASM Market>Failure To Provide At the top of each hour, notifications will be automatically sent to QSEs with shortages in their COP - Check approximately 5 minutes after each hour: IF: - A/S Difference (MW) column displays values in RED (Generation Resources with a negative value is a shortage and Load Resources with a positive value is an overage); THEN: - Verify the data was transferred to the AS Failure To Provide display - Call the QSE with a Failure MW, IF: - The QSE can not correct the deficiency within one hour; THEN: - Notify the Shift Supervisor and determine if a SASM should be opened. IF: - It is determined that a SASM should be opened; THEN: - Verify that the Notification Flag column displays a “Y” on the AS Responsibility – QSE display, and - Manually click the “Send Notification” button, this will ensure this is the most current data - Proceed to the SASM>Running a SASM for Failure To Provide Desktop Guide Resource Desk Section 2.4.2. |
| LOG | Log all actions. |
| Infeasible A/S Capacity from RUC | REVIEW REFERENCE DISPLAY: Market Participation>Physical Market>SASM Market>AS Infeasibility Market Participation>Physical Market>SASM Market> AS Replacement Check after each HRUC has been published or when RUC operator has notified you of a RUC commitment. NOTE: The infeasible hour indicates the shortage based on the system situation when HRUC runs. Therefore, it may be necessary to review at least 3 hours prior to infeasible hour to notify QSE. IF: - The Infeasible MW column is displaying MW values; THEN: - Assess the infeasible MW and hour based on the SASM timeline - Change the Notification Flag to “Y” and commit to database, - Press the “Send Notification”, - Navigate to the AS Replacement display and call the QSE with the Infeasible MW. IF: - The QSE states they cannot replace the service within two hours; THEN: - Notify the Shift Supervisor and determine if a SASM should be opened; IF: - It is determined that a SASM should be opened; THEN: - Proceed to the SASM>Running a SASM for Undeliverable Desktop Guide Resource Guide Section 2.4.1. |
| NOTE | A QSE that has one or more of its Resources RUC-committed to provide Ancillary Services must increase its Ancillary Service Supply Responsibility by the total amount of RUC-committed Ancillary Service quantities. The QSE may only use a RUC-committed Resource to meet its Ancillary Service Supply Responsibility during that Resource’s RUC-Committed Interval if the Resource has been committed by the RUC process to provide Ancillary Service. The QSE shall indicate the exact amount and type of Ancillary Service for which it was committed as the Resource’s Ancillary Service Resource Responsibility and Ancillary Services Schedule for the RUC-Committed Intervals for both telemetry and COP information provided to ERCOT. Upon deployment of the Ancillary Services, the QSE shall adjust its Ancillary Services Schedule to reflect the amounts requested in the deployment. |
| LOG | Log all actions. |

## 3.2	QSE Request to Move Ancillary Services

Procedure Purpose:  Evaluate QSE requests for moving Ancillary Services from one resource to another or through a trade with another QSE.

| Protocol Reference | 6.4.7(6) | 6.4.7(7) |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 2 | Effective Date: December 13, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - A QSE may elect to change a Resource providing Ancillary Service to an alternate Resource; however they are NOT permitted to change the quantity of each type of Ancillary Service awarded. - Movement of A/S Resource responsibility from a Resource during the Adjustment Period is accomplished by use of COP updates. - A QSE may vary the quantity of A/S Resource Responsibility on Resources without obtaining prior ERCOT approval during the time window beginning 30 seconds prior to a five-minute clock interval and ending ten seconds prior to that five minute clock interval, provided the QSE complies with its total A/S Obligation. |
| Evaluate Request | IF: - A QSE makes notification to move any type of A/S from one resource to another or through a trade with another QSE; THEN: - Log all actions. |
| Infeasible | IF: - It is determined later to be infeasible; THEN: - Notify the QSE that the A/S needs to be moved or replaced by ERCOT. |
| ERCOT Replaces at QSE Request | IF: - The QSE informs ERCOT that all or part of the A/S needs to be replaced; THEN: - Determine if the insufficient amount is significant enough to replace through SASM. - Refer to the “Replacement of A/S Due to Failure to Provide” in the SASM procedure. |

## 3.3	Notifications for Diminishing Reserves

Procedure Purpose:  Monitor the Physical Responsive Capability (PRC) for issuing advance notice of diminishing Responsive Reserve.  Steps within this procedure are intended to keep ERCOT from progressing into EEA.

| Protocol Reference | 3.17.3(2) | 6.5.7.6.2.3(1) | 6.5.9.4.1(d) | 6.5.9.4.1(e) |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.5.3.1(d) | 4.5.3.1(e) |  |  |
| NERC Standard | EOP-001-2.1b R2.1 | EOP-002-3.1 R4 | IRO-005-3-1a R1.4, R1.5 |  |

| Version: 1 | Revision: 12 | Effective Date: June 1, 2014 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - ERCOT, at management’s discretion, may issue an appeal through the public news media for voluntary energy conservation at any time. - System conditions may dictate operating beyond the scope of this procedure. The System Operator has the authority to issue and/or keep a notification in effect as he/she deems necessary. |
| ### Advisory |  |
| Issue Advisory | IF: - PRC falls < 3000 MW; THEN: - Coordinate with the Real-Time Operator, AND - Post message on MIS Public Typical MIS Posting: “ERCOT is issuing an Advisory for Physical Responsive Capability less than 3000 MW.” |
| Cancel Advisory | WHEN: - PRC > 3000 MW; THEN: - Coordinate with Real-Time Operator, AND - Cancel message on MIS Public. |
| Log | Log all actions. |
| ### Watch |  |
| Issue Watch | IF: - PRC falls < 2500 MW; THEN: - Coordinate with the Real-Time Operator, - Deploy Off-Line Non-Spin, AND - Post message on MIS Public Typical MIS Posting: “ERCOT is issuing a Watch for Physical Responsive Capability less than 2500 MW”. |
| Cancel Watch | WHEN: - PRC > 2800 MW; THEN: - Coordinate with Real-Time Operator, - Recall Off-Line Non-Spin, AND - Cancel message on MIS Public. |
| Log | Log all actions. |

## 3.4	Deploying Non-Spin for PRC < 2500 MW

Procedure Purpose:  Deployment/recall of Non-Spin Reserve Service for PRC < 2500 MW as requested by the Real-Time Operator.

| Protocol Reference | 6.5.7.6.2.2(13) | 6.5.7.6.2.3 |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.5.3.1(d) |  |  |  |
| NERC Standard | EOP-002-3.1 R2, R4 |  |  |  |

| Version: 1 | Revision: 16 | Effective Date: December 15, 2014 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Deployment | WHEN: - Notified by the Real-Time Operator to deploy Non-Spin; THEN: - Coordinate with the Transmission Operator to verify the Non-Spin does not create congestion, - Deploy Non-Spin, (Refer to Desktop Guide Resource Desk Section 2.1.1) - Post message on MIS Public Typical MIS Posting: “At [x:xx] approximately [xx] MW of Non-Spin has been deployed, anticipated duration is [xx].” |
| Additional Deployment | IF: - Additional Non-Spin becomes available going into next hour; THEN: - Determine if the additional Non-Spin is needed, - Deploy if needed (Refer to Desktop Guide Resource Desk Section 2.1.1) |
| Commit | IF: - Notified by a QSE that their Off-line Non-Spin obligation has ended, AND - PRC < 2500 MW; THEN: - Request that the Resource stay On-line, - Issue an electronic VDI (see Desktop Guide Common to Multiple Desks Section 2.3) - Choose Resource tab - Choose Commit as the Instruction Type - State Capacity in Other Information - Confirm with Market Participant electronic VDI received. When issuing a VDI or when confirming the receipt of an Electronic VDI ensure the use of three-part communication: - Issue the directive - Receive a correct repeat back - Give an acknowledgement |
| NOTE | If Non-Spin is deployed from one operating day to the next operating day, new deployments will need to be sent for the new day. |
| Termination | WHEN: - Notified by the Real-Time Operator that the Non-Spin is no longer needed; THEN: - Recall as instructed (Refer to Desktop Guide Resource Desk Section 2.1.4) - Post message on MIS Public Typical MIS Posting: - “At [x:xx], All Non-Spin has been recalled.” |
| Log | Log all actions. |

## 3.5	System Failures

Procedure Purpose: To ensure Market Participants are notified via MIS Public using Notice Builder of any SCED/RLC/LFC (AGC) failures.

| Protocol Reference | 6.5.9.2(2) | 6.5.9.3.3(2)(g) |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 7 | Effective Date: April 4, 2014 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| 1 | WHEN: - Notified by the Real-Time Operator of a SCED/RLC/LFC(AGC) failure; THEN: - Post the appropriate message on MIS Public - WATCH for SCED failure - Emergency Notice if both MMS and EMS have failed Typical MIS posting: “ERCOT has issued an [Watch or Emergency Notice] due to the failure of [SCED/RLC Failure], and/or [LFC].” |
| 2 | WHEN: - Notified by the Real-Time Operator that SCED/RLC/LFC(AGC) has been restored; THEN: - Cancel message on MIS Public |
| Log | Log all actions. |

## 3.6	Responding to GTLs

Procedure Purpose:  Deployment/Termination of Non-Spin Reserve Service and/or Load Resources for Congestion Management as requested by the Transmission Operator.

| Protocol Reference | 6.5.7.6.2.3(10) |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | TOP-004-2 R1, R2, R6 | TOP-007-0 R3 | TOP-008-1 R1, R2 |  |

| Version: 1 | Revision: 12 | Effective Date: December 15, 2014 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ## North to Houston Interface |  |
| Deploy Non-Spin | WHEN: - Notified by the Transmission Operator to deploy Non-Spin in the Houston area for the North-Houston Interface; THEN: - Deploy Non-Spin in the Houston area (Coast Weather Zone WZ_COAST) (Refer to Desktop Guide Resource Desk Section 2.1.3) |
| NOTE | To the extent that ERCOT deploys a Load Resource that has chosen a block deployment option, ERCOT shall either deploy the entire offer or, if only partial deployment is possible, skip the offer by the Load Resource with the block deployment option and proceed to deploy the next available Resource. |
| NOTE | If Non-Spin is deployed from one operating day to the next operating day, new deployments will need to be sent for the new day. |
| Deploy Load Resources | WHEN: - Notified by the Transmission Operator to deploy Load Resources in the Houston area for the North-Houston Interface; THEN: - Deploy Load Resources in the Houston area (Coast Weather Zone WZ_COAST) by XML (Refer to Desktop Guide Resource Desk Section 2.2.2). |
| Recall Load Resources | WHEN: - Notified by the Transmission Operator to recall Load Resources in the Houston area for the North-Houston Interface; THEN: - Recall Load Resources in the Houston area (Coast Weather Zone WZ_COAST) by sending a Zero MW XML (Refer to Desktop Guide Resource Desk Section 2.2.4). |
| Recall Non-Spin | WHEN: - Notified by the Transmission Operator to recall Non-Spin in the Houston area for the North-Houston Interface; THEN: - Recall Non-Spin in the Houston area (Coast Weather Zone WZ_COAST) by sending a Zero MW XML, (Refer to Desktop Guide Resource Desk Section 2.1.4). |
| ## Rio Grande Valley Interface |  |
| Deploy Load Resources | WHEN: - Notified by the Transmission Operator to deploy Load Resources in the Rio Grande Valley; THEN: - Deploy Load Resources (Refer to Desktop Guide Resource Desk Section 2.2.3). |
| Recall Load Resources | WHEN: - Notified by the Transmission Operator to recall Load Resources in the Rio Grande Valley; THEN: - Recall Load Resources in the Rio Grande Valley (Refer to Desktop Guide Resource Desk Section 2.2.4). |
| Log | Log all actions. |

## 3.7	Deploying Non-Spin for Local Congestion

Procedure Purpose:  Mitigating local congestion.

| Protocol Reference | 6.5.7.6.2.3(1) |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 10 | Effective Date: August 1, 2014 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| 1 | IF: - Notified by the ERCOT Transmission and Security operator that specific Resources carrying Non-Spin are needed for local congestion; THEN: - Deploy specific Resources |
| NOTE | If Non-Spin is deployed from one operating day to the next operating day, new deployments will need to be sent for the new day. |
| 2 | IF: - The Non-Spin obligation ends for the Resource deployed, AND - The Resource is still needed; THEN: - Issue an electronic VDI (see Desktop Guide Common to Multiple Desks Section 2.3) - Choose Resource tab - Choose Commit as the Instruction Type - State Local Congestion in Other Information - Confirm with Market Participant electronic VDI received. When issuing a VDI or when confirming the receipt of an Electronic VDI ensure the use of three-part communication: - Issue the directive - Receive a correct repeat back - Give an acknowledgement |
| 3 | IF: - An additional Resource is needed to be deployed; THEN: - The previous Resource deployed will need to be deployed again, along with the additional Resource. |
| Termination | IF: - Notified by the ERCOT Transmission and Security Operator that Non-Spin is no longer needed; THEN: - Recall the Non-Spin, by sending a Zero MW XML (Refer to Desktop Guide Resource Desk Section 2.1.4). |
| LOG | Log all actions. |

4.	Decommitment Request

## 4.1	Approve/Reject Resource Decommitment Request

Procedure Purpose:  Review and approve / reject Resource decommitments in the Operating Period (two-hour period comprised of the Operating Hour and the clock hour preceding the Operating Hour).  A QSE may verbally request to decommit a Resource provided the Resource has not been RUC-Committed and the Resource has no manual overrides for interval being requested.  ERCOT shall review the requests in order of receipt.

| Protocol Reference | 3.8.3.1 | 6.4.7 | 6.4.7.1 |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | TOP-002-2a R5, R7, R11 |  |  |  |

| Version: 1 | Revision: 14 | Effective Date: December 15, 2014 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Approve/Reject Decommitment QSE Requests in Operating Period |  |
| Exceptions | No request necessary for: - Combined Cycle Train (CCT) transitioning from one configuration to another - Quick Start Generation Resources (QSGR’s) |
| 1 | IF: - A QSE requests to decommit a Resource that has been Self-Committed; THEN: - Verify with the Transmission and Security Operator that the decommitment will not adversely impact current transmission conditions - If it does, deny the request - Verify that if the Resource comes Off-Line, PRC will not drop below 2500 MW - If it will, deny the request. - If no PRC issue, grant the approval |
| Log | Log all actions. |

## 5.	Supplemental Ancillary Service Market

## 5.1	Supplemental Ancillary Service Market

Procedure Purpose:  To open and execute a Supplemental Ancillary Service Market (SASM) for A/S when the DAM process is insufficient, when increasing A/S above DAM requirement, when there is infeasiblity (stranded) caused by congestion, or failure to provide by the QSE.

| Protocol Reference | 3.16 | 5.2.2.2 | 6.4.9.1 | 6.4.9.1.1 |
| --- | --- | --- | --- | --- |
|  | 6.4.9.1.2 | 6.4.9.1.3 | 6.4.9.2 | 6.5.7.5(2) |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 18 | Effective Date: December 22, 2014 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - There is no definitive time by which a SASM needs to start, however the SASM process must be completed at least one hour before the start of the Operating Hour (Example: for A/S needed in HE 14, SASM must be completed by HE 12). The SASM timeline depends on the triggering of the event. - ERCOT may not buy more of one A/S in place of the quantity of a different service. - A QSE may not self-arrange for A/S procured in response to Emergency Conditions. - See Desktop Guide Common to Multiple Desks Section 2.16 if the savecase function fails when running a SASM |
| ### Procurement of Ancillary Services when DAM process is insufficient |  |
| Procurement Timeline | If the Day-Ahead Market is aborted the ancillary services have to be procured through SASM. The SASM must be executed in the Adjustment Period for the next day (which starts at 1800). ERCOT shall allow at least 1 hour between the issuance of the Watch and the beginning of this SASM. The SASM timeline is as follows Time X = Notify QSEs of time the SASM will begin Time X + 30min = Determine amount of A/S to be procured Time X + 35min = Execute SASM Time X + 45min = Notify QSEs with awards Time X + 60min = Validate COPs for A/S Resource Responsibility |
| 1 | IF: - The Day-Ahead Market is aborted; THEN: - Verify that the RUC Operator has issued a Watch, - Procure adequate Ancillary Services for the next operating day through a SASM, (Refer to Desktop Guide Resource Desk Section 2.4.4) |
| 2 | IF: - SASM did not procure the amount of A/S requested; THEN: - Notify the Shift Supervisor of the remaining A/S insufficiencies to be procured through RUC if necessary. |
| 3 | Prepare email with the following information: - SASM ID (use YYYYMMDDHHMMSS format) - Delivery Date - Delivery Hour - QSE and Resource name (if known) you are replacing the AS for - AS type(s) - MW amounts you are replacing - Total MW amount SASM has awarded - Verify PVT transferred |
| 4 | Send information in an email to the following distribution list: - SASM |
| ### Increasing Ancillary Services for Extreme Cold Weather |  |
| NOTE | When temperatures or wind chill is expected to be below freezing for sustained periods and may impact load levels or generation availability, it may be necessary to procure additional Non-Spin and/or RRS. After DRUC has completed, determined if sufficient reserves are available to meet peak demand. |
| Guideline | OPSMON: 11 COP vs MTLF Procure additional Non-Spin and/or RRS through a SASM when “SS_HSL_MARGIN” is below the guideline below: Guideline of additional Non-Spin and/or RRS through SASM: - When wind chill is expected to be below freezing, a minimum of 600 MW is required for those hours, OR - When wind chill is expected to be below 20°F, a minimum of 1300 MW is required for those hours. This can be a combination of Non-Spin or RRS. |
| A/S Plan Increase Timeline | Time X is greater than two hours from the start of the Operating Hour for which the additional A/S capacity is required. The timeline is as follows: Time X = Notify QSEs and allow 30 min for QSEs to update AS Offers Time X + 30 min = Close SASM Time X + 35 min= Execute the SASM Time X + 45 min = Publish results Time X + 60 min = Validate COPs and A/S schedules |
| 1 | IF: - More Ancillary Services are needed for one or more Operating Hours than were provided in the Day-Ahead; THEN: - Issue a Watch by making a Hotline to QSEs - Post message on MIS Secure - Notify Transmission Operator to make Hotline call to TOs - Procure more Ancillary Services through a SASM (Refer to Desktop Guide Resource Desk Section 2.4.3). Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name], at [xx:xx] ERCOT is issuing a Watch due to the need to increase the system wide Ancillary Services requirement above what was procured in the Day-Ahead Market due to the anticipation of extreme cold weather. At [xx:xx] ERCOT will open a SASM to procure [A/S type(s)] for hours [hours] for operating day [day]. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| 2 | IF: - SASM did not procure the amount of A/S requested; THEN: - Notify the Shift Supervisor of the remaining insufficiencies to be procured through RUC if necessary. |
| 3 | Prepare email with the following information: - SASM ID (use YYYYMMDDHHMMSS format) - Delivery Date - Delivery Hour - QSE and Resource name (if known) you are replacing the AS for - AS type(s) - MW amounts you are replacing - Total MW amount SASM has awarded - Verify PVT transferred |
| 4 | Send information in an email to the following distribution list: - SASM |
| 5 | ONCE: - Ancillary Service has been procured; THEN: - Cancel the Watch by making Hotline call to QSEs - Cancel MIS posting - Notify Transmission Operator to make Hotline call to TOs Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. ERCOT is canceling the Watch for increasing Ancillary Services, SASM has completed. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| LOG | Log all actions. |
| ### Increasing Ancillary Services for other reasons |  |
| A/S Plan Increase Timeline | Time X is greater than two hours from the start of the Operating Hour for which the additional A/S capacity is required. The timeline is as follows: Time X = Notify QSEs and allow 30 min for QSEs to update AS Offers Time X + 30 min = Close SASM Time X + 35min= Execute the SASM Time X + 45min = Publish results Time X + 60min = Validate COPs and A/S schedules |
| 1 | IF: - More Ancillary Services are needed for one or more Operating Hours than were provided in the Day-Ahead; THEN: - Issue a Watch by making a Hotline to QSEs - Post message on MIS Secure - Notify Transmission Operator to make Hotline call to TOs - Procure more Ancillary Services through a SASM (Refer to Desktop Guide Resource Desk Section 2.4.3). Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name], at [xx:xx] ERCOT is issuing a Watch due to the need to increase the system wide Ancillary Services requirement above what was procured in the Day-Ahead Market due to [state the reason]. At [xx:xx] ERCOT will open a SASM to procure the additional [type of A/S] Ancillary Services for hours [hours] for operating day [day]. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| 2 | IF: - SASM did not procure the amount of A/S requested; THEN: - Notify the Shift Supervisor of the remaining A/S insufficiencies to be procured through RUC if necessary. |
| 3 | Prepare email with the following information: - SASM ID (use YYYYMMDDHHMMSS format) - Delivery Date - Delivery Hour - QSE and Resource name (if known) you are replacing the AS for - AS type(s) - MW amounts you are replacing - Total MW amount SASM has awarded - Verify PVT transferred |
| 4 | Send information in an email to the following distribution list: - SASM |
| 5 | ONCE: - Ancillary Service has been procured; THEN: - Cancel the Watch by making Hotline call to QSEs - Cancel MIS posting - Notify Transmission Operator to make Hotline call to TOs Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. ERCOT is canceling the Watch for increasing the system wide A/S requirement. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| ### Replacement of Ancillary Service Due to Infeasibility or Failure to Provide |  |
| NOTE | - Undeliverable/Infeasibility is when a QSE can not provide their A/S because ERCOT has asked them to move it due to congestion - Failure to provide is all other reasons |
| Undeliverable /Insufficient A/S Timeline | If the SASM is being executed to replace A/S capacity, either due to transmission constraints or QSE failure-to-provide, the timeline is as follows: Time X = Determine type and amount of A/S to procure. Notify QSEs Time X + 30min = Execute SASM (and Price Run/Sensitivity Analysis if needed) Time X + 45min = Notify QSEs with awards Time X + 60min = Validate COPs and A/S schedules |
| NOTE | For A/S that is Infeasible, a QSE has two (2) hours to notify ERCOT: - It will be substituted on another Resource - They will replace the A/S through a trade with another QSE - All or Part of the A/S needs to be replaced For an A/S shortage that is due to Failure to Provide, a QSE must notify ERCOT within an acceptable timeframe, but no longer than two (2) hours: - It will be substituted on another Resource, - They will replace the A/S through a trade with another QSE - The A/S needs to be replaced |
| 1 | IF: - A QSE is unable to provide the A/S capacity allocated to a specific Resource; THEN: - Determine if the infeasible/insufficient amount is significant enough to replace through SASM IF: - It is determined that a SASM should be run, - Post on MIS Public, using Notice Builder under operational information, low priority, to provide notice that a SASM will begin in 30 minutes; Typical Posting: “ERCOT will execute a SASM at [xx:xx] for operating day [xx/xx/xx] for HE [xx-xx] for [type of A/S] MW [X], [X], [X]”. THEN: - Execute SASM (Refer to Desktop Guide Resource Desk Section 2.4.1 or 2.4.2). |
| 2 | IF: - SASM did not procure the amount of A/S requested; THEN: - Notify the Shift Supervisor of the remaining A/S insufficiencies. |
| 3 | IF: - A QSE is unable to provide their SASM awards; THEN: - Determine if there is time to open an additional SASM, AND - Send failure to provide notification. |
| 4 | Cancel posting on MIS |
| 5 | Prepare email with the following information: - SASM ID (use YYYYMMDDHHMMSS format) - Delivery Date - Delivery Hour - QSE and Resource name (if known) you are replacing the AS for - AS type(s) - MW amounts you are replacing - Total MW amount SASM has awarded - Verify PVT transferred |
| 6 | Send information in an email to the following distribution list: - SASM |
| ### Daily Reconfiguration SASM |  |
| Daily SASM Timeline | (Refer to Desktop Guide Resource Desk Section 2.4.7) Reconfiguration Supplemental Ancillary Service Market (SASM) allows QSEs to modify their Ancillary Services (AS) during the Operating Day. Reconfiguration SASMs are expected to be run daily for Operating Hours HE 13 thru 24.) The timeline is as follows: Time 08:45 = Determine type and amount of A/S to procure. Time 09:00 = Execute SASM (and Price Run/Sensitivity Analysis if needed) Time 09:15 = Notify QSEs with awards Time 09:30 = Validate COPs and A/S schedules |
| 1 | QSEs must have valid AS Offers of an amount equal to or greater than the requested reconfiguration amount; IF: - There are not sufficient AS Offers to cover the total requested amount; THEN: - Do not publish the SASM, - Post an Operational Information message, low priority, on MIS Public - Send email to SASM distribution list - QSEs will retain their original AS Supply Responsibility and should update their COPs accordingly Typical MIS Posting: The Daily Reconfiguration SASM will not be occurring due to insufficient AS Offers. |
| 2 | IF: - There are NO participating QSEs in the reconfiguration SASM process; THEN: - Do not proceed with SASM process - Post an Operational Information, low priority, message on MIS Public - Send email to SASM distribution list Typical MIS Posting: The Daily Reconfiguration SASM will not be occurring due to zero participating QSEs. |
| 3 | IF: - There ARE participating QSEs in the reconfiguration SASM THEN: - Proceed with the reconfiguration SASM - Prepare email with the following information: - SASM ID (use YYYYMMDDHHMMSS format) - Delivery Date - Delivery Hour - QSE - AS type(s) - MW amounts you are replacing - Total MW amount SASM has awarded - Verify PVT transferred |
| 4 | Send information in an email to the following distribution list: - SASM |
| LOG | Log all actions. |

## 5.2	SASM Failure/Timeline Deviation

Procedure Purpose:  To manage SASM software failure or timeline deviation.

| Protocol Reference | 6.5.9.3.3(2)(e) |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 6 | Effective Date: June 1, 2014 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Failure of the SASM Software |  |
| 1 | IF: - The SASM workflow controller fails during any stage of the run; THEN: - Press the Abort button to cancel the current run, - Press the Shut Down button, - Press the Start Up button, - Press the Run All button to restart the sequence. |
| 2 | IF: - The SASM workflow controller continues to fail; NOTIFY: - Notify the appropriate ERCOT personnel. |
| ### Timeline Deviations |  |
| NOTE | - There is no definitive time by which a SASM needs to start, however the SASM process must be completed at least one hour before the start of the Operating Hour (Example: for A/S needed in HE 14, SASM must be completed by HE 12). The SASM timeline depends on the triggering of the event. - SASM process from notifying QSEs to the COP update is approximately 1 hour 30 minutes for an A/S plan increase. For replacement due to undeliverable/insufficient A/S, the timeline is 1 hour. |
| A/S Plan Increase Timeline | Time X = Notify QSEs and allow 30 min for QSEs to update AS Offers Time X + 30min = Open SASM market Time X + 60min = Verify SASM market has closed Time X + 65min = Execute SASM (and Price Run/Sensitivity Analysis if needed) Time X + 75min = Notify QSEs with awards Time X + 90min = Validate COPs and A/S schedules |
| 1 | IF: - SASM Workflow Controller fails or needs to be restarted and cannot meet the timelines above; THEN: - Using the Hotline, notify the Market Participants that the SASM will be delayed. - Notify the Help Desk and appropriate support personnel. Typical Hotline Script: “This is ERCOT Operator [first and last name]. ERCOT is making notification that SASM has not met its timeline. ERCOT will manually commit A/S as needed. Any questions”? |

# 6.	Managing Outages

## 6.1	Manage Resource Forced & Maintenance Outages

Procedure Purpose:  Monitor and respond to Resource Forced and Maintenance outages.

| Protocol Reference | 2.1 | 3.1.1(2)(j) | 3.1.4.2 | 3.1.4.4 |
| --- | --- | --- | --- | --- |
|  | 3.1.4.5 | 3.1.4.6 | 3.1.4.7 | 3.1.6.4(4) |
|  | 3.1.6.7 | 3.1.6.9 | 3.1.6.10 | 3.1.6.11 |
|  | 6.4.7 |  |  |  |
| Guide Reference | 2.4 |  |  |  |
| NERC Standard | TOP-002-2 R6 |  |  |  |

| Version: 1 | Revision: 6 | Effective Date: August 1, 2014 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Forced Outages |  |
| NOTE | The QSE should: - Immediately notify ERCOT of a forced outage, - Enter the forced outage in the Outage Scheduler within two hours, - Update their COP within 1 hour - Update their telemetry. A call to the QSE may be necessary if the above are not complete within the designated time frame. |
| NOTE | ERCOT Operators can only make the following changes in the Outage Scheduler: - Remove actual start/end time if it is within 2 hours of the time the MP entered the outage, - Change status, - Add notes If a MP needs assistance or is unable to enter their outages, direct them to Outage Coordination. Outage Coordination has an “Impersonation” certification that will allow them to make the needed changes. |
| ### Maintenance Outages |  |
| Definition | - Level 1- Equipment that must be removed from service within 24 hours to prevent a potential Forced Outage; - Level 2 - Equipment that must be removed from service within 7 days to prevent a potential Forced Outage; and - Level 3 - Equipment that must be removed from service within 30 days to prevent a potential Forced Outage. |
| Maintenance Outage with start time ≤ 24 Hours | IF: - A Maintenance Outage is received, review the outage if the scheduled start time is within the next 24 hours; THEN: - Discuss with the Transmission and Security Operator to determine if the outage will cause any reliability issues. |
| Accept Maintenance Outage with start time ≤ 24 Hours | IF: - No reliability issues identified; THEN: - Accept the Maintenance Outage. |
| Coordinate Maintenance Outage with start time ≤ 24 Hours | IF: - Reliability issues exist; THEN: - Coordinate the start of the outage with the QSE to ensure system reliability as long as the outage is allowed to start within 24 hours, AND - Accept the Maintenance Outage. |
| Coordinate Maintenance Level 2 and 3 Outage ≤ 24 Hours | REQUEST: - Support from the Transmission Desk or Shift Supervisor, IF: - Maintenance Level 2 and 3 outages are received with a start time of less than the next 24 hours, AND - Reliability issues exist; THEN: - Coordinate the start of the outage with the QSE to ensure system reliability as long as the outage is within the allowed Maintenance Level 2 (7 Days) and 3 (30 Days) outage criteria, - ERCOT Outage Coordination group may help coordinate a new start time. IF: - Reliability issues continue; THEN: - REQUEST the Operations Support Engineer investigate the development of a MP or TOAP (see section 4.6 Mitigation Plan) located in the Transmission Desk Procedure, - Accept the Maintenance Outage after coordination. |
| Maintenance Level 2 and 3 Outages | IF: - Maintenance Level 2 and 3 outages are received with a start time of greater than the next 24 hours; THEN: - The ERCOT Outage Coordination group has a process to review all Maintenance Level 2 and 3 outages without further action. |
| Log | Log all actions. |
| ### Forced Derate |  |
|  | IF: - A Resource’s capability is reduced by 10 MW or 5% of its Seasonal net max sustainable rating and is expected to last more than 48 hours; THEN: - The QSE must do the following: - Enter the derating into the Outage Scheduler as a Forced Outage, - Replace AS responsibility if applicable - Update their COP to reflect the changes, - Update the necessary telemetered parameters for the Resource. |
| ### Short-Noticed Resource Outages |  |
|  | IF: - A newly proposed Resource Outage or proposed changes to a Planned Outage is submitted three days or less from the outage start date; THEN: - Notify Outage Coordination Group. |
| ### Opportunity Outages |  |
| NOTE | Opportunity Outages for Resources are a special category of Planned Outages that may be approved by ERCOT when a specific Resource has been forced Off-Line due to a Forced Outage and the Resource has been previously accepted for a Planned Outage during the next eight days. The QSE must give as much notice as practicable to ERCOT. |
| 1 | WHEN: - A Forced Outage occurs on a Resource that has an accepted or approved Outage scheduled within the following eight days, AND IF: - Approved by ERCOT; THEN: - The Resource may remain Off-Line and start the accepted or approved Outage earlier than scheduled. IF: - Reliability issues exist; THEN: - Reject the outage to ensure system reliability, IF: - No issues identified; THEN: - Approve the Outage as received, - Notify the QSE and Outage Coordination Group. |
| ### Returning from Planned Outage Early |  |
| Verify | IF: - A Resource returns from a Planned Outage early; THEN: - Coordinate with the Transmission and RUC Operators to determine if there is an associated transmission outage or any reliability issues exist. |
| Approve | IF: - No issues identified; THEN: - Notify the QSE of approval and to update their COP and Telemetry, - Notify the Outage Coordination Group. |
| Deny | IF: - Reliability issues, OR - Transmission is not available; THEN: - Coordinate between the TO and QSE to schedule a time agreeable to both parties for all facilities to be restored to service, - Notify the QSE within two hours, - Issue a VDI to stay Off-Line (see Desktop Guide Common to Multiple Desks Section 2.3) - Choose “Can Not Return Early From Outage” as the Instruction Type from Resource level. - Confirm with Market Participant electronic VDI received. When issuing a VDI or when confirming the receipt of an Electronic VDI ensure the use of three-part communication: - Issue the directive - Receive a correct repeat back - Give an acknowledgement |
| Log | Log all actions. |

## 6.2	Forced Outage Detection

Procedure Purpose:  To detect forced outages of Resources

| Protocol Reference | 6.4.7 | 6.5.7.1.6 |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | TOP-006-2 R1 |  |  |  |

| Version: 1 | Revision: 2 | Effective Date: December 15, 2014 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Resource Outages |  |
| NOTE | Work in conjunction with the appropriate desks in the Control Room for notification. |
| NOTE | Be aware that Resource outages detected in FOD will be based on the station model. If the breaker is between the generator and step-up transformer, FOD will display this as a unit (UN). If the breaker is on the “HIGH” side of the step-up transformer, FOD will display this as a transformer (XMR) and associated breakers (CB). Be sure to look at all forced outages on transformers to determine if it is actually a generator trip. |
| 1 | IF FOD identifies a Resource Outage: The QSE should: - Immediately notify ERCOT of a forced outage, - Enter the forced outage in the Outage Scheduler within two hours, - Update their COP within 1 hour - Update their telemetry. A call to the QSE may be necessary if the above are not complete within the designated time frame. |
| 2 | FOD can be used to detect telemetry oscillations. Monitor the “OTs” column; this represents the number of times the Resource has been outaged in a 24 hour period. IF: - An unusually high value is detected; THEN: - Discuss with Real-Time Operator and contact the QSE to correct the issue. |
| Log | Log all actions. |

# 7.	Emergency Operation

## 7.1	Market Notices

Procedure Purpose:  Guidelines for issuing Emergency Conditions and the four possible levels: Operating Condition Notices (OCN), Advisories, Watches, and Emergency Notices.

| Protocol Reference | 6.3.2(3)(a)(i)(ii) | 6.3.3 | 6.5.9.2(1) | 6.5.9.3 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.3.1 | 6.5.9.3.2 | 6.5.9.3.3 | 6.5.9.3.4 |
| Guide Reference | 4.2.1 | 4.2.2 | 4.2.3 | 4.2.4 |
| NERC Standard | COM-002-2 R2 | EOP-001-2.1b R3.1 |  |  |

| Version: 1 | Revision: 16 | Effective Date: October 1, 2014 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### OCN |  |
| NOTE | Consider the severity of the potential Emergency Condition. The severity of the Emergency Condition could be limited to an isolated local area, or the condition might cover large areas affecting several entities, or the condition might be an ERCOT-wide condition potentially affecting the entire ERCOT System. |
| 1 | As directed by the Shift Supervisor or when appropriate, issue an Operating Condition Notice (OCN). The OCN can be issued for any of the following reasons or to obtain additional information from Market Participants. - There is a projected reserve capacity shortage that could affect reliability and may require more Resources - When extreme cold weather is forecasted approximately 5 days away - When extreme hot weather is forecasted approximately 5 days away - When an approaching Hurricane / Tropical Storm is approximately 5 days away - Unplanned transmission Outages that may impact reliability - When adverse weather conditions are expected, ERCOT may confer with TOs and QSEs regarding the potential for adverse reliability impacts and contingency preparedness |
| ### Advisory |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue an Advisory. The Advisory can be issued for any of the following reasons or to obtain additional information from Market Participants. - When an approaching Hurricane / Tropical Storm is approximately 3 days away - When extreme cold weather is forecasted approximately 3 days away - When extreme hot weather is forecasted approximately 1 to 3 days away - When conditions are developing or have changed and more Ancillary Services will be needed to maintain current or near-term reliability - ERCOT may exercise its authority to increase Ancillary Service requirements above the quantities originally specified in the Day-Ahead Market in accordance with ERCOT procedures - When extreme weather or conditions require more lead-time than the normal Day-Ahead Market allows - Transmission system conditions are such that operations within security criteria are not likely or possible because of Forced Outages or other conditions unless a CMP exists - Loss of communications or control condition is anticipated or significantly limited - ERCOT may require information from QSEs representing Resources regarding the Resources’ fuel capabilities. Requests for this type of information shall be for a time period of no more than seven days from the date of the request |
| ### Watch |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue a Watch. The Watch can be issued for any of the following reasons or to obtain additional information from Market Participants. - A projected reserve capacity shortage is projected with no market solution available that could affect reliability - When an approaching Hurricane / Tropical Storm is approximately 1 day away - When extreme cold weather is projected for next day or current day - When extreme hot weather is projected for next day or current day - Conditions have developed such that additional Ancillary Services are needed in the Operating Period - Insufficient Ancillary Services or Energy Offers in the DAM - Market-based congestion management techniques embedded in SCED will not be adequate to resolve transmission security violations - Forced Outages or other abnormal operating conditions have occurred, or may occur that require operations with active violations of security criteria as defined in the Operating Guides unless a CMP exists - The SCED process fails to reach a solution, whether or not ERCOT is using one of the measures in Failure of the SCED Process. - The need to immediately procure Ancillary Services from existing offers - ERCOT may instruct TOs to reconfigure transmission elements as necessary to improve the reliability of the system |
| ### Emergency Notice |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue an Emergency Notice. The Emergency Notice can be issued for any of the following reasons or to obtain additional information from Market Participants. - Loss of Primary Control Center functionality - Load Resource deployment for North-Houston voltage stability - ERCOT cannot maintain minimum reliability standards (for reasons including fuel shortages) during the Operating Period using every Resource practically obtainable from the market - Immediate action cannot be taken to avoid or relive a Transmission Element operating above its Emergency Rating - ERCOT forecasts an inability to meet applicable reliability standards and it has exercised all other reasonable options - A transmission condition has been identified that requires emergency energy from any of the DC-Ties or curtailment of schedules - The Transmission Grid is such that a violation of security criteria as defined in the Operating Guides presents the threat of uncontrolled separation or cascading outages, large-scale service disruption to Load (other than Load being served from a radial transmission line) and/or overload of Transmission Elements, and no timely solution is obtainable through SCED or CMPs - When extreme cold weather is beginning to have an adverse impact on the System - When extreme hot weather is beginning to have an adverse impact on the System - When Hurricane / Tropical Storm is in the ERCOT Region and is beginning to have an adverse impact on the System |
| ### Scripts |  |
| Hotline | Hotline calls are usually made by Real-Time Operator, the scripts below are for reference if needed: Notify QSEs of Notice: Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing a [state Notice type] for [state reason]. [QSE] please repeat this back to me. That is correct, thank you.” Notify Transmission Operator to make Hotline call to TOs: Typical script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing a [state Notice type] for [state reason]. [TO] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| Post | - All notices must be posted on MIS Public - For “free form” messages, the “Notice priority” will be specified as follows: - Operational Information/OCN type messages – low priority - Advisory/Watch type messages – medium priority - Emergency type messages – high priority |
| Hotline Cancellation | Typical Hotline Script cancellation: “This call requires everyone to remain on the line until it is complete. [QSE/TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is cancelling the [state Notice type] for [state reason]. [QSE/TO] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| Log | Log all actions. |

## 7.2	Implement EEA Levels

Procedure Purpose:  To provide for maximum possible continuity of service while maintaining the integrity of the ERCOT system to reduce the chance of cascading outages.

| Protocol Reference | 6.5.7.6.2.2(1)(b) & (13) | 6.5.9.4 | 6.5.9.4.2 |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.5.3 | 4.5.3.1 | 4.5.3.2 | 4.5.3.3 |
|  | 4.5.3.4 |  |  |  |
| NERC Standard | COM-002-2 R2 | EOP-001-2.1b R2.1, R2.3, R3.1, R3.2, R4 | EOP-002-3.1 R1, R2, R4, R7 | EOP-003-2 R1, R5 |

| Version: 1 | Revision: 14 | Effective Date: August 1, 2014 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - IF frequency falls below 59.8 Hz, ERCOT CAN immediately implement EEA 3. - IF frequency falls below 59.5 Hz, ERCOT SHALL immediately implement EEA 3. |
| ERS-30 | ERS with a thirty-minute ramp period. |
| ERS-10 | ERS with a ten-minute ramp period. |
| WS-ERS | Weather Sensitive ERS are only available June – September during Business Hour 2 (BH2) and Business Hour 3 (BH3) and only on business days. |
| TCEQ | When increased generation is requested during EEA events, Texas Commission on Environmental Quality (TCEQ) will exercise enforcement discretion for exceedances of emission limits as well as operational limits for power generating plants for Generators who exceed air permit limits in order to maximize generation for the duration of the EEA event. ERCOT General Council will send out a Market Notice each time ERCOT enters into an EEA with this reminder. |
| ### Implement EEA Level 1 |  |
| 1 | IF: - PRC < 2300 MW; THEN: - Deploy all available Non-Spin (if not previously deployed) (see Desktop Guide Resource Desk Section 2.1.1). - Determine whether system conditions require the deployment of ERS-30 (see Desktop Guide Resource Desk Section 2.3.2). - Make EEA 1 posting to MIS Public - Use preformatted notice “EEA Level 1” |
| 2 | IF: - ERS-30 is deployed; THEN: - Also deploy WS ERS if available - Notify the Real-Time Operator when XML message has been completed. ERS must be deployed before hotline call is made. |
| 3 | Verify all measures have been implemented. |
| Log | Log all actions. |
| ### Implement EEA Level 2 |  |
| 1 | IF: - PRC < 1750 MW or unable to maintain system frequency at 60.00Hz; THEN: - Determine when system conditions require the deployment of Load Resources and/or ERS Resources (Do Not forget the WS ERS if available): - Deploy ERS-30 if not already done in EEA1 - Deploy ERS-10 - Deploy Load Resources Group 1 and/or 2 - Notify the Real-Time Operator when XML message has been completed. Load Resources/ERS must be deployed first before hotline call is made, - Desktop Guide Resource Desk (Section 2.2.1 for Load Resources; Section 2.3.2 for ERS). - Make EEA 2 posting to MIS Public - Use preformatted notice “EEA Level 2” |
| ERS Business Hour Changes | IF: - ERS Resources are deployed, and the Business Hour is changing and if ERS is still needed; THEN: - Deploy next business hour - Take into consideration the time requirement for the ERS-10 and ERS-30 - Notify the Real-Time Operator when XML message has been completed. ERS must be deployed before hotline call is made. |
| 2 | IF: Went straight to EEA Level 2; THEN: - Ensure tasks in EEA Level 1 are complete. |
| 3 | Verify all measures have been implemented. |
| Log | Log all actions. |
| ### Implement EEA Level 3 |  |
| 1 | IF: - Unable to maintain system frequency at 59.80 Hz; THEN: - Make EEA 3 posting to MIS Public - Use preformatted notice “EEA Level 3” |
| 2 | Verify all measures have been implemented. |
| Log | Log all actions. |

## 7.3	Restore EEA Levels

Procedure Purpose:  To restore the ERCOT grid to normal state as system conditions warrant while recovering from an EEA event.

| Protocol Reference | 6.5.9.4.3 |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.5.3.5 |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 12 | Effective Date: August 1, 2014 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| RESERVES | 1375 MW of PRC must be restored within 90 minutes. |
| ### Restore Firm Load |  |
| 1 | IF: - Sufficient Regulation Service exist to control to 60 Hz, AND - PRC – Regulation Up Responsibility ≥ 1375 MW for the last 15 minutes; THEN: - Transmission Operator will restore firm load. |
| ### Move from EEA Level 3 to EEA Level 2 |  |
| 1 | IF: - Sufficient Regulation Service exist to control to 60 Hz, AND - PRC is ≥ 1750 MW, AND - All firm load have been instructed to be restored; THEN: - When instructed by the Real-Time Operator to recall Load Resources - Send XML message to recall Load Resources, (see Desktop Guide Resource Desk Section 2.2.4) - Make EEA 3 to EEA 2 posting to MIS Public - Use preformatted notice |
| ### Move from EEA Level 2 to EEA Level 1 |  |
| 1 | IF: - The system can maintain PRC ≥ 2300 MW, AND - All Load Resources have been instructed to be restored; THEN: - Send XML message to recall 10 MIN/30 MIN ERS (see Desktop Guide Resource Desk Section 2.3.3) - Make EEA 2 to EEA 1 posting to MIS Public - Use preformatted notice |
| ### Move from EEA Level 1 to EEA 0 |  |
| 1 | IF: - The system can maintain PRC ≥ 2300 MW, AND - All uncommitted units secured in EEA 1 can be released, AND - Emergency energy from the DC Ties is no longer needed; THEN: - Terminate EEA 1 by posting to MIS Public - Use preformatted notice “EEA 1 to Normal” |
| ### Recall Non-Spin and Cancel Watch |  |
| 1 | WHEN: - Avail_CAP_30Min ≥ 1000, AND - PRC is ≥ 2800 MW; THEN: - Coordinate with the Real Time Operator and recall half of the Non-Spin by sending a Zero MW XML message (Refer to Desktop Guide Resource Desk Section 2.1.3). WHEN: - Avail_CAP_30Min ≥ 1000, AND - PRC is ≥ 3000 MW; THEN: - Coordinate with the Real Time Operator and recall all of the Non-Spin by sending a Zero MW XML message (Refer to Desktop Guide Resource Desk Section 2.1.1). |

## 7.4	Restoration of Primary Control Center Functionality

Procedure Purpose:  To be performed once Resource Desk Operator has arrived at ACC.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | EOP-001-0 R4.1, R4.2, 4.4 |  |  |  |

| Version: 1 | Revision: 1 | Effective Date: December 13, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - Assist the Real-Time operator as needed - Follow procedure manual as normal operation returns |
| Log | Log all actions. |

# 8.	Communication Testing

## 8.1	Weekly Hotline Test

Procedure Purpose: To perform a weekly communication test of the ERCOT Hotline phone system.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 7.1.3 (c) |  |  |  |
| NERC Standard | COM-001-1.1 R2 |  |  |  |

| Version: 1 | Revision: 6 | Effective Date: April 4, 2014 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | In the event of a failure of the Forum Conference Client software, the most recent printout of the Hotline log may be used to perform a manual roll call of the QSEs. |
| NOTE | Insure all Invalid Hotlines “Lost Souls” are cleared prior to the hotline call. |
| NOTE | Confirm with Shift Supervisor the threat alert level, which can be viewed at the following links: http://www.esisac.com/SitePages/Home.aspx, OR http://www.dhs.gov/files/programs/ntas.shtm The definitions for the threat alert level are listed in the Security Alert Plan. |
| 1 | Test the ERCOT Hotline: - Each Monday between 0630 and 1100, AND - When working from the Alternate Control Center during the monthly scheduled dates. |
| 2 | Using the Hotline, notify all QSEs/TOs of the purpose of the call. - When QSEs have answered the Hotline, print Hotline participants. Typical Hotline Script: “This is ERCOT Operator [first and last name]. ERCOT is conducting the weekly [QSE/TO] Hotline test. ERCOT is currently at threat alert level [state alert level]. The following notices are currently in effect: - List OCNs, Advisories, Watches and/or Emergency Notices in effect. - State “None” if none are in effect. This ends the test of the ERCOT Hotline. That is all.” |
| 3 | IF: - A QSE did not answer; THEN: - Contact them using their OPX line or LD line to inquire why they were not on the Hotline call; - Open a Help ticket if ERCOT’s Telecommunications department is needed to investigate. |
| 4 | Place printout in the appropriate folder in the file in the back of the room. |
| 5 | If a Hotline call was made between 0630 and 1100 Monday, it is not necessary to make an additional call. |
| LOG | Log all actions. |

## 8.2	Monthly Testing of Satellite Phones

Procedure Purpose: To ensure ERCOT maintains communication capability via the Satellite Phone System.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | COM-001-1.1 R2 |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 5 | Effective Date: December 13, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Primary Control Center |  |
| NOTE | When a participant dials into the conference bridge before the moderator dials in, they will hear music and be placed on hold. |
| NOTE | On the first weekend of each month, between the hours of 0000 Saturday and 0500 Monday, the Satellite Phone System Conference Bridge will be tested with the TOs. As the Shift Supervisor makes the call to the individual TO, they will set a time that the ERCOT Operator will call the Satellite Phone System Conference Bridge and establish communication with the appropriate TO. |
| NOTE | Use the ERCOT Satellite Phone User Guide (See Desktop Guide Common to Multiple Desks Section 2.7) for a list of the TOs that will be contacted by the ERCOT Operator and instructions on how to place a Satellite Phone System Conference Bridge call. |
| NOTE | The numbers for the ERCOT Operator to call into the Conference Bridge are Desk specific. Select: SATELLITE directory or go to page 35 to view the programmed numbers on the Turret phone for each Bridge: - BLACKSTRT RUC – RUC Desk - BLACKSTRT RES – Resource Desk - BLACKSTRT REAL – Real-Time Desk - BLACKSTRT TS#1 – Transmission Desk (Island Coordination) - BLACKSTRT TS#2 – Transmission Desk |
| 1 | IF: - The preprogrammed number does not function correctly; THEN: - Refer to the ERCOT Satellite Phone User Guide (See Desktop Guide Common to Multiple Desks Section 2.7.2) for the appropriate conference number and continue with this procedure. |
| 2 | When prompted: - Enter the Moderator Pass Code - If necessary, allow five minutes for Participants to dial in - As each Participant connects, record the following: - Name of Participant - Company Name - Any problems identified with the connection process |
| 3 | IF: - One or more of the TOs fails to connect to the Bridge call; THEN: - Investigate the cause and log the following: - Reason for inability to connect - Actions taken by ERCOT - Establish a time for a retest of the TOs not able to connect in the initial test. |
| 4 | Inform the Shift Supervisor when test is complete indicating any issues identified. |
| LOG | Log all actions. |
| ### Alternate Control Center |  |
| 1 | When working out of the alternate during the monthly scheduled dates: - Test the turret Satellite phone on each desk. |
| 2 | Inform the Shift Supervisor when test is complete indicating any issues identified. |
| LOG | Log all actions. |

# 9.	Perform Miscellaneous

## 9.1	Respond to Miscellaneous Issues

Procedure Purpose: To minimize telemetry issues that could have an impact on LMPs.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 5 | Effective Date: December 13, 2013 |
| --- | --- | --- |

| Step |  |  | Action |  |
| --- | --- | --- | --- | --- |
| ### Telemetry Issues that could affect SCED and/or LMPs |  |  |  |  |
| Notification of Telemetry Issue |  |  | IF: - There is a telemetry issue, THEN: - Ensure the appropriate Control Room personnel are aware of the issue, and - Instruct the QSE to correct the issue. |  |
| QSE Override |  |  | IF: - The QSE cannot fix the issue in a timely manner, THEN: - Ask the QSE to override the bad telemetry. |  |
| QSE unable to Override |  |  | IF: - For some reason, the QSE cannot override the bad telemetry, NOTIFY: - Shift Supervisor and Operations Support Engineer The Operations Support Engineer will work with the QSE and/or the ANA group to override the bad telemetry; however it may be necessary for the Real-Time operator to make manual adjustments in SCED until the issue is resolved. |  |
| ### Backup/Alternate Control Center Transfer |  |  |  |  |
| 1 |  |  | When notified by a QSE that they will be transferring to or from their backup/alternate control center, - Identify the [QSE] in the email notification - Send e-mail to “1 ERCOT System Operators” |  |
| Log |  |  | Log all actions. |  |
| ### QSE Issues |  |  |  |  |
| 1 |  | If a QSE is not satisfied with ERCOT Operations responses to their issues, refer them to their Wholesale Client Representative for clarification/resolution. |  |  |
| 2 |  | If the System Operator believes the issue is with ERCOT systems applications (ICCP down, etc.), notify the ERCOT Help Desk. |  |  |
| 3 |  | If a QSE is having an issue with ERCOT system applications (unable to access the portal, outage scheduler, etc.), instruct them to call the ERCOT Help Desk. |  |  |
| 4 |  | As time permits, notify the Shift Supervisor of any actions taken and unresolved issues. |  |  |
| Log |  | Log all actions. |  |  |
| ### Missing Data from MIS Postings |  |  |  |  |
| 1 |  | IF: - A call is received about data missing or data being incorrect, THEN: - Transfer call to the Help Desk, and - Notify the Shift Supervisor and Operations Support Engineer. |  |  |
| Log |  | Log all actions. |  |  |
| ### Courtesy Hotline calls for ERCOT Application Issues |  |  |  |  |
| 1 |  | WHEN: - Notified from IT support of application(s) issues that are causing Market Participants an inability to submit data to ERCOT; THEN: - Make a courtesy hotline to inform them. Typical Hotline script: “This is ERCOT Operator [first and last name]. This is a courtesy call to inform you that ERCOT is experiencing application problems which is causing QSEs issues with submittals. |  |  |
| ### Power System Stabilizers (PSS) & Automatic Voltage Regulators (AVR) |  |  |  |  |
| 1 | WHEN: - Notified by a QSE of a change in status with any PSS or AVR; THEN: - Transfer call to the ERCOT Transmission Operator. |  |  |  |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Frosch, Hartmann, Stone, and Barcalow | Preparers | November 10, 2010 |
| Frosch and Hartmann | Procedure writers and editors | November 29, 2010 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2010 |
| Frosch and Hartmann | Procedure writers and editors | January 26, 2011 |
| Frosch and Hartmann | Procedure writers and editors | March 23, 2011 |
| Frosch and Hartmann | Procedure writers and editors | April 20, 2011 |
| Frosch and Hartmann | Procedure writers and editors | May 10, 2011 |
| Frosch and Hartmann | Procedure writers and editors | June 6, 2011 |
| Frosch and Hartmann | Procedure writers and editors | July 18, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 30, 2011 |
| Frosch and Hartmann | Procedure writers and editors | September 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | October 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 16, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | April 25, 2012 |
| Frosch and Hartmann | Procedure writers and editors | May 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | May 30, 2012 |
| Barcalow, Frosch and Hartmann | Procedure writers and editors | July 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | August 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | October 26, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 26, 2013 |
| Frosch and Hartmann | Procedure writers and editors | May 28, 2013 |
| Frosch and Hartmann | Procedure writers and editors | July 8, 2013 |
| Cheng, Frosch and Hartmann | Procedure writers and editors | August 7, 2013 |
| Frosch and Hartmann | Procedure writers and editors | September 25, 2013 |
| Frosch and Hartmann | Procedure writers and editors | December 11, 2013 |
| Frosch, Gaddy and Hartmann | Procedure writers and editors | April 1, 2014 |
| Frosch, Gaddy and Hartmann | Procedure writers and editors | May 27, 2014 |
| Frosch and Hartmann | Procedure writers and editors | July 29, 2014 |
| Frosch and Hartmann | Procedure writers and editors | September 29, 2014 |
| Frosch and Hartmann | Procedure writers and editors | December 10, 2014 |
| Frosch and Thompson | Procedure writers and editors | December 19, 2014 |

Manual Change History

| Procedure | Ver/Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All Sections | 1.0 / 0 | New procedures for all sections for Nodal implementation | November 28, 2010 |
| 3.1 3.4 3.5 3.7 4.1 5.1 5.1 5.2 6.1 7.2 | 1.0 / 1 1.0 / 1 - / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Deleted WGR section, in section “Monitor QSE Ancillary Services Obligation”, updated step Infeasible A/S Capacity from RUC & A/S Difference in COP Updated Note Updated step 3 Updated whole procedure Updated step 2 In section “Procurement of Ancillary Services due to DAM Failure”, “ERCOT Increases the Amount of Ancillary Services”, “Replacement of Ancillary Service Due to Infeasibility/Failure to Provide”, “Replacement of Ancillary Services in Real Time”, Updated step 1 Updated whole procedure In section “Timeline Deviations”, Updated 2nd Note In section “Returning from Planned Outage Early”, Updated Deny In section “Implement EEA Level 1”, Updated step 1 | December 1, 2010 |
| 3.1 3.7 3.8 5.1 | 1.0 / 2 1.0 / 2 1.0 / 0 1.0 / 2 | Deleted “Monitor Base Point Deviations” and updated “A/S Difference in COP” Deleted step Note, Deployment, & Termination New Procedure Updated “Procurement of Ancillary Services due to DAM Failure”, “ERCOT Increases the Amount of Ancillary Services” and “Replacement of Ancillary Service Due to Infeasibility/Failure to Provide“ step 3 and 4 | December 15, 2010 |
| 3.1 3.2 3.4 3.3 3.5 3.7 4.1 5.1 5.2 7.1 7.2 7.3 8.2 | 1.0 / 3 1.0 / 1 1.0 / 2 1.0 / 1 1.0/ 2 1.0 / 3 1.0 / 2 1.0 / 3 - / 2 - / 1 - / 2 1.0 / 1 1.0 / 1 | Updated step Telemetered Status, step 1 in Manual Override Checks and removed workaround step “Real Time A/S shortage” in Monitor QSE Ancillary Services Obligation Updated all steps Updated steps “Deployment” and “Termination” Updated step 1 on “Cancelation” Updated all steps and added note Updated all steps Updated and deleted Notes and step 1 Updated “Procurement of Ancillary Services due to DAM Failure”, “ERCOT Increases the Amount of Ancillary Services”, “Replacement of Ancillary Service Due to Infeasibility/Failure to Provide“ step 3 and added note on Replacement of Ancillary Services in Real Time Updated Second Note on “Timeline Deviations” Updated Hotline on “Scripts” Updated Step 1 on ” Implement EEA Level 1” and “Implement EEA Level 2A” Updated Steps 1 on “Move from EEA Level 3 to EEA Level 2B” and “Cancel Watch” Deleted Site Failover Notification procedure & changed 8.3 to 8.2 | January 31, 2011 |
| 3.3 3.4 3.7 5.1 7.1 | 1.0 / 2 1.0 / 3 1.0 / 4 1.0 / 4 1.0 / 2 | Updated step 1 in “Watch” & step 1 in “Cancelation” Updated “Deployment” and “Termination” Updated “Issue Watch & Deploy Non-Spin” and “Recall Non-Spin” Updated step 2 in “Replacement of Ancillary Service Due to Infeasibility/Failure to Provide” Updated “Watch” and “Emergency Notice” | March 25, 2011 |
| 3.5 7.1 7.3 | 1.0 / 3 1.0 / 3 1.0 / 2 | Updated NERC Recovery Criteria Updated step 1 in Watch and Emergency Notice and step Post Updated 1st and 2nd script in Restore Firm Load, Updated 1st in Move From EEA Level 3 to EEA Level 2B | April 22, 2011 |
| 3.8 3.9 5.1 8.1 | 1.0 / 0 1.0 / 1 1.0 / 5 1.0 / 1 | Added new procedure Changed section number from 3.8 to 3.9 Updated steps 3-5 in Replacement of A/S due to Infeasibility/Failure to Provide, deleted Replacement of A/S in Real-Time Change section name, updated step 2 & 3 | May 11, 2011 |
| 3.3 3.4 3.6 3.7 3.8 7.1 | 1.0 / 3 1.0 / 4 1.0 / 1 1.0 / 5 1.0 / 1 1.0 / 4 | Updated step 1 in Advisory and Watch Updated step Deployment Updated step 1 Updated step Deploy Non-Spin & Post & Deploy Load Resources & Post Updated step Post Updated all steps | June 8, 2011 |
| 3.3 3.4 3.5 3.8 4.1 5.2 7.1 7.2 7.3 9.1 | 1.0 / 4 1.0 / 5 1.0 / 4 - / 2 1.0 / 3 1.0 / 3 1.0 / 5 1.0 / 3 1.0 / 3 1.0 / 1 | Updated step 1 in Advisory and Watch Updated step on Deployment Updated step on PRC Below 2300 Added step Termination, updated steps on Post and Cancel Posting Updated step 2 in Approve/Reject Decommitment QSE Requests in Operating Period Updated step 1 and deleted 2nd note in Timeline Deviations Updated step Watch Updated all steps Updated all steps Added Market Participant Backup Control Center Transfer procedure | July 20, 2011 |
| 3.3 3.4 5.1 7.1 7.2 7.3 8.2 | 1.0 / 5 1.0 / 6 1.0 / 6 1.0 / 6 - / 4 1.0 / 4 1.0 / 2 | Updated step 1 in Cancelation Updated Note, added steps Additional Deployment & Commit, updated steps Note & Deployment Updated 1st Note Added projected reserve capacity shortage and Extreme Hot Weather in Watch Updated 2nd Note, step 1 & 2 in EEA Level 1, step 1 in EEA Level 2A, added note in EEA Level 2B Updated step 1 in Cancel Watch Updated 4th Note and step 1 | September 1, 2011 |
| 7.2 7.3 8.1 | 1.0 / 5 1.0 / 5 1.0 / 2 | Combined EEA 2A & B per NPRR 379 Combined EEA 2A & B per NPRR 379 Updated step 2 | October 1, 2011 |
| 3.1 3.4 3.6 3.8 3.9 4.1 5.1 8.1 | 1.0 / 4 1.0 / 7 1.0 / 2 1.0 / 3 1.0 / 2 1.0 / 4 1.0 / 7 1.0 / 3 | Changed desktop guide reference in Monitor QSE Ancillary Services Obligation Updated step Commit Updated procedure title and all steps Updated steps 1 & Termination, added step 2 Deleted procedure due to protocol change Added 2nd Note Updated steps 1 – 3 in Procurement of A/S due to DAM Failure, steps 1 -2 in ERCOT Increased the Amount of A/S, steps 1 & 4 in Replacement of A/S Due to Infeasibility/Failure to Provide Added Note 2 & 3 | November 1, 2011 |
| 3.3 3.4 3.7 3.8 7.1 | 1.0 / 6 1.0 / 8 1.0 / 6 1.0 / 4 1.0 / 7 | Add Note in Watch Added second Note Added second Note Added Note Updated Post in “Scripts” All procedures in this manual have been reviewed. | December 15, 2011 |
| 1.2 3.1 3.4 4.1 5.1 | 1.0 / 1 1.0 / 5 1.0 / 9 1.0 / 5 1.0 / 8 | Updated Scope Updated Monitor QSE A/S Obligation procedure Updated 1st Note Updated steps 1 & 2 Updated step 2, 3 & 4 | January 19, 2012 |
| 2.1 3.1 3.3 3.4 3.5 3.7 3.8 4.1 5.1 7.1 7.2 7.3 8.2 9.1 | 1.0 / 1 1.0 / 6 1.0 / 7 1.0 / 10 1.0 / 5 1.0 / 7 1.0 / 5 1.0 / 6 1.0 / 9 1.0 / 8 1.0 / 6 1.0 / 6 1.0 / 3 1.0 / 2 | Updated paragraph 4 Updated Desktop Guide references Updated Desktop Guide references Updated Desktop Guide references Updated Desktop Guide references Updated Desktop Guide references Updated Desktop Guide references Updated 1st Note & step 1 Updated Desktop Guide references, step 3s & 4 Updated step 1 of Watch Updated Desktop Guide references Updated Desktop Guide references Updated Desktop Guide references Updated QSE Override, QSE unable to Override, Backup/Alternate Control Center Transfer, QSE Issues & step Power System Stabilizers (PSS) & Automatic Voltage Regulators (AVR) | March 1, 2012 |
| 2.1 3.1 3.5 3.6 3.7 4.1 5.1 7.1 9.1 | 1.0 / 2 1.0 / 7 1.0 / 6 1.0 / 3 1.0 / 6 1.0 / 7 1.0 / 10 1.0 / 9 1.0 / 3 | Changed TSP/DP to TO Updated step Not Dispatchable to SCED Deleted Potential DCS Event, changed section number for System Failures Changed section number Changed section number & added step 3 Updated step 1 Updated information needed in e-mail Updated all step 1’s Changed Shift Engineer to Ops Support Engineer | May 1, 2012 |
| 3.3 3.4 | 1.0 / 8 1.0 / 11 | Updated to reflect changes in the TAC approved Non-Spin document Updated to reflect changes in the TAC approved Non-Spin document | May 14, 2012 |
| 7.2 7.3 | 1.0 / 7 1.0 / 7 | Updated EILS to ERS per NPRR 451 Updated EILS to ERS per NPRR 451 | June 1, 2012 |
| 1.3 4.1 6.1 7.1 7.2 7.3 8.2 | 1.0 / 1 1.0 / 8 1.0 / 2 1.0 / 10 1.0 / 8 1.0 / 8 1.0 / 4 | Removed ERCOT Shift Supervisor paragraph Added Desktop Guide to VDI reference Added Desktop Guide to VDI reference and updated Maintenance Level 2 and 3 outages Updated all step 1’s Added Desktop Guide to VDI reference, updated step 1 Implement EEA Level 2 and added ERS Updated step 1 Move from EEA Level 3 to EEA Level 2 Updated 4th note | July 16, 2012 |
| 3.1 7.2 | 1.0 / 8 1.0 / 9 | Updated step ONTEST Updated step 1 of Implement EEA Level 1 | August 29, 2012 |
| 2.2 7.2 8.1 | 1.0 / 1 1.0 / 10 1.0 / 4 | Added Hotline Call Communication Updated Implement EEA Level 1 step 2, Implement EEA Level 2 step 1 and ERS Business Hour Changes Updated 1st Note, step 1, 2 & 3. Added step 4 and Log All procedures in this manual have been reviewed. | November 1, 2012 |
| 3.3 3.4 3.6 3.7 4.1 5.1 7.3 | 1.0 / 9 1.0 /12 1.0 / 9 1.0 / 7 1.0 / 8 1.0 / 11 1.0 / 9 | Non-Spin deployment messages are now automated Non-Spin deployment messages are now automated Non-Spin deployment messages are now automated Non-Spin deployment messages are now automated Updated steps 1 & 2 Updated steps Note, Procurement Timeline & 1. Added new procedure, Daily Reconfiguration SASM Updated step 1 of Cancel Watch | March 1, 2013 |
| 3.3 3.5 5.1 5.2 7.1 7.2 7.3 8.1 9.1 | 1.0 / 10 1.0 / 4 1.0 / 12 1.0 / 4 1.0 / 11 1.0 / 11 1.0 / 10 1.0 / 5 1.0 / 4 | Removed notice builder reference Removed notice builder reference Updated steps 1 & 5 in ERCOT Increased the amount of A/S & steps in Daily Reconfiguration SASM Updated step 1 Updated Scripts Removed notice builder reference & Updated Scripts Removed notice builder reference Updated Script Updated Script | June 1, 2013 |
| 3.1 7.1 | 1.0 / 9 1.0 / 12 | Deleted 1st Note, added step Log, moved Not Dispatchable to SCED, Control Block Up/Down, & Real-Time RRS A/S Shortages to Real-Time procedure, deleted Manual Override Checks Updated step 1 in Watch & Emergency Notice | July 15, 2013 |
| 5.1 5.2 | 1.0 / 13 1.0 / 5 | Updated 1st Note for R4 changes, Daily SASM Timeline Updated 1st Note for R4 changes | August 9, 2013 |
| 5.1 6.1 | 1.0 / 14 1.0 / 3 | Updated 1st Note, Daily SASM Timeline Updated to reflect SCR770 changes | September 27, 2013 |
| 3.1 3.2 3.3 3.5 3.6 3.7 4.1 5.1 6.1 6.2 7.1 7.2 7.4 8.2 9.1 | 1.0 / 10 1.0 / 2 1.0 / 11 1.0 / 5 1.0 / 10 1.0 / 8 1.0 / 10 1.0 / 15 1.0 / 4 1.0 / 1 1.0 / 13 1.0 / 12 1.0 / 1 1.0 / 5 1.0 / 5 | Added Monitor QSE A/S Obligation Title Updated Evaluate Request Updated step Log Updated step Log Updated step Log Updated step Log Updated step 3 Updated step Log Updated Accept Maintenance Outage, Coordinate Maintenance Outage, Coordinate Maintenance Level 2 and 3 and Log Updated step Log Updated step Log Updated last step and added Log Updated step Log Updated step Log Updated and added step Log All procedures in this manual have been reviewed. | December 13, 2013 |
| 3.4 3.5 3.74.1 6.1 7.1 7.2 7.3 8.1 | 1.0 / 13 1.0 / 7 1.0 / 9 1.0 / 11 1.0 / 5 1.0 / 14 1.0 / 13 1.0 / 11 1.0 / 6 | Updated VDI information Updated for NPRR542 Updated VDI information Updated VDI information Updated VDI information Updated to incorporate NPRR542 Updated ERS, Media appeal, TCEQ, VDI language, and moved steps to RUC desk Updated Reserves and step 1 Updated step 1 & 3, added step 5 | April 4, 2014 |
| 2.2 3.1 3.3 3.4 4.1 5.1 5.2 7.1 | 1.0 / 2 1.0 / 11 1.0 / 12 1.0 / 14 1.0 / 12 1.0 / 16 1.0 / 6 1.0 / 15 | Added VDIs to Master QSEs Updated Monitor QSE AS Obligations steps Updated steps in Watch Updated title, step Deployment & Termination Updated step 1 & 2 Updated section titles & steps Updated Timeline Deviations Added Note, updated Advisory & Watch | June 1, 2014 |
| 3.1 3.4 3.6 3.7 4.1 5.1 6.1 7.2 7.3 | 1.0 / 12 1.0 / 15 1.0 / 11 1.0 / 10 1.0 / 13 1.0 / 17 1.0 / 6 1.0 / 14 1.0 / 12 | Updated Desktop references Updated Desktop references Updated Desktop references Updated Desktop references Updated Desktop reference Updated steps 1, 4-6 in Replacement of A/S due to infeasibility or failure to provide, & Desktop references Updated Forced Derate Updated Desktop references Updated Desktop references | August 1, 2014 |
| 7.1 | 1.0 / 16 | Updated Scripts | October 1, 2014 |
| 3.4 3.6 4.1 6.2 | 1.0 / 16 1.0 / 12 1.0 / 14 1.0 / 2 | Deleted Note & added Log Changed title & added Rio Grande Valley Re-worded procedure Added step 2 All procedures in this manual have been reviewed | December 15, 2014 |
| 5.1 | 1.0 / 18 | Added new procedure “Increasing A/S for Extreme Cold Weather and changed title for “Increasing A/S for other reasons and updated timeline | December 22, 2014 |