- Power Operations Bulletin # 726

ERCOT has posted/revised the Real Time manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

- http://www.ercot.com/mktrules/guides/procedures/index.html

## 2.6	Site Failovers and Database Loads

Procedure Purpose: To provide notice to the Market Participants when ERCOT is performing updates to the Energy and Market Management Systems.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 16 | Effective Date: December 31, 2015 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| EMS Changes | Approximately 5 - 30 minutes before a database load, local failover, or EMS migration, make the following Hotline call to QSEs: Q#18 - Typical Hotline Script for EMS changes |
| MMS Changes | Approximately 5 - 30 minutes before a MMS migration, make the following Hotline call to QSEs: Q#19 - Typical Hotline Script for MMS changes |
| Site Failover Posting | The site failover message is already built in Notice Builder under “EMMS Site Failover”. |
| Site Failover | Approximately 5 - 30 minutes before site failover, make the following Hotline call to QSEs: Q#20 - Typical Hotline Script for Site Failover |
| Site Failover Complete | Q#21 - Typical Hotline Script for Site Failover complete |
| If EBPs are needed | IF: - Site Failover is taking longer than expected and EMS is functional and MMS is not, or - SCED is not solving with a valid solution and EBPs are needed; THEN: - Enter the EBP increment/decrement as needed to control frequency, - Notify Resource Operator to post a message on MIS Public , - Notify Transmission Operator to make Hotline call to TOs, - Make the following hotline call to QSEs: Q#22 - Typical Hotline Script for Watch and Emergency Basepoints until Site Failover complete |
| Site Failover Complete If EBPs were needed | WHEN: - SCED is solving with a valid solution; THEN: - Remove the Emergency Base Point flag, - Initiate Hotline call to cancel the Watch, - Notify Resource Operator to cancel MIS posting, - Notify Transmission Operator to cancel the Watch with TOs. Q#23 - Typical Hotline Script Cancel Watch and Emergency Basepoints, Site Failover complete |

## 3.2	Monitor Large Ramp Events

Procedure Purpose:  The ERCOT Large Ramp Alert System (ELRAS) is designed to monitor the probability of large wind output ramps in the ERCOT region and provide ERCOT Operators with further situational awareness.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 7 | Effective Date: December 31, 2015 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | ERCOT Large Ramp Alert System (ELRAS) link: AWS primary web server site: http://products.meso.com/elras_dev AWS backup web server site: http://products2.meso.com/elras_dev The potential for a large ramp can be identified using the “Graphical Forecast” page of ELRAS forecast Real-Time Mode. An example of the page is in figure 1 below. The “Graphical Forecast” page plots the probability of a ramp rate event starting at a given time during the next 6 hours. The graphical displays are broken up into three timeframes; 15-minute probabilities, 60-minute probabilities, and 180-minute probabilities, and Up and Down ramp rate events are split up for each time frame. These displays are interpreted by first looking at a particular interval on a given display. The value for that interval on that display is characterized as the probability of a given MW change occurring over a specified amount of time starting at the specified interval. For example, looking again at figure 1, the “Graphical Forecast” is showing a 50% probability of at least a 2,000 MW increase occurring over 180 minutes starting at 18:00. In other words, between 18:00 and 21:00 there is a 50% chance that the aggregate wind output will increase by at least 2,000 MW. For the purpose of this procedure, the forecasted ramp rates to be considered significant are those that are indicated in Red; 1,000 MW in 15-minutes, 2,000 MW in 60-minutes, and 4,000 MW in 180-minutes. In the event that one of these ramp rates is forecasted to have at least a 30% probability of occurring, determine if the system has the ramp rate to keep up with the wind ramp. |
| 1 | IF: - The ELRAS tool does not forecast a ramp that you believe it should have; THEN: - Send an e-mail to “Operations Analysis” and “shiftsupv” |
| ### Down Ramp Event |  |
| 1 | PERIODICALLY REVIEW: - EMS Applications>Frequency>Frequency Dashboard - OpsMon Dashboard Viewer under the MOS folder: - “Monitor Large Ramp Events” |
| 2 | IF: - There is a 30% probability of a projected system wide down-ramp of 4,000 MW within the next 180 minutes, OR - There is a 30% probability of a projected system wide down-ramp of 2,000 MW within the next 60 minutes; THEN: - Refer to the “180 min. HASL(COP) - LF or 60 min. HASL(COP) - LF” on the 60 to 180 minute OpsMon Dashboard to determine if system ramp rate capability is sufficient, AND - Make a Hotline call to provide situational awareness about a possible down-ramp event of 2,000 MW or greater within the next 60 minutes or 4,000 MW or greater within the next 180 minutes. IF: - System ramp rate is not sufficient; THEN: - Notify RUC Operator to procure Resources as needed. Q#26 - Typical Hotline Script for OCN for Forecasted Probability of a Large Down Ramp |
| 3 | IF: - There is a 30% probability of a projected system wide down-ramp of 1,000 MW within the next 15 minutes; THEN: - Refer to the “HDL-Gen” on the 15 minute OpsMon Dashboard and the available Regulation UP Service in the EMS Display, IF: - The margin is less than available to adequately maintain the potential system ramp rate; THEN: - Deploy Non-Spin as needed, and - Continue to monitor frequency and “HDL-Gen” |
| ### Up Ramp Event |  |
| NOTE | Up ramps should be self-mitigating since a majority of the wind generators have governor response capabilities. |
| 1 | PERIODICALLY REVIEW: - EMS Applications>Frequency>Frequency Dashboard - OpsMon Dashboard Viewer under the MOS folder: - “Monitor Large Ramp Events” |
| 2 | IF: - There is a 50% probability of a projected system wide up-ramp of 2,000 MW within the next 15 minutes; THEN: - Refer to the “Gen - LASL” on the 15 minute OpsMon Dashboard and the available Regulation DOWN Service in the EMS Display, IF: - The margin is less than available to adequately maintain the potential system ramp rate; THEN: - Monitor frequency, Reg-Down and run SCED as often as required. |
| Log | Log all actions. |

## 3.3	System Failures

Procedure Purpose:  To ensure that frequency is maintained in the event of an AGC failure.

| Protocol Reference | 6.3.3 | 6.5.9.1(2) | 6.5.9.2 (1)& (3) | 6.5.9.3.3(2)(g) |
| --- | --- | --- | --- | --- |
| Guide Reference | 2.2.4.3 (1) |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 19 | Effective Date: December 31, 2015 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### SCED Failure |  |
| NOTE | When RLC sees that the SCED solution has not updated within the last 605 seconds, emergency base points (EBP) will automatically activate. Any time EBPs are activated, SCED solutions are being blocked from being communicated to MPs. The RLC Control Parameters (SCED Failure Threshold) should be set to 305 seconds. This is due to a code that adds 300 seconds to the 305 seconds from SCED Failure Threshold Parameter in the display, so total number of seconds RLC waits for SCED solution is 605 before enabling the emergency base points. |
| NOTE | If for some reason a manual EBP is required for a Resource, communicate the Resource name, MW output requested, start time and duration of the dispatch instruction to the QSE representing the Resource. |
| 1 | IF: - Any module of the SCED Workflow Controller fails; THEN: - Manually run the SCED process. |
| 2 | IF: - SCED still fails after manually running, AND - EBPs have automatically activated; THEN: - Contact the Help Desk, - Initiate the Watch Hotline call to QSEs, - Notify Resource Operator to post a message on MIS Public, - Notify Transmission Operator to make Hotline call to TOs. Q#27 - Typical Hotline Script for Watch for SCED Failure |
| 3 | EMP Applications>Generation Area Status>Related Displays>ERCOT Nodal Summary MONITOR: - Regulation Service (Up/Dn) margins to ensure frequency can be adequately maintained. IF: - It is determined that remaining Regulation Service (Up/Dn) is no longer sufficient to maintain system frequency; THEN: - Enter the EBP increment/decrement as needed to control frequency to recall deployed Regulation. - Once the MW amount has ramped, the EBP amount will return to zero |
| 4 | WHEN: - SCED is solving with a valid solution; THEN: - Remove the Emergency Base Point flag, - Initiate Hotline call to cancel the Watch, - Notify Resource Operator to cancel MIS posting, - Notify Transmission Operator to cancel the Watch with TOs. Q#28 - Typical Hotline Script for Cancel Watch for SCED is Solving |
| Log | Log all actions. |
| ### SCED Data Input Failure |  |
| 1 | IF: - SCED receives data input failures and gives erroneous results; THEN: - Manually activate EBP, - Contact the Help Desk, - Initiate the Watch Hotline call - Notify Resource Operator to post the message on MIS Public, - Notify the Transmission Operator to make Hotline call to TOs. Q#29 - Typical Hotline Script for Watch for SCED Data Input Failure |
| 2 | Follow steps 4 and log in SCED Failure above as needed. |
| ### RLC Failure |  |
| 1 | The Resource Limit Calculator (RLC) can fail independently of AGC. If RLC fails, SCED will not function (invalid results), even though it shows available. A RLC failure will be displayed to the Operator in the upper right corner of the RLC display as follows: - Process Status: RLC Up (Normal Operation) - Process Status: RLC Down (will be displayed in RED when failed) - RLC (PI Alarm) will be flashing RED. |
| NOTE | Regulation is functioning, RRS is not. LFC (AGC) will automatically switch to EBP mode. |
| 2 | IF: - RLC has failed; THEN: - Verify the status of AGC - IF AGC is also failed, proceed to the EMS (LFC and RLC) Failure procedure - Contact the Help Desk, - Initiate a Watch Hotline call to QSEs - Notify Resource Operator to post the message on MIS Public - Notify Transmission Desk Operator to make Hotline call to TOs. Q#30 - Typical Hotline Script for Watch for RLC Failure |
| 3 | EMP Applications>Generation Area Status>Related Displays>ERCOT Nodal Summary MONITOR: - Regulation Service (Up/Dn) margins to ensure frequency can be adequately maintained. IF: - It is determined that remaining Regulation Service (Up/Dn) is no longer sufficient to maintain system frequency; THEN: - Enter the EBP increment/decrement as needed to control frequency to recall deployed Regulation. - Once the MW amount has ramped, the EBP amount will return to zero |
| 4 | WHEN: - RLC is restored; THEN: - Remove the Emergency Base Point flag, - Initiate Hotline call to cancel the Watch, - Notify Resource Operator to cancel MIS posting, - Notify Transmission Operator to cancel the Watch with TOs. Q#31 - Typical Hotline Script to Cancel Watch for RLC is Restored |
| Log | Log all actions. |
| ### LFC (AGC) Failure |  |
| NOTE | When LFC (AGC) is paused or suspended and RLC and SCED are functioning, then Regulation, RRS and EBP are not functioning. |
| 1 | IF: - LFC is not functioning as indicated by: - AGC is SUSPENDED or PAUSED OR - “Last AGC Cycle” time on Generation Area Status display is not updating; THEN: - Verify the status of RLC - If RLC is also failed, proceed to the next procedure “EMMS Failure” - If RLC is still functioning properly, - Contact Help Desk, - Continue with this procedure REFERENCE Display: EMP Applications>Generation Area Status>Nodal Operational Status>Resource Limits Data DETERMINE: - Which QSE has ample capacity to place on constant frequency control, THEN: - Direct selected QSE to go on constant frequency, - As time permits, issue electronic Dispatch Instruction, - Choose “OPERATE AT CONSTANT FREQUENCY” as the Instruction Type from QSE Level - Confirm with Market Participant that the electronic Dispatch Instruction was received. When issuing a VDI or when confirming the receipt of an electronic Dispatch Instruction ensure the use of three-part communication: - Issue the directive - Receive a correct repeat back - Give an acknowledgement - Place ERCOT AGC into ‘Monitor” mode. Typical Script to Direct a QSE on Constant Frequency for LFC Failure: “This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is directing you to go on constant frequency until further notice due to an LFC failure. The frequency bias to enter into your control system is [bias]. Please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.”If INCORRECT, repeat the process until the repeat back is correct.All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 2 | THEN: - Initiate the Emergency Notice Hotline call to QSEs - Notify Resource Operator to post the message on MIS Public, - Notify Transmission Operator to make Hotline call to TOs. Q#32 - Typical Hotline Script for Emergency Notice a QSE is on Constant Frequency for LFC Failure |
| 3 | MONITOR: - Frequency and capacity availability for QSE on constant frequency, AND/OR - The QSE on constant frequency notifies ERCOT of capacity issue; THEN: - Determine available capacity for SCED and enter an operator manual offset, OR if no SCED room - Request RUC Operator to decommit a Resource |
| 4 | WHEN: - ERCOT AGC Control is functioning properly; THEN: - Direct QSE to come off Constant Frequency by ending the electronic Dispatch Instruction, - Place ERCOT AGC back into “ON” mode, - Initiate Hotline to cancel the Emergency Notice to QSEs, - Notify Resource Operator to cancel the MIS posting, - Notify Transmission Operator to cancel the Emergency Notice with TOs. Typical Script to Direct QSE to End Constant Frequency for LFC Functioning: “This is ERCOT Operator [first and last name]. At [xx:xx], LFC is now functioning, ERCOT is directing you to end constant frequency. Please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. Q#33 - Typical Hotline Script to Cancel Emergency Notice for QSE on Constant Frequency for LFC Functioning: |
| Log | Log all actions. |
| ### EMMS (LFC and RLC/SCED) Failure |  |
| NOTE | Regulation, RRS, UDBP, BP, EBP, and manual offset not functioning. |
| 1 | LFC (AGC): - AGC is SUSPENDED or PAUSED, - “Last ACE crossing zero” time on the Generation Area Status page is not updating, - AGC operation adversely impacts the reliability of the Interconnection, - SCED and EMS are not functioning, - Problem cannot be resolved quickly RLC: - Process Status: RLC Down will be displayed in RED in the upper right hand corner of the RLC display - RLC (PI Alarm) will be flashing RED. REFERENCE Display: EMP Applications>Generation Area Status>Nodal Operational Status>Resource Limits Data DETERMINE: - Which QSE has ample capacity to place on constant frequency Control; THEN: - Direct the selected QSE to go on constant frequency - As time permits, issue an electronic Dispatch Instruction - Choose “OPERATE AT CONSTANT FREQUENCY” as the Instruction Type from QSE Level - Confirm with Market Participant electronic Dispatch Instruction received. When issuing a VDI or when confirming the receipt of an electronic Dispatch Instruction ensure the use of three-part communication: - Issue the directive - Receive a correct repeat back - Give an acknowledgement - Place ERCOT AGC into “Monitor” mode Typical Script to Direct a QSE on Constant Frequency for LFC/SCED Failure: “This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is directing you to go on constant frequency until further notice due to an LFC and SCED failure. The frequency bias to enter into your control system is [bias]. Please repeat this back to me. That is correct, thank you”. All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 2 | THEN: - Initiate the Emergency Notice Hotline call to QSEs, - Notify Resource Operator to post the message on MIS Public, - Notify Transmission Operator to make Hotline call to TOs Q#34 - Typical Hotline Script for Emergency Notice a QSE is on Constant Frequency for LFC and SCED failure: |
| 3 | MONITOR: - Frequency and Capacity availability for QSE on constant frequency, AND/OR - The QSE on Constant Frequency notifies ERCOT that they are having control issues; THEN: - Determine which QSE has the most available Capacity, - Issue a unit specific instructions to assist the QSE on Constant Frequency, - Choose “Other For Resource” as the Instruction Type |
| 4 | IF: - There is no longer any available capacity to issue unit specific deployments; THEN: - Request RUC Operator to commit a Resource |
| 5 | WHEN: - AGC and RLC is restored; THEN: - Direct QSE to come off constant frequency by ending VDI, - Place ERCOT AGC back into “ON” mode, - Cancel VDI(s) for additional generation, if issued, - Initiate Hotline to cancel Emergency Notice to QSEs, - Notify Resource Operator to cancel MIS posting, - Notify Transmission Operator to cancel Emergency Notice with TOs. Typical Script to Direct a QSE to end Constant Frequency for LFC Functioning, AGC/RLC Restored: “This is ERCOT Operator [first and last name]. At [xx:xx], LFC is now functioning, ERCOT is directing you to end constant frequency. Please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. Q#35 - Typical Hotline Script to Cancel Emergency Notice with LFC Functioning, SCED valid: |
| Log | Log all actions. |

## 3.4	Potential DCS Event

Procedure Purpose:  To meet NERC Recovery Criteria after a potential NERC Reportable DCS Event

| Protocol Reference | 6.5.7.6.2.2 (2) |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 2.2.4 (2) |  |  |  |
| NERC Standard | BAL-002-1 R1, R6 | IRO-005-3.1a R6 |  |  |

| Version: 1 | Revision: 11 | Effective Date: December 31, 2015 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NERC Recovery Criteria | Restore system frequency to the following limit within 15 minutes: - Scheduled Frequency if it was greater than or equal to scheduled Frequency prior to the disturbance, OR - Its pre-disturbance value if it was less than scheduled frequency prior to the disturbance. ERCOT shall fully restore the minimum Contingency Reserve requirement of ERCOT Region’s Largest Single Contingency (1375 MW) within 90 minutes. The 90 minute restoration period begins at the end of the Disturbance Recovery period which is when system frequency is restored as described above. ERCOT will restore Responsive Reserves to 2300 MW or greater, as soon as possible. |
| DCS | - A loss of Generation, equal to or greater than 1100 MW (consisting of a single generator or the total of multiple generators within 1 minute), or there is NO indication of a Generation loss and the magnitude of the event is determined to be greater than 1000 MW - Determine the magnitude of the event by using the “Raw ACE” tag, Analyze the change in this tag after a minimum of 30 seconds to avoid the initial overshoot. Example: If the “Raw ACE” pre-disturbance value is +150 MW, and post disturbance (30 seconds) value is -950 MW, then the total generation loss is 1100 MW. This constitutes a NERC Reportable DCS Event. - It can be assumed that a potential NERC Reportable DCS Event has occurred |
| NOTE | The steps below will need to happen quickly, let phones ring, or if available, another desk will take the calls. |
| 1 | IF: - ERCOT experiences a low frequency disturbance; THEN: - Immediately check to ensure that SCED sees the units correct telemetry (HSL of zero or Resource Status of “off”), Contact the QSE(s) if telemetry needs to be changed, - If SCED does not automatically execute within 60 seconds of the event, manually execute a SCED run, - Enter a manual off-set as necessary. |
| 2 | IF: - Frequency dropped below 59.7 Hz; THEN: - Load Resources have deployed on UFR. |
| NOTE | If Load Resources are deployed it may become necessary to periodically execute SCED manually and/or use the manual offset to control frequency. |
| 3 | WHEN: - System frequency has been restored; THEN: - Make Hotline call to QSEs to recall Load Resources. Q#36 - Typical Hotline Script to Recall Load Resources After a Frequency Event |
| PRC Below 2300 | IF: - PRC < 2300 MW; THEN: - Implement EEA (see section 5.3). |
| Log | Log all actions. |

## 3.6	Monitor and Control Time Error Correction

Procedure Purpose:  This procedure will establish the standard for implementing time error correction.  ERCOT ISO is the Reliability Coordinator and Balancing Authority that implements and terminates ERCOT Time Corrections in accordance with ERCOT Protocols and Operating Guides.  ERCOT Reliability Coordinator is the Interconnection Time Monitor within the ERCOT Interconnection.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 2.2.1(3)(c)(vi) | 2.2.9.1 | 2.2.9.2 |  |
| NERC Standard | BAL-004-0 R1, R2, R3, R4 |  |  |  |

| Version: 1 | Revision: 7 | Effective Date: December 31, 2015 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Requirements | - When time error is equal to or greater than +/- 30 seconds, ERCOT may initiate a time correction. - Time Error Corrections normally start and end on the hour or half-hour. - The Time Error Correction will be ended when the error is less than +/- 27.0 seconds. - The time correction may be postponed if it is determined that load patterns in the immediate future will result in the desired time correction - Time Error Correction Notifications shall be labeled alphabetically on a monthly basis (A-Z). In the succeeding month, the first Time Error Correction will revert back to “A”. |
| Log | Log the start time, stop time, Time Error ID letter, time error, and Frequency Offset for each start and termination. |
| Initiating Time Error Correction | IF: - Time error is greater than +/- 30 seconds; THEN: - Start Time Error Correction Schedule, - Enter the appropriate Time Error ID letter, - Enter the frequency offset using – 0.02 for fast time correction (59.98 Hz) or +0.02 for slow time correction (60.02 Hz), - Enter a Start Time later than the current time AND enter a Stop Time later than the scheduled start time, - Before starting the Time Error, notify the QSEs via a Hotline call of the start time and frequency offset, - Log in the Operator’s Log start time, stop time, Time Error ID letter, time error, and frequency offset for each start and termination. Q#37 - Typical Hotline Script for Time Error Correction |
| NOTE | If a Time Error Correction is prematurely terminated or a scheduled Time Error Correction is cancelled for reliability considerations, log all actions taken and wait at least one hour between sending the termination and re-initiation notices. |
| Terminating Time Error Correction | Monitor the Time Error until it reaches an acceptable value (+/- 27.0 seconds) - Time Error Correction may be terminated after five hours, or after any hour it has reached an acceptable value of +/- 27.0 seconds. - Notify QSEs using the Hotline before ending the time correction. Q#38 - Typical Hotline Script to End Time Error Correction |

## 3.7	Responding to North to Houston Interface Issues

Procedure Purpose:  Deployment/Termination of Non-Spin Reserve Service for Congestion Management as requested by the Transmission Operator.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.2.4(1) | 4.5.2(2)(b) |  |  |
| NERC Standard | EOP-001-2.1b R2.2, R3, R3.1, R3.2, R4 | EOP-003-2 R8 | IRO-006-TRE-1 R1, R2 | IRO-009-2 R2, R3, R4 |
|  | TOP-002-2.1b R10 | TOP-004-2 R1 |  |  |

| Version: 1 | Revision: 6 | Effective Date: December 31, 2015 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Issue Watch & Deploy Non-Spin | WHEN: - Notified by the Transmission Operator that Non-Spin needs to be deployed in the Houston area for the North-Houston Interface; THEN: - Using the hotline, issue a Watch, - Resource Operator will deploy the Non-Spin Q#39 - Typical Hotline Script for Watch/Deploy Non-Spin for N-H Interface |
| NOTE | To the extent that ERCOT deploys a Load Resource that has chosen a block deployment option, ERCOT shall either deploy the entire offer or, if only partial deployment is possible, skip the offer by the Load Resource with the block deployment option and proceed to deploy the next available Resource. |
| Issue Emergency Notice & Deploy Load Resources | WHEN: - Notified by the Transmission Operator to deploy Load Resources in the Houston area for the North-Houston Interface; THEN: - Using the hotline, issue the Emergency Notice Q#40 - Typical Hotline Script for Emergency/ Deploy Load Resources for N-H Interface |
| Recall Load Resources | WHEN: - Notified by the Transmission Operator to recall Load Resources in the Houston area for the North-Houston Interface; THEN: - Using the hotline, cancel the Emergency Notice, Q#41 - Typical Hotline Script to Cancel Emergency Notice for N-H Interface / Recall Load Resources: |
| Recall Non-Spin | WHEN: - Notified by the Transmission Operator to recall Non-Spin in the Houston area for the North-Houston Interface; THEN: - Using the hotline, cancel the Watch, Q#42 - Typical Hotline Script to Cancel Watch for N-H Interface / Recall Non-Spin |
| Log | Log all actions. |

# 3.9	Unannounced Constant Frequency Control Testing

Procedure Purpose: This procedure provides direction and guidelines for conducting unannounced testing to verify a QSE’s capability to operate in CFC mode.  Only QSEs with at least 350 MW of spinning reserve room will be tested.  QSEs shall be tested at least every three years.

| Protocol Reference | 6.6.9 |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 2.2.4.3 |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 2 | Effective Date: December 31, 2015 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - Testing will be coordinated with staff from Operations Analysis, they will select the QSE to test - EMMS Production personnel will be in the Control Room to take the EMS off AGC - The frequency bias can be found on the Generation Area Status display - The Constant Frequency Control Testing Document can be found in Section 2.11 of the Desktop Guide Real Time Desk. |
| START CFC Test | Typical Script for Constant Frequency Control Test: “This is ERCOT operator [first and last name]. At [time], ERCOT is conducting an unannounced test with [QSE] to test your ability to operate on constant frequency control mode. The frequency bias to enter into your control system is [bias]. You have five minutes to switch to CFC mode then hold for 15 minutes. I will give another call when you can return to normal operation. [QSE] please repeat this back to me. That is correct, thank you.” |
| END CFC Test | Typical Script to End Constant Frequency Control Test: “This is ERCOT operator [first and last name]. At [time], ERCOT is ending the unannounced constant frequency control test with [QSE]; please change your control mode back to normal. I will send you an electronic Dispatch Instruction that you will need to acknowledge. [QSE] please repeat this back to me. That is correct, thank you.” |
| ISSUE Electronic Dispatch Instruction | Issue electronic Dispatch Instruction: - QSE Level - Instruction Type: Operate at Constant Frequency - Confirm with Market Participant electronic Dispatch Instruction received. When issuing a VDI or when confirming the receipt of an electronic Dispatch Instruction ensure the use of three-part communication: - Issue the directive - Receive a correct repeat back - Give an acknowledgement |
| LOG | Make log entry |

### 3.10	Geomagnetic Disturbance Notification

Procedure Purpose:  To provide notification and increase situational awareness when a K-7 and greater or G3 and greater GMD storm has entered an Alert and is advancing or decreasing.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.7 |  |  |  |
| NERC Standard | EOP-010-1 | IRO-005-3.1a R3 |  |  |

| Version: 1 | Revision: 3 | Effective Date: December 31, 2015 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - The Geomagnetic Disturbance Reference Document can be found in Section 2.13 of the Common to Multiple Desks Desktop Reference Guide. - An Advisory is issued when a GMD Alert of K-7 or higher is issued, however the Advisory will not be canceled until the GMD Warning is canceled. |
| 1 | WHEN: - Notified by the Shift Supervisor that an Alert from the Space Weather Prediction Center has been issued for a K-7 and greater or G3 and greater; THEN: - Issue an Advisory by making a Hotline call to QSEs Q#43 - Typical Hotline Script for Advisory for GMD Alert: |
| K Level Increases / Decreases | IF: - Notified by the Shift Supervisor that an Alert from the Space Weather Prediction Center has been increased or decreased for a K-7 and greater or G3 and greater; THEN: - Making a Hotline call to QSEs Q#44 - Typical Hotline Script for GMD K-Index Level Increase / Decrease |
| Issues | IF: - Any QSE report any issues that could be related to the GMD event; THEN: - Coordinate an action plan if necessary, - Report issues to Shift Supervisor |
| Cancel | WHEN: - Notified by the Shift Supervisor that the GMD Warning has expired; THEN: - Cancel the Advisory by making a Hotline call to QSEs Q#45 - Typical Hotline Script to Cancel Advisory for GMD |
| Log | Log all actions. |

## 5.1	Market Notices

Procedure Purpose: Guidelines for issuing Emergency Conditions and the four possible levels: Operating Condition Notices (OCN), Advisories, Watches, and Emergency Notices.

| Protocol Reference | 6.3.3 | 6.5.9.3 | 6.5.9.3.1 | 6.5.9.3.2 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.3.3 | 6.5.9.3.4 |  |  |
| Guide Reference | 4.2.1 | 4.2.2 | 4.2.3 | 4.2.4 |
| NERC Standard | EOP-001-2.1b R3.1 |  |  |  |

| Version: 1 | Revision: 21 | Effective Date: December 31, 2015 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### OCN |  |
| NOTE | Consider the severity of the potential Emergency Condition. The severity of the Emergency Condition could be limited to an isolated local area, or the condition might cover large areas affecting several entities, or the condition might be an ERCOT-wide condition potentially affecting the entire ERCOT System. |
| 1 | As directed by the Shift Supervisor or when appropriate, issue an Operating Condition Notice (OCN). The OCN can be issued for any of the following reasons or to obtain additional information from Market Participants. - There is a projected reserve capacity shortage that could affect reliability and may require more Resources - When extreme cold weather is forecasted approximately 5 days away - When extreme hot weather is forecasted approximately 5 days away - When an approaching Hurricane / Tropical Storm is approximately 5 days away - Unplanned transmission Outages that may impact reliability - When adverse weather conditions are expected, ERCOT may confer with TOs and QSEs regarding the potential for adverse reliability impacts and contingency preparedness |
| ### Advisory |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue an Advisory. The Advisory can be issued for any of the following reasons or to obtain additional information from Market Participants. - When an approaching Hurricane / Tropical Storm is approximately 3 days away - When extreme cold weather is forecasted approximately 3 days away - When extreme hot weather is forecasted approximately 1 to 3 days away - When conditions are developing or have changed and more Ancillary Services will be needed to maintain current or near-term reliability - ERCOT may exercise its authority to increase Ancillary Service requirements above the quantities originally specified in the Day-Ahead Market in accordance with ERCOT Procedures - When extreme weather or conditions require more lead-time than the normal Day-Ahead Market allows - Transmission system conditions are such that operations within security criteria are not likely or possible due to Forced Outages or other conditions unless a CMP exists - Loss of communications or a control condition is anticipated or significantly limited - ERCOT may require information from QSEs representing Resources regarding the Resources’ fuel capabilities. Requests for this type of information shall be for a time period of no more than seven days from the date of the request |
| ### Watch |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue a Watch. The Watch can be issued for any of the following reasons or to obtain additional information from the Market Participants. - A projected reserve capacity shortage is projected with no market solution available that could affect reliability - When an approaching Hurricane / Tropical Storm is approximately 1 day away - When extreme cold weather is projected for next day or current day - When extreme hot weather is projected for next day or current day - Conditions have developed that require additional Ancillary Services in the Operating Period - Insufficient Ancillary Services or Energy Offers in the DAM or in SASM - Market-based congestion management techniques embedded in SCED will not be adequate to resolve transmission security violations - Forced Outages or other abnormal operating conditions have occurred, or may occur that would require ERCOT to operate with active violations of security criteria as defined in the Operating Guides unless a CMP exists - ERCOT varies from timing requirements or omits one or more Day-Ahead or Adjustment Period and Real-Time procedures. - ERCOT varies from timing requirements or omits one or more scheduling procedures in the Real-Time process. - The SCED process fails to reach a solution, whether or not ERCOT is using one of the measures in Failure of the SCED Process. - The need to immediately procure Ancillary Services from existing offers - ERCOT may instruct TOs to reconfigure transmission elements as necessary to improve the reliability of the system - ERCOT may require information from QSEs representing Resources regarding the Resources’ fuel capabilities. Requests for this type of information shall be for a time period of no more than seven days from the date of the request |
| ### Emergency Notice |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue an Emergency Notice. The Emergency Notice can be issued for any of the following reasons or to obtain additional information from Market Participants. - Loss of Primary Control Center functionality - Load Resource deployment for North-Houston voltage stability - ERCOT cannot maintain minimum reliability standards (for reasons including fuel shortages) during the Operating Period utilizing every Resource practically obtainable from the market - Immediate action cannot be taken to avoid or relieve a Transmission Element operating above its Emergency Rating - ERCOT forecasts an inability to meet applicable Reliability Standards and has exercised all other reasonable options - A transmission condition has been identified that requires emergency energy from any of the DC-Ties or curtailment of schedules - The Transmission Grid is such that a violation of security criteria as defined in the Operating Guides presents the threat of uncontrolled separation or cascading outages, large-scale service disruption to Load (other than Load being served from a radial transmission line) and/or overload of Transmission Elements, and no timely solution is obtainable through SCED or CMPs - When extreme cold weather is beginning to have an adverse impact on the System - When extreme hot weather is beginning to have an adverse impact on the System - When Hurricane / Tropical Storm is in the ERCOT Region and is beginning to have an adverse impact on the System |
| ### Operating Condition Script |  |
| Hotline | Communications must specify the severity of the situation, the area affected, the areas potentially affected, and the anticipated duration of the Emergency Condition. Notify QSEs: Q#46 - Typical Hotline Script for Operating Condition [OCN/Advisory/Watch/Emergency] |
| Post | - All notices must be posted on MIS Public. - For “free form” messages, the “Notice Priority” will be specified as follows: - Operational Information/OCN type messages – low priority - Advisory/Watch type messages – medium priority - Emergency type messages – high priority |
| Hotline Cancellation | Q#47 - Typical Hotline Script to Cancel Operating Condition [OCN/Advisory/Watch/Emergency] |
| Log | Log all actions. |
| ### Specific Scripts for Transmission Operator [State Estimator/RTCA/VSAT] |  |
| NOTE | - At times, the Transmission operator takes the lead on the issuance of Hotline calls for specific procedures they have. The following scripts are to help guide you when specific procedures don’t exist for the Real-Time operator. |
| State Estimator/ RTCA Not Solved In 30 MIN | - Q#48 - Typical Hotline Script for Advisory for State Estimator / RTCA not solved in 30 Min - Q#49 - Typical Hotline Script to Cancel Advisory for State Estimator / RTCA now solving |
| VSAT Not Solved In 30 MIN | Q#50 - Typical Hotline Script for Advisory for VSAT not solved in 30 Min: Q#51 - Typical Hotline Script Cancel Advisory for VSAT now solving |
| Qualifying Facility Directed to Operate below LSL | Q#52 - Typical Hotline Script for Emergency Notice for directing Qualifying Facility to operator offline/below LSL Q#53 - Typical Hotline Script to Cancel Emergency Notice for Qualifying Facility to operate offline/below LSL |
| New GTC | Q#54 - Typical Hotline Script for OCN for a new Generic Transmission Constraint |
| Transmission Watch | Q#55 - Typical Hotline Script for Transmission Watch for Post-Contingency Overload Q#56 - Typical Hotline Script Cancel Transmission Watch for Post-Contingency Overload |

## 5.2	Notifications for Diminishing Reserves

Procedure Purpose:  Monitor the Physical Responsive Capability (PRC) for the purpose of providing advance notice of diminishing Responsive Reserve.  Steps within this procedure are intended to keep ERCOT from progressing into EEA.

| Protocol Reference | 3.17.3(2) | 6.5.7.6.2.3 | 6.5.9.4.1(d) | 6.5.9.4.1(e) |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.5.3.1(d) | 4.5.3.1(e) |  |  |
| NERC Standard | BAL-002-1 R1 | EOP-002-3.1 R2, R4, R6.1, R6.2, R8 | IRO-005-3.1a R1.4, R1.5, R4 |  |

| Version: 1 | Revision: 13 | Effective Date: December 31, 2015 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - ERCOT, at Management’s discretion, may issue an appeal through the Public News Media for voluntary energy conservation at any time. |
| ### Advisory |  |
| Issue Advisory | IF: - PRC < 3000 MW; THEN: - Using the Hotline, issue an Advisory, AND - Instruct the Resource Operator to post a message on MIS Public. Q#1 - Typical Hotline Script for Advisory for PRC <3000 MW |
| Cancel Advisory | WHEN: - PRC > 3000 MW; THEN: - Using the Hotline, cancel the Advisory, AND - Instruct the Resource Desk Operator to cancel MIS message. Q#2 - Typical Hotline Script to Cancel Advisory for PRC <3000 MW |
| Log | Log all actions. |
| ### Watch |  |
| Issue Watch | IF: - PRC < 2500 MW, THEN: - Using the Hotline, issue a Watch, - Instruct the Resource Desk Operator to deploy Off-Line Non-Spin, AND - Post a message on MIS Public. Q#3 - Typical Hotline Script for Watch for PRC <2500 MW |
| Cancel Watch | WHEN: - PRC > 2800 MW; THEN: - Using the Hotline, cancel the Watch, - Instruct the Resource Desk Operator to recall Off-Line Non-spin, AND - Cancel MIS posting. Q#4 - Typical Hotline Script Cancel Watch for PRC < 2500 MW |
| Log | Log all actions. |

## 5.3	Implement EEA Levels

Procedure Purpose:  To provide for maximum possible continuity of service while maintaining the integrity of the ERCOT System to reduce the chance of Cascading Outages.

| Protocol Reference | 6.5.7.6.2.2(1)(b) & (12) | 6.5.9.3.4(6) | 6.5.9.4 | 6.5.9.4.2 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.4.3 |  |  |  |
| Guide Reference | 4.5.3 | 4.5.3.1 | 4.5.3.2 | 4.5.3.3 |
|  | 4.5.3.4 |  |  |  |
| NERC Standard | EOP-001-2.1b R3.1, R3.2, R3.3, R4 | EOP-002-3.1 R2, R4, R6.1, R6,2, R6.4, R6.6 | TOP-001-1a R8 |  |

| ### Version: 1 | Revision: 20 | Effective Date: December 31, 2015 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - IF steady state system frequency falls < 59.8 Hz, ERCOT CAN immediately implement EEA 3. - IF steady state system frequency falls < 59.5 Hz, ERCOT SHALL immediately implement EEA 3. |
| NOTE | Confidentiality requirements regarding Transmission Operations and System Capacity information will be lifted, as needed to restore reliability. |
| ERS-30 | ERS with a thirty-minute ramp period. |
| ERS-10 | ERS with a ten-minute ramp period. |
| WS ERS | Weather Sensitive ERS are only available June – September during Business Hour (BH2) and Business Hour 3 (BH3) which are only on business days. |
| TCEQ | When increased generation is requested during EEA events, Texas Commission on Environmental Quality (TCEQ) will exercise enforcement discretion for exceedances of emission limits as well as operational limits for power generating plants for Generators who exceed air permit limits in order to maximize generation for the duration of the EEA event. ERCOT General Council will send out a Market Notice each time ERCOT enters into an EEA with this reminder. |
| Media Appeal | When an ERCOT-wide appeal through the public news media for voluntary energy conservation is made. Notify the QSEs by hotline. |
| ### Implement EEA Level 1 |  |
| EEA 1 PRC<2300 | IF: - PRC < 2300 MW and is not projected to be recovered above 2300 MW within 30 minutes without the use of EEA Level 1; THEN: - Select the activate EEA flag in EMS, - Maintain steady state system frequency near 60 Hz and maintain PRC above 1750 MW, - Determine whether system conditions warrant the deployment of ERS-30. Refer to the ERS tab on the Real-Time Values Spreadsheet for amounts in each business hours and number of times deployed: - Consider the peak hour, deploy all ERS-30 if needed to prevent PRC from falling < 1750 MW, - When deploying the ERS-30, also deploy the weather-sensitive ERS if available for the current business hour. - Using the Hotline, notify all QSEs to implement EEA 1. Q#5 - Typical Hotline Script for EEA1 NOT deploying ERS OR IF: - Deploying ERS, the Resource Operator must complete the XML deployment of the ERS before the Hotline call is made. - Deploy all ERS Resources as a single group - If it is June – September and during Business hour BH2 or BH3 on a business day, use this script. Q#6 - Typical Hotline Script for EEA1 deploying ERS-30 / ERS-30 including Weather Sensitive |
| RRS Release to HASL | REVIEW REFERENCE DISPLAY: EMP Applications>Generation Area Status>Nodal Operations Status>Responsive Reserve Service Summary Data IF: - PRC < 2000 MW; THEN: - Activate Manual Responsive Reserve - Manually deploy all remaining RRS |
| Log | Log all actions. |
| ### Implement EEA Level 2 |  |
| EEA 2 PRC<1750 | IF: - PRC < 1750 MW or unable to maintain system frequency at a minimum of 59.91 Hz and is not projected to be recovered above 1750 MW within 30 minutes without the use of EEA Level 2; THEN: - Verify with Shift Supervisor a public appeal has been issued - Maintain steady state system frequency at a minimum of 59.91 Hz and maintain PRC above 1000 MW, - Determine when system conditions require the deployment of Load Resources and/or ERS Resources (Do Not forget the WS ERS if available): - Deploy ERS-30 if not already done in EEA 1 - Deploy ERS-10 - Deploy Load Resources Group 1 and/or 2 - Using the Hotline, notify all QSEs to implement EEA 2 and any measures associated with EEA 1, if not already implemented. |
| ERS Resources | IF: - Deploying ERS, the Resource Operator must complete the XML deployment of the ERS before the Hotline call is made. - Deploy all ERS Resources as a single group. - If it is June – September and during Business Hour BH2 or BH3 on a business day Q#7 - Typical Hotline Script for EEA2 deploying ERS-10 / ERS-30 / both ERS-10 and ERS 30 / ERS-30 including Weather Sensitive ERS / ERS-10 and ERS-30 including Weather Sensitive |
| Load Resources | IF: - Deploying Load Resources, the Resource Operator must complete the XML deployment of the Load Resources before the Hotline call is made. - PRC < 1750 MW, deploy Group 1 - PRC < 1375 MW, deploy both Groups 1 and 2 simultaneously Q#8 - Typical Hotline Script for EEA2 deploying Load Resources Group 1 / Load Resources Group 1 and 2 |
| When ERS Business Hours Change | IF: - ERS Resources are deployed and the Business Hour is changing - If it is June – September and during Business Hour BH2 or BH3 on a business day; THEN: - After Resource Operator has completed the XML deployment, make the QSE hotline call Q#9 - Typical Hotline Script for EEA2 deploying ERS-10 / ERS-30 / both ERS-10 and ERS-30 / ERS-10, ERS-30 including Weather Sensitive Script |
| NOTE | - All Load Resources, 10 MIN ERS, and 30 MIN ERS must be deployed before firm load |
| Media Appeal | - Unless already in effect, verify with the Shift Supervisor that the communications group has issued an appeal through the public news media for voluntary energy conservation, - Notify QSEs, via Hotline, that a media appeal for conservation is in effect. Q#10 - Typical Hotline Script for Media Appeal |
| Log | Log all actions. |
| ### Implement EEA Level 3 |  |
| EEA3 Unable to Maintain 59.8 Hz | IF: - PRC < 1000 MW or unable to maintain system frequency at 59.80 Hz and is not projected to be recovered above 1000 MW within 30 minutes without the use of EEA Level 3; THEN: - Using the Hotline, notify all QSEs to implement EEA 3 and any measures associated with EEA 1 and 2, if not already implemented. Q#11 - Typical Hotline Script for EEA3 |
| When ERS Business Hours Change | IF: - ERS Resources are deployed and the Business Hour is changing - If it is June – September and during Business Hour BH2 or BH3 on a business day; THEN: - After Resource Operator has completed the XML deployment, make the QSE hotline call Q#12 - Typical Hotline Script for EEA3 deploying ERS-10 / ERS-30 / both ERS-10 and ERS-30 / ERS-10, ERS-30 including Weather Sensitive |
| Log | Log all actions. |

## 5.4	Restore EEA Levels

Procedure Purpose:  To restore the ERCOT grid to normal state as system conditions warrant while recovering from an EEA event.

| Protocol Reference | 6.5.9.4.1(e) | 6.5.9.4(3)(g) | 6.5.9.4.3 |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.5.3.5 |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 16 | Effective Date: December 31, 2015 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Restore Firm Load |  |
| RESERVES | 1375 MW of PRC must be restored within 90 minutes. |
| 1 | IF: - Sufficient Regulation Service exists to control to 60 Hz, AND - PRC – Regulation Up Responsibility is ≥ 1375 MW for the last 15 minutes; THEN: - Using the Hotline, notify all QSEs of firm load restoration. Q#13 - Typical Hotline Script for Restoring Firm Load |
| ### Move From EEA Level 3 to EEA Level 2 |  |
| 1 | IF: - Sufficient Regulation Service exists to control to 60 Hz, AND - PRC is ≥ 1750 MW, AND - All firm load has been instructed to be restored; THEN: - Using the Hotline, notify all QSEs of the reduction from EEA 3 to EEA 2 - Coordinate with the Resource Desk and recall Load Resources Q#14 - Typical Hotline Script for EEA3 to EEA2, recall Load Resources |
| Log | Log all actions. |
| NOTE | Once Load Resources are recalled, they have 3 hours to return to service. |
| ### Move From EEA Level 2 to EEA Level 1 |  |
| 1 | IF: - The system can maintain PRC ≥ 2300 MW, AND - All Load Resources have been instructed to be restored; THEN: - Using the Hotline, notify all QSEs of the reduction from EEA 2 to EEA 1 - Coordinate with the Resource Desk and recall the 10 MIN and/or 30 MIN, including the weather-sensitive ERS Resources. Q#15 - Typical Hotline Script for EEA2 to EEA1 recall ERS |
| NOTE | Once ERS Resources are recalled, they have 10 hours to return to service. |
| ### Move From EEA Level 1 to EEA 0 |  |
| 1 | IF: - The system can maintain PRC ≥ 2300 MW, AND - All uncommitted units secured in EEA 1 can be released, AND - Emergency energy from the DC Ties is no longer needed; THEN: - Uncheck the EEA flag in EMS and make inactive, - Using the hotline, notify all QSEs of the termination of EEA. Q#16 - Typical Hotline Script for Terminate EEA |
| ### Cancel Watch |  |
| 1 | WHEN: - PRC is ≥ 2800 MW, AND - Non-Spin has been recalled; THEN: - Cancel Watch Q#17 - Typical Hotline Script to Cancel Watch for PRC < 2500 MW |

## 5.5	Restoration of Primary Control Center Functionality

Procedure Purpose: To be performed once the Real-Time Operator has arrived at ACC.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| ### Version: 1 | Revision: 6 | Effective Date: December 31, 2015 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | Before normal operation can be restored, be sure to communicate with the other desks to determine the current state of the grid and any communications that may have taken place with Market Participants. |
| Restoring Frequency Control | WHEN: - SCED is functional; THEN: - Remove the QSE that was directed on constant frequency by ending the VDI. - Put ERCOT AGC into “ON” mode. |
| Return to Normal QSE Notification | When ready to resume normal operations: - Check with RUC Operator on desk status to include in hotline call if appropriate - Place the following Hotline call to the QSEs: - Q#57 - Typical Hotline Script to Cancel Emergency Notice and Restore primary control center: |
| Log | Log all actions. |

## 6.1	Hurricane/Tropical Storm

Procedure Purpose: To ensure ERCOT is prepared for an approaching Hurricane/Tropical Storm

| Protocol Reference | 6.3.2(3)(a)(ii) | 6.5.9.3(2)&(3) | 6.5.9.3.1(4) | 6.5.9.3.2(4) |
| --- | --- | --- | --- | --- |
|  | 6.5.9.3.3(6) | 6.5.9.3.4(1) |  |  |
| Guide Reference | 4.2.1 | 4.2.2 | 4.2.3 | 4.2.4 |
| NERC Standard | IRO-005-3.1a R1.10 |  |  |  |

| Version: 1 | Revision: 6 | Effective Date: December 31, 2015 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | Hurricane / Tropical Storm notifications are called when there is a probability of landfall in the ERCOT Region. (http://www.nhc.noaa.gov) |
| OCN | When an approaching Hurricane / Tropical Storm is approximately 5 days away. Using the Hotline, issue an OCN to all QSEs: Q#58 - Typical Hotline Script for OCN for Hurricane/Tropical Storm |
| Advisory | When an approaching Hurricane / Tropical Storm is approximately 3 days away. Using the Hotline, issue an Advisory to all QSEs: Q#59 - Typical Hotline Script for Advisory for Hurricane/Tropical Storm |
| Watch | When approaching Hurricane / Tropical Storm is 1 day away. Using the Hotline, issue a Watch to all QSEs: Q#60 - Typical Hotline Script for Watch for Hurricane/Tropical Storm |
| Emergency Notice | When Hurricane / Tropical Storm is in the ERCOT Region and is beginning to have an adverse impact on the ERCOT System. Using the Hotline, issue an Emergency Notice to all QSEs: Q#61 - Typical Hotline Script for Emergency Notice for Hurricane/Tropical Storm |
| Post | Coordinate with the Transmission & Security Operator for the posting of the notices on MIS Public. |
| Cancel Posting | Coordinate with the Transmission & Security Operator for the cancelation of the postings on MIS Public. |
| Log | Log all actions. |

## 6.2	Extreme Cold Weather

Procedure Purpose: To ensure ERCOT and Market Participants are prepared for extreme cold weather operations.

| Protocol Reference | 6.3.2(3)(a)(ii) | 6.5.9.3(2)&(3) | 6.5.9.3.1(4) | 6.5.9.3.2(4) |
| --- | --- | --- | --- | --- |
|  | 6.5.9.3.3 (6) | 6.5.9.3.4 (1) |  |  |
| Guide Reference | 4.2.1 | 4.2.2 | 4.2.3 | 4.2.4 |
| NERC Standard | EOP-001-2.1b R2.2 | IRO-005-3.1a R1.10 |  |  |

| Version: 1 | Revision: 12 | Effective Date: December 31, 2015 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - Extreme cold weather notifications will be issued when temperatures or wind chill is forecasted to be below freezing for sustained periods and may abnormally impact load levels or generation availability - For such events, additional reserves may be necessary |
| OCN | When approaching extreme cold weather is approximately 5 days away, using the Hotline issue an OCN to all QSEs: Q#62 - Typical Hotline Script for OCN for Extreme Cold Weather |
| Advisory | When approaching extreme cold weather is approximately 3 days away, using the Hotline issue an Advisory to all QSEs: Q#63 - Typical Hotline Script for Advisory for Extreme Cold Weather |
| Watch | When approaching extreme cold weather is approximately 1 day away and concerns exists to escalate the notice, using the Hotline issue a Watch to all QSEs: Q#64 - Typical Hotline Script for Watch for Extreme Cold Weather |
| Emergency Notice | When extreme cold weather has arrived and is beginning to have an adverse impact on the system, using the Hotline issue an Emergency Notice to all QSEs: Q#65 - Typical Hotline Script for Emergency Notice for Extreme Cold Weather |
| Post | Coordinate with the Transmission & Security Operator for the posting of the notices on MIS Public. |
| Cancel Posting | Coordinate with the Transmission & Security Operator for the cancelation of the postings on MIS Public. |
| Log | Log all actions. |

## 6.3	Extreme Hot Weather

Procedure Purpose: To ensure ERCOT and Market Participants are prepared for Extreme Hot weather operations.

| Protocol Reference | 6.3.2(3)(a)(ii) | 6.5.9.3(2)&(3) | 6.5.9.3.1(4) | 6.5.9.3.2(4) |
| --- | --- | --- | --- | --- |
|  | 6.5.9.3.3 (6) | 6.5.9.3.4 (1) |  |  |
| Guide Reference | 4.2.1 | 4.2.2 | 4.2.3 | 4.2.4 |
| NERC Standard | EOP-001-2.1b R2.2 | IRO-005-3.1a R1.10 |  |  |

| Version: 1 | Revision: 10 | Effective Date: December 31, 2015 |
| --- | --- | --- |

| Step |  | Action |
| --- | --- | --- |
| NOTE |  | Extreme Hot weather notifications are issued when: Temperatures are forecasted to be 103°F or above in the North Central and South Central weather zones. – OR – Temperatures are forecasted to be 94°F or above in the North Central and South Central weather zones during the following months (October – May). |
| OCN |  | When extreme hot weather is forecasted approximately 5 days away. using the Hotline issue an OCN to all QSEs: Q#66 - Typical Hotline Script for OCN for Extreme Hot Weather |
| Advisory |  | When extreme hot weather is forecasted approximately 1 to 3 days away, using the Hotline issue an Advisory to all QSEs: Q#67 - Typical Hotline Script for Advisory for Extreme Hot Weather |
| Watch |  | When extreme hot weather is projected for next day or current day and ERCOT has reliability concerns, using the Hotline issue a Watch to all QSEs: Q#68 - Typical Hotline Script for Watch for Extreme Hot Weather |
| Emergency Notice |  | When extreme hot weather has arrived and is beginning to have an adverse impact on the ERCOT System, using the Hotline issue an Emergency Notice to all QSEs: Q#69 - Typical Hotline Script for Emergency Notice for Extreme Hot Weather |
| Post | Coordinate with the Transmission & Security Operator for the posting of the notices on MIS Public. |  |
| Cancel Posting | Coordinate with the Transmission & Security Operator for the cancelation of the postings on MIS Public. |  |
| Log | Log all actions. |  |

## 6.4	Other Significant Weather Events

Procedure Purpose:  Monitor severe weather conditions for the ERCOT Region and adjacent NERC regions which can arise with little or no warning that could possibly impact the ERCOT Grid.

| Protocol Reference | 6.3.2(3)(a)(ii) | 6.5.9.3(2)&(3) | 6.5.9.3.1(4) | 6.5.9.3.2(4) |
| --- | --- | --- | --- | --- |
|  | 6.5.9.3.3 (6) | 6.5.9.3.4 (1) |  |  |
| Guide Reference | 4.2.1 | 4.2.2 | 4.2.3 | 4.2.4 |
| NERC Standard | IRO-005-3.1a R1.10 |  |  |  |

| Version: 1 | Revision: 9 | Effective Date: December 31, 2015 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | Significant weather events can consist of, but are not limited to the following: - Tornados - Strong straight line winds - Hail - Severe lightning - Flooding - Freezing precipitation - Hard freeze |
| OCN/ Advisory/ Watch | When a significant weather event that could or does impact the ERCOT Region, make the proper notification. Using the Hotline, issue a notification to all QSEs: Q#70 - Typical Hotline Script for OCN/Advisory/Watch for other Weather Events |
| Post | Coordinate with the Transmission & Security Operator for the posting of the notices on MIS Public. |
| Cancel Posting | Coordinate with the Transmission & Security Operator for the cancelation of the postings on MIS Public. |
| Log | Log all actions. |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Frosch, Hartmann, Stone, and Barcalow | Prepares | November 10 , 2010 |
| Frosch and Hartmann | Procedure writers and editors | November 29, 2010 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2010 |
| Frosch, Foster and Hartmann | Procedure writers and editors | January 3, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 26, 2011 |
| Frosch and Hartmann | Procedure writers and editors | March 23, 2011 |
| Frosch and Hartmann | Procedure writers and editors | April 20, 2011 |
| Frosch and Hartmann | Procedure writers and editors | June 6, 2011 |
| Frosch and Hartmann | Procedure writers and editors | July 18, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 1, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 30, 2011 |
| Frosch and Hartmann | Procedure writers and editors | September 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | October 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 16, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | April 25, 2012 |
| Frosch and Hartmann | Procedure writers and editors | May 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | May 30, 2012 |
| Barcalow, Frosch and Hartmann | Procedure writers and editors | July 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | August 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | October 26, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 26, 2013 |
| Frosch and Hartmann | Procedure writers and editors | May 28, 2013 |
| Frosch and Hartmann | Procedure writers and editors | July 8, 2013 |
| Frosch and Hartmann | Procedure writers and editors | August 7, 2013 |
| Frosch and Hartmann | Procedure writers and editors | September 25, 2013 |
| Frosch and Hartmann | Procedure writers and editors | December 11, 2013 |
| Frosch and Hartmann | Procedure writers and editors | December 20, 2013 |
| Frosch, Gaddy, Hartmann and Solis | Procedure writers and editors | April 1, 2014 |
| Frosch, Gaddy and Hartmann | Procedure writers and editors | May 27, 2014 |
| Frosch and Hartmann | Procedure writers and editors | July 29, 2014 |
| Frosch and Hartmann | Procedure writers and editors | September 29, 2014 |
| Drummond, Frosch and Hartmann | Procedure writers and editors | December 10, 2014 |
| Frosch and Thompson | Procedure writers and editors | December 19, 2014 |
| Frosch and Hartmann | Procedure writers and editors | February 25, 2015 |
| Frosch and Hartmann | Procedure writers and editors | March 25, 2015 |
| Frosch and Hartmann | Procedure writers and editors | April 29, 2015 |
| Frosch, Hartmann and Gaddy | Procedure writers and editors | July 13, 2015 |
| Hartmann and Gaddy | Procedure writers and editors | December 22, 2015 |

Manual Change History

| Procedure | Ver/Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All Sections | 1.0 / 0 | New procedures for all sections for Nodal implementation | November 28, 2010 |
| 2.4 3.1 3.2 3.4 3.5 3.6 4.2 5.3 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Updated Categories and Priorities Updated Response to High Frequency steps 15, 20 and 25 minutes and Response to Low Frequency step 15 Updated steps Failure Indication/Issues and QSE Capacity Issues Updated steps AGC/RLC Issues, System Wide Capacity Issue and AGC/RLC Issues Resolved Updated step 1 Updated step Capacity Surplus Updated step 2, 3, 4 and 5 Updated all steps of “Implement Level 2B” | December 1, 2010 |
| 4.1 4.2 5.2 | 1.0 / 1 1.0 / 2 1.0 / 1 | Updated step “MP unable to Override” Updated step 1 & 2 Updated step 1 in sections WATCH and Advisory | December 15, 2010 |
| 3.1 3.2 3.3 3.4 4.1 5.1 5.4 | 1.0 / 2 1.0 / 2 1.0 / 1 1.0 / 2 1.0 / 2 1.0 / 1 1.0 / 1 | Updated step “BAAL” Updated step “AGC Issues Resolved” Updated step “Hotline” Updated step “Failure Indications, AGC/RLC Issues, System Wide Capacity Issue, AGC/RLC Issues Resolved” Updated step 2 in “Workflow Controller Messages”, added new procedure “Exceeding West – North Stability Limit”, updated Note in “Generation Resource Shut-down/Start-up Process” Updated step 1 in “Watch” and step Hotline in “Scripts” Updated step 1 in “Move from EEA level 3 to EEA lever 2B” | January 5, 2011 |
| 2.4 2.5 2.6 2.7 3.1 3.2 3.3 3.4 3.5 4.1 4.2 5.1 5.2 5.3 5.4 5.5 6.1 6.2 6.3 | 1.0 / 0 1.0 / 2 1.0 / 0 1.0 / 0 1.0 / 3 1.0 / 3 1.0 / 2 1.0 / 2 1.0 / 1 1.0 / 3 1.0 / 3 1.0 / 2 1.0 / 2 1.0 / 2 1.0 / 2 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Added new procedure Changed procedure number Added new procedure Added new procedure Updated sections “Maintain System Frequency”, “Response to High Frequency”, “Response to Low Frequency” and “Actions when Frequency Telemetry in Incorrect. Combined sections 3.3, 3.4 & 4.2 into 3.2 Changed 3.5 “Potential DCS Event” to 3.3 & updated whole procedure Changed 3.6 “Monitor Capacity Reserves & Respond to Capacity Issues to 3.4 Changed 3.7 “Monitor and Control Time Error Correction to 3.5 & updated script Deleted Exceeding West-North Stability Limit Deleted Procedure Updated script Updated step 1 in “Advisory” and “Watch” Updated all steps Updated all steps Updated all steps Updated all steps Updated all steps Updated OCN | January 31, 2011 |
| 2.6 3.2 3.3 3.4 3.6 5.1 5.2 | 1.0 / 1 1.0 / 4 1.0 / 3 - / 3 1.0 / 0 1.0 / 3 1.0 / 3 | Updated step Site Failovers Updated step 3 in SCED Failure, step 4 in RLC Failure, Note in LFC (AGC) Failure and step 2 in EMS (LFC and RLC/SCED Failure Updated step 3 Updated step Capacity Shortage Added new procedure Updated Watch and Emergency Notice All step 1’s | March 25, 2011 |
| 2.6 3.1 3.2 3.3 3.6 5.1 5.4 5.5 | 1.0 / 2 1.0 / 4 1.0 / 5 1.0 / 4 1.0 / 1 - / 4 1.0 / 3 1.0 / 2 | Added steps and updated whole procedure Added new step to Maintain System Frequency and updated Response to High Frequency & Response to Low Frequency Updated steps 2, 3, 5 in SCED Failure; steps 2, 3, 4, 6 in RLC Failure; steps 1, 3 in LFC (AGC) Failure; steps 2, 5 in EMS (LFC and RLC/SCED) Failure Updated NERC Recovery Criteria, step 1 & 4 Updated 1st script Updated step 1 in Watch and Emergency Notice and step Post Updated 1st and 2nd script in Restore Firm Load, Updated 1st in Move From EEA Level 3 to EEA Level 2B Updated step 3 | April 22, 2011 |
| 3.3 5.1 5.3 5.4 6.1 6.2 6.3 6.4 | 1.0 / 5 1.0 / 5 1.0 / 3 1.0 / 4 1.0 / 2 1.0 / 0 1.0 / 2 1.0 / 2 | Updated step NERC Recovery Criteria Updated all step 1’s Updated step 1 in Implement EEA Level 1, step 1 in Implement EEA Level 2A, added note and updated step 2 in Implement EEA Level 2B, step 1 in Implement EEA Level 3 Updated all step 1’s Updated all steps Added new procedure Updated section number and all steps Updated section number and all steps | June 8, 2011 |
| 2.6 3.1 5.1 5.2 5.3 5.4 8.1 | 1.0 / 3 1.0 / 5 1.0 / 6 1.0 / 4 1.0 / 4 1.0 / 5 1.0 / 1 | Added step If EBPs are needed”, updated step IF EBPs are needed and W-N was Active before site failover started Added step Hydro, updated step Frequency Deviations Updated step Watch Updated all steps Updated 1st note, step 1 in EEA level 1 & 2A Updated step 1 in Move for EEA level 1 to 0 Added Market Participant Backup Control Center Transfer procedure | July 20, 2011 |
| 3.1 3.2 3.4 4.1 6.4 6.5 | 1.0 / 6 1.0 / 6 1.0 / 4 1.0 / 4 1.0 / 0 1.0 / 3 | Updated step Monitor, 15 minutes, 20 minutes and 25 minutes in Response to High Frequency Updated step 2 in LFC Failure, step 4 & 5in EMS Failure Updated step Capacity Surplus Updated step 2 in Workflow Controller Messages Added new procedure “Extreme Hot Weather” Changed section number | August 3, 2011 |
| 2.7 3.1 5.1 5.2 5.3 5.4 6.4 7.1 | 1.0 / 1 1.0/ 7 1.0 / 7 1.0 / 5 1.0 / 5 1.0 / 6 1.0 / 1 1.0 / 1 | Updated step Hotline Call Updated NERC Standard reference table Added projected reserve capacity shortage and Extreme Hot Weather in Watch Updated step 1 in Advisory & Watch Updated 2nd Note, step 1 in Implement EEA 1, step Media Appeal & 1 in Implement EEA 2A, 1st Note & step 2 in Implement EEA 2B Added Note to Move From EEA 3 to EEA 2B and Move From EEA 2A to EEA 1 Updated temperature from 102 to 103 Updated 4th note and step 1 | September 1, 2011 |
| 3.2 5.3 5.4 | 1.0 / 7 1.0 / 6 1.0 / 7 | Updated SCED Failure step 2 and 3, RLC Failure step 3 and LFC (AGC) Failure step 3 Combined EEA 2A & B per NPRR 379 Combined EEA 2 A & B per NPRR 379 | October 1, 2011 |
| 3.2 | 1.0 / 8 | Updated script for LFC and EMS Failure | November 1, 2011 |
| 2.4 2.6 4.1 5.1 6.3 | 1.0 / 1 1.0 / 4 1.0 / 5 1.0 / 8 1.0 / 3 | Added step Review, Updated “Site Failover with W-N Active” Added Note to Large Resource Trips or Runbacks Updated Post in “Scripts” Updated “OCN” and “Advisory” All procedures in this manual have been reviewed. | December 15, 2011 |
| 1.2 3.1 4.1 8.1 | 1.0 / 1 1.0 / 7 1.0 / 6 - / 2 | Updated Scope Updated Response to High Frequency & Response to Low Frequency Updated Large Resource Trips or Runbacks, Quick Start Generation Resource Updated Market Participant Backup Control Center Transfer | January 19, 2012 |
| 2.1 3.1 5.1 5.3 7.1 8.1 | 1.0 / 1 1.0 / 8 1.0 / 7 1.0 / 9 1.0 / 7 1.0 / 2 1.0 / 3 | Updated paragraph 4 Updated BAAL Updated Desktop Guide reference & step QSE Override & QSE unable to Override Updated step 1 in Watch Updated Step 1 in Implement EEA Level 1 Updated Desktop Guide references Changed title names, updated steps 1 & 3 & step Power System Stabilizers (PSS) & Automatic Voltage Regulators (AVR) | March 1, 2012 |
| 2.1 3.1 3.2 3.3 3.5 4.1 5.1 6.2 6.3 6.4 8.1 | 1.0 / 2 1.0 / 9 1.0 / 9 1.0 / 6 1.0 / 2 1.0 / 8 1.0 / 10 1.0 / 4 1.0 / 2 1.0 / 4 1.0 / 4 | Changed TSO, DSP to TO Changed Shift Engineer to Operations Support Engineer, removed Automatic SCED Runs & Hydro Generation in Fast Response Mode, updated Note, Monitor/Deploy, 15 minutes, 20 minutes in Response to Low Frequency Updated step 2, 4 & 5, added SCED Data Input Failure, updated RLC Failure, LFC Failure, & EMMS Failure sections Updated Nerc Recovery Criteria step & step 3 Updated Requirements and Notes Changed Shift Engineer to Operations Support Engineer, deleted Large Resource Trips or Runbacks section Updated OCN, Advisory, Watch, Emergency Notice sections Deleted Cold Weather, replaced with Extreme Cold Weather Section changed to Extreme Hot Weather, added OCN and Emergency Notice steps Section number changed Changed Shift Engineer to Operations Support Engineer | May 1, 2012 |
| 3.1 3.4 5.2 | 1.0 / 10 1.0 / 5 1.0 / 6 | Added back step Hydro Generation Operating in Synchronous Condenser Fast Response Mode Updated to reflect changes in the TAC approved Non-Spin document Updated to reflect changes in the TAC approved Non-Spin document | May 14, 2012 |
| 2.6 5.3 5.4 6.3 | 1.0 / 5 1.0 / 8 1.0 / 8 1.0 / 3 | Updated Site Failover step Updated EILS to ERS per NPRR 451 Updated EILS to ERS per NPRR 451 Updated EILS to ERS per NPRR 451 | June 1, 2012 |
| 1.3 2.6 5.1 5.3 5.4 6.2 6.3 7.1 | 1.0 / 1 1.0 / 6 1.0 / 11 1.0 / 9 1.0 / 9 1.0 / 5 1.0 / 4 1.0 / 3 | Removed ERCOT Shift Supervisor paragraph Updated all steps Updated all step 1’s Updated 2nd note, added TCEQ, & XML for ERS Clarified LR and ERS recalls Updated script for Emergency Notice Updated script for Emergency Notice Updated 4th note | July 16, 2012 |
| 2.6 3.1 4.1 5.3 | 1.0 / 7 1.0 / 11 1.0 / 9 1.0 / 10 | Added note to step Database Load Updated Frequency Deviations and Monitor Frequency for the Loss of EMS or Site Failover Incorporated NPRR348 Added 30 MIN ERS and updated steps 1, 2 & 3 on Implement EEA Level 1 | August 29, 2012 |
| 2.2 2.5 3.5 4.1 5.3 | 1.0 / 1 1.0 / 3 1.0 / 3 1.0 / 10 1.0 / 11 | Added Hotline Call Communication Updated step 3 Updated per NOGRR100 Added Note to Shut-down/Start-up Process and new Combine Cycle Generation Resources section Updated ERS scripts All procedures in this manual have been reviewed. | November 1, 2012 |
| 2.5 3.1 3.2 3.3 3.4 3.5 3.6 3.7 5.4 | 1.0 / 4 1.0 / 12 1.0 / 0 1.0 / 10 1.0 / 7 1.0 / 6 1.0 / 4 1.0 / 2 1.0 / 10 | Updated step 3 Updated BAAL New procedure, Monitor Large Ramp Events Updated section # & SCED failure step 2 Updated section # Updated section # Updated section # Updated section # Updated Cancel Watch All procedures in this manual have been reviewed. | March 1, 2013 |
| 2.6 2.7 3.1 3.2 3.3 3.4 3.7 4.1 5.1 5.2 5.3 5.4 5.5 6.1 6.2 6.3 6.4 | 1.0 / 8 1.0 / 2 1.0 / 13 1.0 / 1 1.0 / 11 1.0 / 8 1.0 / 3 1.0 / 11 1.0 / 12 1.0 / 8 1.0 / 12 1.0 / 11 1.0 / 3 1.0 / 3 1.0 / 6 1.0 / 5 1.0 /5 | Updated scripts Updated scripts Updated Monitor Frequency for the Loss of EMS or Site Failover & Actions when Frequency Telemetry is Incorrect Updated scripts Updated scripts Updated script Updated scripts Added QSGR Decommitment step to QSGR Added Generic and Specific scripts Updated Note and scripts Updated TCEQ section and scripts Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts Correct spelling and updated script | June 1, 2013 |
| 2.6 3.1 3.2 3.8 5.1 5.3 5.4 | 1.0 / 9 1.0 / 14 1.0 / 2 1.0 / 0 1.0 / 13 1.0 / 13 1.0 / 12 | Changed title name & updated step EMS Changes & added MMS Changes Updated steps Base Point Deviation & 10 Minutes Updated 1st note Moved procedures from Resource desk Updated step 1 in Watch & Emergency Notice Updated step Pilot Project WS ERS Updated step Reserves | July 15, 2013 |
| 2.6 3.2 3.8 4.1 | 1.0 / 10 1.0 / 3 1.0 / 1 1.0 / 12 | Updated MMS Changes Updated 1st Note Updated Unit & Load RRS Shortage & Not Dispatchable to SCED Updated Shutdown/Startup | August 9, 2013 |
| 3.8 | 1.0 / 2 | Updated Unit RRS Shortage, Load RRS Shortage, REG Shortage, & added Real-Time Non-Spin Shortage | September 27, 2013 |
| 2.4 3.1 3.2 3.3 3.4 3.5 3.7 4.1 5.1 5.2 5.3 5.4 5.5 6.1 6.2 6.3 6.4 7.1 8.1 | 1.0 / 2 1.0 / 15 1.0 / 4 1.0 / 12 1.0 / 9 1.0 / 7 1.0 / 4 1.0 / 13 1.0 / 14 1.0 / 9 1.0 / 14 1.0 / 13 1.0 / 4 1.0 / 4 1.0 / 7 1.0 / 6 1.0 / 6 1.0 / 4 1.0 / 5 | Updated step Log Updated step Frequency Deviations & step Log Updated step Log Updated step Log Updated step Log Added step RMR & updated step Log Updated step Log Updated step Log Updated step Log Updated step Log Updated step Log Updated step Log Updated step Log Updated step Log Updated step Log Updated step Log Updated note and step Log Updated step Log Added & updated step Log All procedures in this manual have been reviewed | December 13, 2013 |
| 2.6 3.3 5.1 | 1.0 / 11 1.0 / 13 1.0 / 15 | Updated for NPRR542 Updated for NPRR542 Updated for NPRR542, deleted West to North GTL and updated procedure for North to Houston to a new GTL | January 1, 2014 |
| 2.6 3.1 3.3 3.5 3.6 4.1 5.3 5.4 6.4 8.1 | 1.0 / 12 1.0 / 16 1.0 / 14 1.0 / 8 1.0 / 5 1.0 / 14 1.0 / 15 1.0 / 14 1.0 / 7 1.0 / 6 | Updated Site Failover Complete Updated VDI information, step Monitor/Deploy & step 10 Minutes in Response to Low Frequency Updated VDI information Updated VDI information Updated step Terminating Time Error Correction Updated VDI information Updated ERS, Media appeal, TCEQ and VDI information Updated steps Reserves and 1 in Restore firm load and step 2 in Move From EEA Level 2 to EEA Level 1 Updated Note Updated Requests to Decommit Self-committed Resource in Operating Period | April 4, 2014 |
| 2.2 3.1 3.3 4.1 5.1 5.2 6.2 6.3 | 1.0 / 2 1.0 / 17 1.0 / 15 1.0 / 15 1.0 / 16 1.0 / 10 1.0 / 8 1.0 / 7 | Added VDIs to Master QSEs Updated step BAAL Updated SCED Failure & SCED Data Input Failure steps Updated QSGR in Quick Start Generation Resource Added Note, updated Market Notices Advisory & Watch Updated Watch steps Updated Emergency Notice step Updated Emergency Notice step | June 1, 2014 |
| 3.5 5.3 | 1.0 /9 1.0 / 16 | Updated Deploying Non-Spin, added HASL Release & Recall Added Media Appeal | August 1, 2014 |
| 4.1 5.1 5.3 | 1.0 / 16 1.0 / 17 1.0 / 17 | Updated Reference section step 2 Updated Generic Script Added HASL Release step | October 1, 2014 |
| 2.3 2.4 2.6 3.3 3.5 5.1 5.3 | 1.0 / 1 1.0 / 3 1.0 / 13 1.0 / 16 1.0 / 10 1.0 / 18 1.0 / 18 | Updated all steps Updated step Send E-mail Deleted Site Failover with W-N Active & updated step If EBPs are Needed Updated 1st note & updated scripts Added new procedure, “Valley Generation” Updated GMD scripts Updated scripts to consolidate All procedures in this manual have been reviewed | December 15, 2014 |
| 6.2 | 1.0 / 9 | Updated Note and scripts | December 22, 2014 |
| 2.2 3.1 3.2 3.5 3.9 6.2 | 1.0 / 3 1.0 / 181.0 / 5 1.0 / 11 1.0 / 0 1.0 / 10 | Added Dispatch and VDI definitions Updated Objective and BAAL Updated procedure Updated step 1 and added Log on Valley Generation Added new procedure for NOGRR136 Updated scripts | March 1, 2015 |
| 3.1 3.3 3.5 3.10 4.1 5.1 | 1.0 / 19 1.0 / 17 1.0 / 12 1.0 / 0 1.0 / 17 1.0 / 19 | Clarification to step Frequency Deviation & Hydro Operating in Synch. Condenser Mode Updated Dispatch Instruction scripts Clarification to step HASL Release Manually Deploy RRS New GMD procedure Updated Dispatch Instruction scripts Deleted script for GMD | March 30, 2015 |
| 2.6 2.7 3.2 3.3 3.4 3.63.7 3.10 5.1 5.2 5.3 5.4 5.5 6.1 6.2 6.3 6.4 | 1.0 / 14 1.0 / 3 1.0 / 6 1.0 / 18 1.0 / 10 1.0 / 6 1.0 / 5 1.0 / 1 1.0 / 20 1.0 / 11 1.0 / 19 1.0 / 15 1.0 / 5 1.0 / 5 1.0 / 11 1.0 / 8 1.0 / 8 | Moved scripts to new script procedure Moved scripts to new script procedure Updated 1st note and moved scripts to new script procedure Updated step 2 on SCED Data Input Failure & moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Updated 4th bullet on Emergency Notice & moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure | May 1, 2015 |
| All Sections 2.6 3.5 3.9 3.10 5.1 5.2 6.3 | 1.0 / 1 1.0 / 15 1.0 / 13 1.0 / 1 1.0 / 2 1.0 / 21 1.0 / 12 1.0 / 9 | Added a “Q” for numbered QSE scripts Renamed section to Site Failovers and Database Loads Updated link for Monitor in the Valley Generation Updated 1st Note Updated Procedure Purpose and removed script Updated Specific Scripts, New GTC Updated Q#1, Q#2, Q#3, & Q#4 Script titles Removed Watch script | July 15, 2015 |
| 2.6 3.2 3.3 3.4 3.6 3.7 3.9 3.10 5.1 5.2 5.3 5.4 5.5 6.1 6.2 6.3 6.4 | 1.0 / 16 1.0 / 7 1.0 / 19 1.0 / 11 1.0 / 7 1.0 / 6 1.0 /2 1.0 / 3 1.0 / 21 1.0 / 13 1.0 / 20 1.0 / 16 1.0 / 6 1.0 / 6 1.0 / 12 1.0 / 10 1.0 / 9 | Updated step MMS Changes Typical Script Q#19 Updated step Site Failover Q#20 Updated step Site Failover Complete Q#21 Updated Step If EBP’s are needed Q#22 Updated step Site Failover Complete If EBP’s were needed Q#23 Updated step 2 Q#26 Updated SCED Failure step 2 Q#27 & step 4 Q#28 Updated SCED Data Input Failure step 1 Q#29 Updated RLC Failure step 2 Q#30 & step 4 Q#31 Updated LFC (AGC) Failure step 1 Typical Script step 2 Q#32, step 4 Typical script & Q#33 Updated EMMS (LFC and RLC/SCED) Failure step 1 Typical Script, step 2 Q#34, step 5 Typical Script & Q#35 Updated step 3 Q#36 Updated step Initiating Time Error Correction Q#37 Updated step Terminating Time Error Correction Q#38 Updated step Issue Watch and Deploy Non-Spin Q#39 Updated step Issue Emergency Notice & Deploy Load Resources Q#40 Updated step Recall Load Resources Q#41 Updated step Recall Non-Spin Q#42 Updated step Start CFC Test & End CFC Test Typical Scripts Updated step 1 Q#43 Updated step K Level Increases/Decreases Q#44 Updated step Cancel Q#45 Updated Title Operating Condition Script Updated step Hotline Q#46 Updated step Hotline Cancellation Q#47 Updated Title Specific Scripts for Transmission Operator [State Estimator/RTCA/VSAT] Updated step State Estimator/RTCA Not Solved In 30 MIN Q#48 & Q#49 Updated step VSAT Not Solved In 30 MIN Q#50 & Q#51 Updated step Qualifying Facility Directed to Operate Below LSL Q#52 & Q#53 Updated step New GTC Q#54 Updated step Transmission Watch Q#55 & Q#56 Updated Advisory step Issue Advisory Q#1 Updated Advisory step Cancel Advisory Q#2 Updated Watch step Issue Watch Q#3 Updated Watch step Cancel Watch Q#4 First Note, Updated Implement EEA Level 1 step EEA 1 PRC <2300 Q#5 & Q#6 Updated Implement EEA Level 2 step ERS Resources Q#7 Updated Implement EEA Level 2 step Load Resources Q#8 Updated Implement EEA Level 2 step When ERS Business Hours Change Q#9 Updated Implement EEA Level 3 step When ERS Business Hours Change Q#12, and Implement NPRR708 for EEA Updated Restore Firm Load step 1 Q#13 Updated Move From EEA Level 3 to EEA Level 2 step 1 Q#14 Updated Move From EEA Level 2 to EEA Level 1 step 1 Q#15 Updated Move From EEA Level 1 to EEA Level 0 step 1 Q#16 Updated Cancel Watch step 1 Q#17 Updated step Return to Normal QSE Notification Q#57 Updated step Emergency Notice Q#61 Updated step Emergency Notice Q#65 Updated step Emergency Notice Q#69 Updated step OCN/Advisory/Watch Q#70 All procedures in this manual have been reviewed | December 31, 2015 |