- Power Operations Bulletin # 748

ERCOT has posted/revised the Real Time manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

- http://www.ercot.com/mktrules/guides/procedures/index.html

# 2.  General

## 2.1	System Operator Responsibility and Authority

Procedure Purpose:  To ensure the System Operators know their roles, responsibility and authority.

| Protocol Reference | 6.5.11 | 6.5.1.2(3) | 6.5.2 | 6.5.3(1) |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.5.2(1) |  |  |  |
| NERC Standard | EOP-002-3.1 R1 | IRO-001-1.1 R3 | PER-001-0.2 R1 | TOP-001-1a R1 |

| Version: 1 | Revision: 4 | Effective Date:June 30, 2016 |
| --- | --- | --- |

The System Operator (SO) shall, in accordance with NERC Reliability Standards, have clear decision-making authority to act and to direct actions to be taken by Transmission Operators, Generator Operators, and Transmission Service Providers within its Reliability Coordination Area to preserve the integrity and reliability of the Bulk Electric System during both normal and emergency conditions.  These actions shall be taken without delay, but not longer than 30 minutes which may include the shedding of firm load without obtaining approval from higher-level personnel.  The ERCOT System Operator represents the following NERC functional entities collectively for the ERCOT ISO at any time:

- Reliability Coordinator

- Balancing Authority

- Transmission Operator

- The SO on duty is, in accordance with the ERCOT Protocols, Operating Guides, and NERC Reliability Standards, and acting as the Balancing Authority, Transmission Operator, and Reliability Coordinator shall request and receive information required to continually monitor the operating conditions and request that individual Market Participants (MPs) make changes, which will assure the security and reliability of the ERCOT System.

- The SO issues Dispatch Instructions for the Real-Time Operation of Transmission Facilities to a TO, and to a QSE for the Real-Time Operation of a Resource.

- The SO shall, on an ERCOT-wide basis, coordinate the ERCOT System Restoration (Black Start) Plan.  The SO shall implement the Black Start Plan and shall direct the reconnection efforts of the islands, established by restoration activities.  The SO shall coordinate the mutual assistance activities of the ERCOT participants during system restoration activities.

- The SO shall consider all equipment operating limits when issuing Dispatch Instructions except as stated in Protocol Section 6.5.9, Emergency Operations, if a Dispatch Instruction conflicts with a restriction that may be placed on equipment from time to time by a TO, or a Generation Resource’s QSE to protect the integrity of equipment, ERCOT shall honor the restriction.

- The SO performs security analyses on a Day Ahead and Real-Time basis and ensure that all Forced Outages are entered into the Outage Scheduler. The SO shall obtain or arrange to provide Emergency Energy over the DC Tie(s) on behalf of ERCOT.

- The SO shall issue appropriate OCN’s, Advisories, Watches, and Emergency Notices, and coordinate the reduction or cancellation of clearances, re-dispatch of generation, and request, order, or take other action(s) that the SO determines necessary to maintain safe and reliable operating conditions on the ERCOT System in accordance with ERCOT Protocols, Operating Guides, and NERC Reliability Standards.  The SO will implement and terminate ERCOT Time Corrections, and will determine the need for and implement the operation of a Qualified Scheduling Entity (QSE) on Constant Frequency Control for loss of ERCOT’s Load Frequency Control System.

- As the Reliability Coordinator, ERCOT ISO shall comply with its Regional Reliability Plan which has been approved by the NERC Operating Committee.

## 2.2	Communication

Procedure Purpose:  To improve communication to reduce the possibility of miscommunication that could lead to action or inaction harmful to the reliability of the grid.

| Protocol Reference | 6.5.7.8 | 6.5.8 |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 3.1.3 |  |  |  |
| NERC Standard | COM-002-4 |  |  |  |

| Version: 1 | Revision: 4 | Effective Date: June 30, 2016 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Three-Part Communication |  |
| NOTE | - Operating Instructions and Dispatch Instructions are synonymous and both require ‘three-part communication’. - Refer to the Communications Protocols document for requirements. |
| 1 | When issuing Operating Instructions, use three-part communication: - Issue the Operating Instruction - Receive a correct repeat back - Give an acknowledgement |
| 2 | Many scripts have been placed throughout these procedures as a reminder of three-part communication. However, a script cannot be provided for every scenario. Effective three-part communication skills are mandatory. |
| ### Hotline Call Communication |  |
| 1 | When making Hotline calls, verify that every QSE has answered. IF: - Not every QSE answered the Hotline; THEN: - Contact them using their OPX line or LD line to provide them with the message - Inquire why they were not on the Hotline call - Open a Help ticket if ERCOT’s Telecommunications department is needed to investigate. |
| ### Master QSE |  |
| 1 | Issue the VDI to the Master QSE of a Generation Resource that has been split to function as two or more Split Generation Resources as deemed necessary by ERCOT to effectuate actions for the total Generation Resource for instances when electronic Dispatch Instructions are not feasible. |
| LOG | Log all actions. |

## 3.0	Monitor and Manage System Security

## 3.1	Frequency Control Operating Procedure

Procedure Purpose: To control frequency within defined limits.

| Protocol Reference | 6.5.7.6.1 | 6.5.7.6.2.2(7) | 6.5.9.1(1)(b) |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 2.2.4 | 2.2.8 |  |  |
| NERC Standard | BAL-001-2 | IRO-002-2 R7 | IRO-005-3.1a R1.6, R5, R6 | NUC-001-3 R9.4.2 |

| Version: 1 | Revision: 21 | Effective Date: June 30, 2016 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Maintain System Frequency |  |
| Objective | - Frequency should be maintained within +/- 0.03 Hz of schedule - Attempt to maintain CPS1 scores over 100 - Operate within the BAAL - Frequency Bias set to 739MW/0.1Hz |
| CPS1 less than 100 | IF: - Performance drops below 100 for over three consecutive hours; THEN: - LOG the event and the possible cause of the poor performance. |
| BAAL | Corrective action shall be taken whenever the clock-minute average ACE is outside its clock-minute average Balancing Authority ACE Limit (BAAL). This is to ensure that the Balancing Authority ACE does not remain outside the BAAL for more than 30 consecutive clock-minutes. |
| Caution | NEVER (unless directed by EMMS Production or Support Engineer): - Change other tuning parameters (including QSE ramp rates, dead bands, thresholds, gains, time constraints) |
| Base Point Deviation | REVIEW REFERENCE DISPLAY: EMP Applications>Generation Area Status>Related Displays>Expected Generation and Load Details Not-Tracking Units tab IF: - A QSE has a Resource with a large Base Point deviation (not tracking unit flag), AND - Their generation is not moving in the proper direction to correct their Base Point Deviation; THEN: - Notify the QSE of the issue. |
| Frequency Deviations | IF: - Frequency deviations are equal to or greater than +/- 0.10 Hz, OR - Sudden loss of generation greater than 450 MW; THEN: - Ensure frequency recovers to pre-disturbance within 15 minutes - Manually run SCED or use offset as needed. LOG: - Log the following information: - Possible reasons, if known (Base Point deviation, large schedule change, unit trip, DC-Tie trip, etc.) - If unit trip: - Time of unit trip or DC-Tie, - Name of unit or DC-Tie, - Approximate net MW, - Approximate lowest TrueTime frequency (use 3 decimals), - Amount of RRS deployed (if any), AND - Approximate ERCOT load. |
| Hydro Generation Operating in Synchronous Condenser Fast Response Mode | IF: - Hydro Resources operating in synchronous condenser fast-response mode who provide MW to the System in response to a frequency event without a Responsive Reserve deployment; THEN: - QSE will request an electronic Dispatch Instruction confirmation - Choose Resource tab - Choose requesting QSE for Participant Name - Choose Resource name - Enter MW amount deployed in Current Operating Level - Choose Other For Resource for Instruction Type - State Hydro deployed in response to frequency in Other Information - Initiation Time, and - Completion Time When issuing a VDI or the confirmation, ensure the use of three-part communication: - Issue the Operating Instruction - Receive a correct repeat back - Give an acknowledgement - An electronic Dispatch Instruction confirmation will be needed for each Resource. IF: - QSE contacts ERCOT to determine if it is allowed to recall and reset; THEN: - ERCOT grants approval to come off-line once the frequency recovers to pre-disturbance level or 60 Hz, whichever is lower, OR - Request QSE to remain On-line - May not exceed 30 minutes per deployment for each frequency deviation or event - Shall not exceed two hours per a 12-hour period in aggregate unless an EEA is declared |
| ### Response to High Frequency |  |
| BAAL Sheet | Located on the realtime drive in the _Operations Official Spreadsheets folder. Open BAAL ERCOT Interconnection and select Control T simultaneously. |
| Monitor | IF: - Frequency goes above 60.05 Hz and exceeds 60.05 Hz > 5 minutes AND - Regulation Down service remains and is deploying; THEN: - Manually run SCED - Call QSEs with Resources that have positive Base Point deviations and issue an Operating Instruction to bring their Base Point deviations to zero. IF: - Frequency goes above 60.05 Hz, AND - Out of Down Regulation; THEN: - CHECK the GEN-LDL or Cap to decrease BP on the EMS to ensure there is adequate down room, - Enter manual offset (the offset will continue until removed). IF: - There is no generation left for SCED to lower; THEN: - Coordinate with the Shift Supervisor and Transmission Operator to select a Resource to decommit, - Request RUC Operator to issue an Operating Instruction to decommit Resource. |
| 10 MINUTES | REFERENCE DISPLAY: EMP Applications>Generation Unit Status>Related Displays>Expected Generation and Load Details>Top Ten button AND Market Operation>Real-Time Market>SCED Displays>DSI Displays>DSI Data Processes>DSI Generation Requirement Manual Adjustment IF: - 10 consecutive minutes of ACE above BAALHigh (60.09 Hz); THEN: - Call QSEs with Resources that have positive Base Point deviations and issue an Operating Instruction to bring their Base Point deviations to zero, - Verify SCEDs capacity to decrease Base Points GEN-LDL, - Enter manual offset, - Manually run SCED (do not run SCED more than once between SCED runs). |
| Notify | If it is recognized that Frequency is or expected to be outside +/- 0.1 Hz for a non-transient event and will not recover within 15 minutes, notify the Nuclear Power Plants QSEs. |
| 15 Minutes | IF: - 15 consecutive minutes of ACE above BAALHigh (60.09 Hz); THEN: - Call QSEs with Resources that have positive Base Point deviations and issue an Operating Instruction to bring their Base Point deviations to zero, - Verify SCEDs capacity to decrease Base Points GEN-LDL, - Re-adjust manual offset, - Manually run SCED, - Log the event and notify Operations Support Engineer to send an event notification to OperationsAnalysis@ercot.com. IF: - There is no generation left for SCED to lower; THEN: - Coordinate with the Shift Supervisor and Transmission Operator to select a Resource to decommit, - Request RUC Operator to issue Operating Instruction to decommit Resource. |
| 20 Minutes | IF: - 20 consecutive minutes of ACE above BAALHigh (60.09 Hz) and Frequency is above 60.10 Hz; THEN: - Call QSEs with Resources that have positive Base Point deviations and issue an Operating Instruction to bring their Base Point deviations to zero - Curtail appropriate amount of DC-Tie imports (issue an Emergency), - Coordinate with Shift Supervisor, Transmission Operator to select an additional Resource to decommit, - Request RUC Operator to issue Operaring Instruction to decommit Resource. |
| 25 Minutes | IF: - 25 consecutive minutes of ACE above BAALHigh (60.09 Hz) and Frequency is above 60.10 Hz; THEN: - Call QSEs with Resources with positive Base Point deviations and issue an Operating Instruction to take their Resource off-line. - Coordinate with Shift Supervisor, Transmission Operator to select an additional Resource to decommit, - Request RUC Operator to issue Operating Instruction to decommit Resource. |
| Stable | IF: - A manual offset was used; THEN: - Ensure that it has been removed. |
| Log | Log all actions. |
| ### Response to Low Frequency |  |
| BAAL Sheet | Located on the realtime drive in the _Operations Official Spreadsheets folder. Open BAAL ERCOT Interconnection and select Control T simultaneously. |
| NOTE | UFRs will deploy as follows: - Hydro RRS - 59.80 Hz - Load Resource providing RRS – 59.70 Hz |
| Monitor/ Deploy | IF: - Frequency drops below 59.95 Hz, AND - Regulation Up service remains and is deploying; THEN: - Manually run SCED (do not run SCED more than once between SCED runs) - Call QSEs with Resources with negative Base Point deviations and issue an Operating Instruction to bring their Base Point deviations to zero. IF: - Frequency drops below 59.95 Hz, AND - Out of Up Regulation; THEN: - Check the GTBD2[HDL] on the OpsMon SCED GEN ONLINE Dashboard or Cap to increase BP or HDL-Gen on the EMS and enter appropriate manual offset - If using OpsMon Dashboard, do not enter an offset > than GTBD2[HDL] - If using EMS, do not enter an offset > than Cap to increase BP or HDL-Gen IF: - Frequency is below 59.95 Hz and out of Up Regulation, AND - There is not adequate up room; THEN: - Manually deploy Responsive Reserve using the ERCOT Nodal Summary display on the EMS - Check the box labeled “Activate Manual Responsive Reserve” to activate, - Enter the “Desired RRS MW”, - Select Enter, - Select Commit. - QSE’s have one minute to update schedule to free up the capacity, SCED will automatically run after one minute. - Remember to remove the manual RRS amount when frequency has recovered. |
| 10 Minutes | REFERENCE DISPLAY: EMP Applications>Generation Unit Status>Related Displays>Expected Generation and Load Details>Top Ten button AND Market Operation>Real-Time Market>SCED Displays>DSI Displays>DSI Data Processes>DSI Generation Requirement Manual Adjustment IF: - 10 consecutive minutes of ACE is less than BAALLow (59.91 Hz); THEN: - Call QSEs with Resources with negative Base Point deviations and issue an Operating Instruction to bring their Base Point deviations to zero, - Confirm Responsive Reserve has been deployed, - Verify SCEDs capacity to increase Base Points, - Enter manual offset - If room is available - Manually run SCED IF: - There is no generation left for SCED to increase; THEN: - Confirm with the Resource Operator that Non-Spin has been deployed, - Manually deploy Generation Responsive Reserve using the ERCOT Nodal Summary display on the EMS - Check the box labeled “Activate Manual Responsive Reserve” to activate, - Enter the “Desired RRS MW”, - Select Enter, - Select Commit. - QSE’s have one minute to update schedule to free up the capacity, SCED will automatically run after one minute. - Remember to remove the manual RRS amount when frequency has recovered. - Notify the Shift Supervisor of the need to possibly commit additional Resources. |
| Notify | If it is recognized that the Frequency is or expected to be outside +/- 0.1 Hz for a non-transient event and will not recover within 15 minutes, notify the Nuclear Power Plants QSEs. |
| 15 Minutes | IF: - 15 consecutive minutes of ACE less than BAALLow (59.91 Hz ); THEN: - Curtail appropriate amount of DC-Tie export (issue an Emergency), - Instruct the Resoure Operator to manually deploy one block of Load Resources providing Responsive Reserve, - Call QSEs with Resources that have negative Base Point deviations and issue an Operating Instructon to bring their Base Point deviations to zero, - Verify SCEDs capacity to increase Base Points (HDL-GEN), - Re-adjust manual offset, - If room is available - Manually run SCED, - Log the event and notify Operations Support Engineer to send notification of the event to OperationsAnalysis@ercot.com. |
| 20 Minutes | IF: - 20 consecutive minutes of ACE less than BAALLow (59.91 Hz); THEN: - Call QSEs with Resources that have negative Base Point deviations and issue an Operating Instruction to bring their Base Point deviations to zero, - Verify SCEDs capacity to increase Base Points (HDL-GEN), - If room is available, re-adjust manual offset, - Manually run SCED, - Monitor RRS Load Resource deployments. |
| 25 Minutes | IF: - 25 consecutive minutes of ACE less than BAALLow (59.91 Hz ); THEN: - Verify SCEDs capacity to increase Base Points, - Re-adjusted manual offset, - Do Not enter an offset > than (HDL-GEN) - Manually run SCED as needed, - Monitor RRS Load Resource deployments, - Monitor DC-tie curtailments, - Instruct the Transmission and Security Operator to shed an appropriate amount of firm load. - Make Hotline call to QSE’s ## Q#102 BAAL Firm Load Shed: |
| Stable | IF: - Firm load was shed; THEN: - Instruct the Transmission and Security Operator to restore firm load. - Make Hotline call to QSE’s ## Q#13 Restoring Firm Load: IF: - RRS was manually deployed; THEN: - Uncheck the Activate Manual Responsive Reserve, IF: - An manual offset was used; THEN: - Ensure that it has been removed. |
| Log | Log all actions. |
| ### Monitor Frequency for the Loss of EMS or Site Failover |  |
|  | The ability to view an adequate Frequency source may be limited during a site-failover, database load, or if AGC is temporarily unavailable. To view the System Frequency during these conditions you may monitor the following sources. - ERCOT Control Room digital wall frequency displays - PI ProcessBook → ERCOT → TrueTime Frequency (Taylor) and/or - PI ProcessBook → ERCOT → TrueTime Frequency (Bastrop) It may be necessary to reload the PI ProcessBook “ERCOT Main Summary” display to show the historical data. |
| ### Actions When Frequency Telemetry is Incorrect |  |
|  | REVIEW REFERENCE DISPLAY: EMP Applications>Generation Control>Generation Area Status>Current Frequency Deviation from Nominal IF: - Frequency is believed to be incorrect; THEN: - Check the current Frequency and switch to a different source, - Select Skip on the incorrect Frequency device, - Contact the Help Desk. |

## 3.3	System Failures

Procedure Purpose:  To ensure that frequency is maintained in the event of an AGC failure.

| Protocol Reference | 6.3.3 | 6.5.9.1(2) | 6.5.9.2 (1)& (3) | 6.5.9.3.3(2)(g) |
| --- | --- | --- | --- | --- |
| Guide Reference | 2.2.4.3 (1) |  |  |  |
| NERC Standard | BAL-005-0.2b R7 |  |  |  |

| Version: 1 | Revision: 21 | Effective Date: June 30, 2016 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### SCED Failure |  |
| NOTE | When RLC sees that the SCED solution has not updated within the last 425 seconds, emergency base points (EBP) will automatically activate. Any time EBPs are activated, SCED solutions are being blocked from being communicated to MPs. The RLC Control Parameters (SCED Failure Threshold) should be set to 125 seconds. This is due to a code that adds 300 seconds to the 125 seconds from SCED Failure Threshold Parameter in the display, so total number of seconds RLC waits for SCED solution is 425 before enabling the emergency base points. |
| NOTE | If for some reason a manual EBP is required for a Resource, communicate the Resource name, MW output requested, start time and duration of the dispatch instruction to the QSE representing the Resource. |
| 1 | IF: - Any module of the SCED Workflow Controller fails; THEN: - Manually run the SCED process. |
| 2 | IF: - SCED still fails after manually running, AND - EBPs have automatically activated; THEN: - Contact the Help Desk, - Initiate the Watch Hotline call to QSEs, - Notify Resource Operator to post a message on MIS Public, - Notify Transmission Operator to make Hotline call to TOs. Q#27 - Typical Hotline Script for Watch for SCED Failure |
| 3 | EMP Applications>Generation Area Status>Related Displays>ERCOT Nodal Summary MONITOR: - Regulation Service (Up/Dn) margins to ensure frequency can be adequately maintained. IF: - It is determined that remaining Regulation Service (Up/Dn) is no longer sufficient to maintain system frequency; THEN: - Enter the EBP increment/decrement as needed to control frequency to recall deployed Regulation. - Once the MW amount has ramped, the EBP amount will return to zero |
| 4 | WHEN: - SCED is solving with a valid solution; THEN: - Remove the Emergency Base Point flag, - Initiate Hotline call to cancel the Watch, - Notify Resource Operator to cancel MIS posting, - Notify Transmission Operator to cancel the Watch with TOs. Q#28 - Typical Hotline Script for Cancel Watch for SCED is Solving |
| Log | Log all actions. |
| ### SCED Data Input Failure |  |
| 1 | IF: - SCED receives data input failures and gives erroneous results; THEN: - Manually activate EBP, - Contact the Help Desk, - Initiate the Watch Hotline call - Notify Resource Operator to post the message on MIS Public, - Notify the Transmission Operator to make Hotline call to TOs. Q#29 - Typical Hotline Script for Watch for SCED Data Input Failure |
| 2 | Follow steps 4 and log in SCED Failure above as needed. |
| ### RLC Failure |  |
| 1 | The Resource Limit Calculator (RLC) can fail independently of AGC. If RLC fails, SCED will not function (invalid results), even though it shows available. A RLC failure will be displayed to the Operator in the upper right corner of the RLC display as follows: - Process Status: RLC Up (Normal Operation) - Process Status: RLC Down (will be displayed in RED when failed) - RLC (PI Alarm) will be flashing RED. |
| NOTE | Regulation is functioning, RRS is not. LFC (AGC) will automatically switch to EBP mode. |
| 2 | IF: - RLC has failed; THEN: - Verify the status of AGC - IF AGC is also failed, proceed to the EMS (LFC and RLC) Failure procedure - Contact the Help Desk, - Initiate a Watch Hotline call to QSEs - Notify Resource Operator to post the message on MIS Public - Notify Transmission Desk Operator to make Hotline call to TOs. Q#30 - Typical Hotline Script for Watch for RLC Failure |
| 3 | EMP Applications>Generation Area Status>Related Displays>ERCOT Nodal Summary MONITOR: - Regulation Service (Up/Dn) margins to ensure frequency can be adequately maintained. IF: - It is determined that remaining Regulation Service (Up/Dn) is no longer sufficient to maintain system frequency; THEN: - Enter the EBP increment/decrement as needed to control frequency to recall deployed Regulation. - Once the MW amount has ramped, the EBP amount will return to zero |
| 4 | WHEN: - RLC is restored; THEN: - Remove the Emergency Base Point flag, - Initiate Hotline call to cancel the Watch, - Notify Resource Operator to cancel MIS posting, - Notify Transmission Operator to cancel the Watch with TOs. Q#31 - Typical Hotline Script to Cancel Watch for RLC is Restored |
| Log | Log all actions. |
| ### LFC (AGC) Failure |  |
| NOTE | When LFC (AGC) is paused or suspended and RLC and SCED are functioning, then Regulation, RRS and EBP are not functioning. |
| 1 | IF: - LFC is not functioning as indicated by: - AGC is SUSPENDED or PAUSED OR - “Last AGC Cycle” time on Generation Area Status display is not updating; THEN: - Verify the status of RLC - If RLC is also failed, proceed to the next procedure “EMMS Failure” - If RLC is still functioning properly, - Contact Help Desk, - Continue with this procedure REFERENCE Display: EMP Applications>Generation Area Status>Nodal Operational Status>Resource Limits Data DETERMINE: - Which QSE has ample capacity to place on constant frequency control, THEN: - Issue an Operating Instruction to selected QSE to go on constant frequency, - As time permits, issue electronic Dispatch Instruction confirmation, - Choose “OPERATE AT CONSTANT FREQUENCY” as the Instruction Type from QSE Level When issuing a VDI or the confirmation, ensure the use of three-part communication: - Issue the Operating Instruction - Receive a correct repeat back - Give an acknowledgement - Place ERCOT AGC into ‘Monitor” mode. Typical Script to Instruct a QSE on Constant Frequency for LFC Failure: “This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is instructing you to go on constant frequency until further notice due to an LFC failure. The frequency bias to enter into your control system is [bias]. Please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.”If INCORRECT, repeat the process until the repeat back is correct. All Operating Instructions shall be in a clear, concise, and definitive manner. Ensure the recipient of the Operating Instruction repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 2 | THEN: - Initiate the Emergency Notice Hotline call to QSEs - Notify Resource Operator to post the message on MIS Public, - Notify Transmission Operator to make Hotline call to TOs. Q#32 - Typical Hotline Script for Emergency Notice a QSE is on Constant Frequency for LFC Failure |
| 3 | MONITOR: - Frequency and capacity availability for QSE on constant frequency, AND/OR - The QSE on constant frequency notifies ERCOT of capacity issue; THEN: - Determine available capacity for SCED and enter an operator manual offset, OR if no SCED room - Request RUC Operator to decommit a Resource |
| 4 | WHEN: - ERCOT AGC Control is functioning properly; THEN: - Issue an Operating Instruction to QSE to come off Constant Frequency, - Place ERCOT AGC back into “ON” mode, - Initiate Hotline to cancel the Emergency Notice to QSEs, - Notify Resource Operator to cancel the MIS posting, - Notify Transmission Operator to cancel the Emergency Notice with TOs. Typical Script to Instruct QSE to End Constant Frequency for LFC Functioning: “This is ERCOT Operator [first and last name]. At [xx:xx], LFC is now functioning, end constant frequency and return to normal. Please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. Q#33 - Typical Hotline Script to Cancel Emergency Notice for QSE on Constant Frequency for LFC Functioning: |
| Log | Log all actions. |
| ### EMMS (LFC and RLC/SCED) Failure |  |
| NOTE | Regulation, RRS, UDBP, BP, EBP, and manual offset not functioning. |
| 1 | LFC (AGC): - AGC is SUSPENDED or PAUSED, - “Last ACE crossing zero” time on the Generation Area Status page is not updating, - AGC operation adversely impacts the reliability of the Interconnection, - SCED and EMS are not functioning, - Problem cannot be resolved quickly RLC: - Process Status: RLC Down will be displayed in RED in the upper right hand corner of the RLC display - RLC (PI Alarm) will be flashing RED. REFERENCE Display: EMP Applications>Generation Area Status>Nodal Operational Status>Resource Limits Data DETERMINE: - Which QSE has ample capacity to place on constant frequency Control; THEN: - Issue an Operating Instruction to selected QSE to go on constant frequency - As time permits, issue an electronic Dispatch confirmation - Choose “OPERATE AT CONSTANT FREQUENCY” as the Instruction Type from QSE Level When issuing a VDI or the confirmation, ensure the use of three-part communication: - Issue the Operating Instuction - Receive a correct repeat back - Give an acknowledgement - Place ERCOT AGC into “Monitor” mode Typical Script to Instruct a QSE on Constant Frequency for LFC/SCED Failure: “This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is Instructing you to go on constant frequency until further notice due to an LFC and SCED failure. The frequency bias to enter into your control system is [bias]. Please repeat this back to me. That is correct, thank you”. All Operating Instructions shall be in a clear, concise, and definitive manner. Ensure the recipient of the Operating Instruction repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 2 | THEN: - Initiate the Emergency Notice Hotline call to QSEs, - Notify Resource Operator to post the message on MIS Public, - Notify Transmission Operator to make Hotline call to TOs Q#34 - Typical Hotline Script for Emergency Notice a QSE is on Constant Frequency for LFC and SCED failure: |
| 3 | MONITOR: - Frequency and Capacity availability for QSE on constant frequency, AND/OR - The QSE on Constant Frequency notifies ERCOT that they are having control issues; THEN: - Determine which QSE has the most available Capacity, - Issue a unit specific instructions to assist the QSE on Constant Frequency, - Choose “Other For Resource” as the Instruction Type |
| 4 | IF: - There is no longer any available capacity to issue unit specific deployments; THEN: - Request RUC Operator to commit a Resource |
| 5 | WHEN: - AGC and RLC is restored; THEN: - Instruct QSE to come off constant frequency by ending VDI, - Place ERCOT AGC back into “ON” mode, - Cancel VDI(s) for additional generation, if issued, - Initiate Hotline to cancel Emergency Notice to QSEs, - Notify Resource Operator to cancel MIS posting, - Notify Transmission Operator to cancel Emergency Notice with TOs. Typical Script to Instruct a QSE to end Constant Frequency for LFC Functioning, AGC/RLC Restored: “This is ERCOT Operator [first and last name]. At [xx:xx], LFC is now functioning, ERCOT is intructing you to end constant frequency. Please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. Q#35 - Typical Hotline Script to Cancel Emergency Notice with LFC Functioning, SCED valid: |
| Log | Log all actions. |

## 3.5	Monitor Capacity and Reserves and Respond to Shortages or Surplus

Procedure Purpose:  Monitoring sufficient operating reserves and capacity surplus.  Deploying/Recalling Non-Spin and manually Deploying/Recalling RRS.

| Protocol Reference | 6.5.7.6.2.2 (7) | 6.5.7.6.2.3 |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | EOP-002-3.1 R4, R6.1, R6.2 | IRO-005-3.1a R1.4, R1.5 |  |  |

| Version: 1 | Revision: 14 | Effective Date: June 30, 2016 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | The Day-Ahead process, the Adjustment Period process, and the Real-Time process must be utilized before ordering Resources to specific output levels with Emergency Base Point instructions. |
| ## Insufficient Generation |  |
| RMR | Prior to declaring EEA, start RMR Units available in the time frame of the emergency. RMR Units should be loaded to full capability. |
| Deploying Non-Spin | Triggers to deploy Non-Spin MONITOR: - The OpsMon Dashboard - MOS - 01 SCED GEN ONLINE and scroll down to Lookahead Load Ramping from MTLF - Avail CAP 30Min represents (HASL – Gen) – (30 minute load ramp) IF: - Avail_CAP_30Min < 0 THEN: - Coordinate with the Resource Operator to deploy half of available Non-Spin. IF: - Avail_CAP_30Min < -300, OR - PRC is < 2500 MW; THEN: - Coordinate with the Resource Operator to deploy all of available Non-Spin. |
| Recalling Non-Spin | WHEN: - Avail_CAP_30Min > 1000, AND - PRC is > 2800 MW; THEN: - Coordinate with the Resource Operator to recall half of the deployed Non-Spin. WHEN: - Avail_CAP_30Min > 1000, AND - PRC is > 3000 MW; THEN: - Coordinate with the Resource Operator to recall all of the deployed Non-Spin. |
| HASL Release – Manually Deploy RRS | Triggers to manually deploy RRS MONITOR: - “HASL – Load Ramp” value on the Generation Area Status display, this is HASL – (Gen + 5 minute load ramp) IF: - HASL – Load Ramp < = 200 MW; THEN: - Ensure all Non-Spin has been deployed first before manually deploying RRS. - Manually deploy 500 MW of RRS. IF: - After Resources have responded to the previous deployment, AND - HASL – Load Ramp < = 200 MW; THEN: - Manually deploy another 500 MW of RRS (it is incremental, enter 1,000). IF: - PRC < = 2000 MW; THEN: - Manually deploy all remaining RRS. |
| HASL - RRS Recall | WHEN: - HASL – (Gen + 5 minute load ramp) > 1600 MW AND/OR - PRC > = 3300 MW, AND - Frequency is 59.970 HZ or above; THEN: - Manually recall the RRS, which can be done in 500 MW steps. |
| ## Surplus Generation |  |
| SCED Surplus | MONITOR: - The Generation Area Status Page IF: - (GEN-LDL) < 200 MW; THEN: - Consult with RUC Operator to ensure HRUC is seeing the situation and is decommitting Resources, - If needed, request the RUC Operator to issue VDI to decommit a Resource to help alleviate the surplus |
| Log | Log all actions. |
| ## Valley Generation |  |
| Monitor | Market Operations>Reliability Unit Commitment>HRUC Displays>UC Displays>Output Display Menu>Generator Outputs>Generation Schedule OR Market Operations>Reliability Unit Commitment>HRUC Displays>UC Displays>Input Display Menu>Generation Self-Commitment Status |
| 1 | WHEN: - Two or more Generation plants (DUKE, FRONTERA, NEDIN and/or SILASRAY) are scheduled to go Off-Line at the same time; THEN: - Discuss with Transmission and Security Operator AND Shift Supervisor - Ensure AEP TO is notified with the shut down time and with at least an hours’ notice, they need to pre-posture reactive devices. |
| Log | Log all actions. |

# 3.9	Unannounced Constant Frequency Control Testing

Procedure Purpose: This procedure provides direction and guidelines for conducting unannounced testing to verify a QSE’s capability to operate in CFC mode.  Only QSEs with at least 350 MW of spinning reserve room will be tested.  QSEs shall be tested at least every three years.

| Protocol Reference | 6.6.9 |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 2.2.4.3 |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 3 | Effective Date: June 30, 2016 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - Testing will be coordinated with staff from Operations Analysis, they will select the QSE to test - EMMS Production personnel will be in the Control Room to take the EMS off AGC - The frequency bias can be found on the Generation Area Status display - The Constant Frequency Control Testing Document can be found in Section 2.11 of the Desktop Guide Real Time Desk. |
| START CFC Test | Typical Script for Constant Frequency Control Test: “This is ERCOT operator [first and last name]. At [time], ERCOT is conducting an unannounced test with [QSE] to test your ability to operate on constant frequency control mode. The frequency bias to enter into your control system is [bias]. You have five minutes to switch to CFC mode then hold for 15 minutes. I will give another call when you can return to normal operation. [QSE] please repeat this back to me. That is correct, thank you.” |
| END CFC Test | Typical Script to End Constant Frequency Control Test: “This is ERCOT operator [first and last name]. At [time], ERCOT is ending the unannounced constant frequency control test with [QSE]; please change your control mode back to normal. I will follow-up with an electronic Dispatch Instruction confirmation that you will need to acknowledge. [QSE] please repeat this back to me. That is correct, thank you.” |
| ISSUE Electronic Dispatch Instruction | Issue electronic Dispatch Instruction confirmation: - QSE Level - Instruction Type: Operate at Constant Frequency When issuing a VDI or when confirming the receipt of the confirmation, ensure the use of three-part communication: - Issue the Operating Instruction - Receive a correct repeat back - Give an acknowledgement |
| LOG | Make log entry |

## 4.0	Security Constrained Economic Dispatch

## 4.1	Managing SCED

Procedure Purpose: To ensure that a SCED solution has solved and that the solution is reasonable.

| Protocol Reference | 3.8.3 | 3.9.1(10) | 3.10.7.5.1(5) | 8.1.1.2(16) |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | IRO-002-2 R7 |  |  |  |

| Version: 1 | Revision: 19 | Effective Date: June 30, 2016 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Workflow Controller Messages |  |
| NOTE | The SCED Workflow Controller provides three color coded messages as indicated in the following: - GREEN – Informational (i) and Success (s) - BLUE – Warning (w) - RED – Error (e) and Fatal Error (f) |
| 1 | REVIEW REFERENCE DISPLAY: Market Operation>Real-Time Market>SCED Displays>Workflow>SCED Workflow Messages Monitor SCED Workflow Controller logs for “Warning” and “Error” messages. |
| 2 | IF: - The log indicates an “Error” or “Fatal Error”; THEN: - Contact the Help Desk and notify all Control Room staff, - Attempt to resolve the issue, refer to Desktop Guide Real Time Desk Section 2.5, - Refer to Section 3.3 “Managing SCED Failures” in this procedure. |
| ### SCED Solution Time Parameter |  |
| NOTE | Typically SCED should produce a solution within 20 seconds. It is highly desirable to have at least 3 executions of SCED in any 15 minute period. |
| Automatic Trigger | Verify that SCED is automatically triggered: - Periodically every 5 minutes - About 60 seconds after RRS is automatically deployed by LFC IF: - SCED is not automatically executed (but has not failed); THEN: - Manually execute SCED, - Immediately notify the Shift Supervisor and Operations Support Engineer, - Continue to manually execute SCED approximately every 5 minutes until the condition is corrected. |
| Manual Trigger | SCED may be manually triggered when the following is identified: - Frequency deviates +/-0.05 Hz for more than 5 minutes - Generation Resource trips and Frequency is > 59.91 Hz - When approximately 50% of Regulation has been deployed - Approximately 60 seconds after Generation Resources providing RRS have been deployed. - As frequently as needed after Load Resources providing RRS have been deployed. |
| LOG | Log all actions. |
| ### Quick Start Generation Resource |  |
| QSGR | A Generation Resource that in its cold-temperature state can come On-Line within ten minutes of receiving ERCOT notice and has passed an ERCOT Quick Start Generation Resource test that establishes an amount of capacity that can be deployed within a ten minute period. - These Resources can be viewed at ERCOT SharePoint > System Operations – Control Center > Quick Links > Approved Quick Start (QSGR) Resources |
| COP | The QSE for a QSGR that is available for deployment by SCED shall set the COP Resource Status ON, the COP LSL and HSL values to the expected sustainable LSL and HSL for the QSGR for the hour. If the QSGR is providing Non-Spin, then the A/S Resource Responsibility for Non-Spin shall be set to the Resource’s Non-Spin responsibility in the COP. If the Resource’s Non-Spin responsibility is greater than the difference between HSL and LSL, then the QSGR that is available for deployment by SCED shall set the COP LSL to zero. |
| Telemeter | The QSGR that is available for deployment by SCED shall telemeter a Resource Status of ON and an LSL of zero prior to receiving a deployment instruction from SCED. This status is necessary in order for SCED to recognize that the Resource can be Dispatched. The status of the breaker shall be open and the output of the Resource shall be zero in order for the State Estimator to correctly assess the state of the system. After being deployed for energy by SCED, the Resource shall telemeter an LSL equal to or less than the Resource’s actual output until the Resource has ramped to its physical LSL. After reaching its physical LSL, the QSGR shall telemeter an LSL that reflects its physical LSL. The QSGR that is providing Off-Line Non-Spin shall always telemeter an Ancillary Service Resource Responsibility for Non-Spin to reflect the Resource’s Non-Spin obligation and shall always telemeter an Ancillary Service Schedule for Non-Spin of zero to make the capacity available for SCED. A QSGR with a telemeter breaker status of open and a telemeter Resource Status of ON shall not provide Regulation or Responsive Reserve Service. |
| QSGR Decommitment | Please refer to Desktop Guide Common to Multiple Desks for the QSGR decommitment process. |
| QSGR Qualification Test | WHEN: - Conducting a QSGR qualification test for Operations Analysis; THEN: - Issue a VDI confirmation - Choose “OTHER_RES” as the Instruction Type from Resource level - Enter MW amount that the QSE is requesting to qualify its QSGR to provide. - Enter “QSGR Qualification Test” in “Other Information” - . When issuing a VDI or the confirmation ensure the use of three-part communication: - Issue the Operating Instruction - Receive a correct repeat back - Give an acknowledgement |
| ### Generation Resource Shut-down/Start-up Process |  |
| Shutdown/ Startup | Shut-down: - A QSE representing a Generation Resource that is not actively providing A/S (with the exception of Off-line Non-Spin) may only use a Resource Status of SHUTDOWN through telemetry that the Resource is operating in a shutdown sequence requiring manual control and is not available for Dispatch. Start-up: - A QSE representing a Generation Resource that is not actively providing A/S may only use a Resource Status of STARTUP through telemetry that the Resource is operating in a start-up sequence requiring manual control and is not available for Dispatch. |
| NOTE | QSEs can manage basepoint deviations by adjusting their telemetered ramp rate. |
| NOTE | When a Resource is carrying “Off-Line” Non-spin and that Non-Spin is being recalled, the QSE would continue to show the Non-Spin responsibility on the Resource that is shutting down. |
| ### Combine Cycle Generation Resources |  |
| NOTE | WHEN: - Combine Cycle Generation Resources are changing configuration creating basepoint deviations THEN: - QSEs will need to manage their telemetered HSL for proper basepoints. |
| ### Telemetry Issues that could affect SCED and/or LMPs |  |
| Not Dispatchable to SCED | REVIEW REFERENCE DISPLAY: EMS Applications>Generation Control>Resource Limit Calculation>RLC Unit Input Data and RLC Unit Output Data WHEN: - A QSE has telemetered more A/S on a specific Resource that is greater than their HSL, OR - A Resource is generating more than their telemetered HSL; THEN: - SCED will set the HDL=LDL=MW making the Resource undispatchable, - Request the QSE to make corrections to their telemetry (Resource status, Resource limits, A/S responsibilities, etc.) |
| QSE Override | IF: - The QSE cannot fix the issue in a timely manner; THEN: - Ask the Market Participant to over-ride the bad telemetry. |
| QSE unable to Override | IF: - For some reason, the QSE cannot override the bad telemetry; THEN - Request the Operations Support Engineer to override the bad telemetry, - Manually run SCED, if needed. |

## 5.0	Emergency Operation

## 5.1	Market Notices

Procedure Purpose: Guidelines for issuing Emergency Conditions and the four possible levels: Operating Condition Notices (OCN), Advisories, Watches, and Emergency Notices.

| Protocol Reference | 6.3.3 | 6.5.9.3 | 6.5.9.3.1 | 6.5.9.3.2 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.3.3 | 6.5.9.3.4 |  |  |
| Guide Reference | 4.2.1 | 4.2.2 | 4.2.3 | 4.2.4 |
| NERC Standard | EOP-001-2.1b R3.1 | IRO-005-3.1a R4 |  |  |

| Version: 1 | Revision: 23 | Effective Date: June 30, 2016 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### OCN |  |
| NOTE | Consider the severity of the potential Emergency Condition. The severity of the Emergency Condition could be limited to an isolated local area, or the condition might cover large areas affecting several entities, or the condition might be an ERCOT-wide condition potentially affecting the entire ERCOT System. |
| 1 | As instructed by the Shift Supervisor or when appropriate, issue an Operating Condition Notice (OCN). The OCN can be issued for any of the following reasons or to obtain additional information from Market Participants. - There is a projected reserve capacity shortage that could affect reliability and may require more Resources - When extreme cold weather is forecasted approximately 5 days away - When extreme hot weather is forecasted approximately 5 days away - When an approaching Hurricane / Tropical Storm is approximately 5 days away - Unplanned transmission Outages that may impact reliability - When adverse weather conditions are expected, ERCOT may confer with TOs and QSEs regarding the potential for adverse reliability impacts and contingency preparedness |
| ### Advisory |  |
| 1 | As instructed by the Shift Supervisor or when appropriate, issue an Advisory. The Advisory can be issued for any of the following reasons or to obtain additional information from Market Participants. - When an approaching Hurricane / Tropical Storm is approximately 3 days away - When extreme cold weather is forecasted approximately 3 days away - When extreme hot weather is forecasted approximately 1 to 3 days away - When conditions are developing or have changed and more Ancillary Services will be needed to maintain current or near-term reliability - ERCOT may exercise its authority to increase Ancillary Service requirements above the quantities originally specified in the Day-Ahead Market in accordance with ERCOT Procedures - When extreme weather or conditions require more lead-time than the normal Day-Ahead Market allows - Transmission system conditions are such that operations within security criteria are not likely or possible due to Forced Outages or other conditions unless a CMP exists - Loss of communications or a control condition is anticipated or significantly limited - ERCOT may require information from QSEs representing Resources regarding the Resources’ fuel capabilities. Requests for this type of information shall be for a time period of no more than seven days from the date of the request |
| ### Watch |  |
| 1 | As instructed by the Shift Supervisor or when appropriate, issue a Watch. The Watch can be issued for any of the following reasons or to obtain additional information from the Market Participants. - A projected reserve capacity shortage is projected with no market solution available that could affect reliability - When an approaching Hurricane / Tropical Storm is approximately 1 day away - When extreme cold weather is projected for next day or current day - When extreme hot weather is projected for next day or current day - Conditions have developed that require additional Ancillary Services in the Operating Period - Insufficient Ancillary Services or Energy Offers in the DAM or in SASM - Market-based congestion management techniques embedded in SCED will not be adequate to resolve transmission security violations - Forced Outages or other abnormal operating conditions have occurred, or may occur that would require ERCOT to operate with active violations of security criteria as defined in the Operating Guides unless a CMP exists - ERCOT varies from timing requirements or omits one or more Day-Ahead or Adjustment Period and Real-Time procedures. - ERCOT varies from timing requirements or omits one or more scheduling procedures in the Real-Time process. - The SCED process fails to reach a solution, whether or not ERCOT is using one of the measures in Failure of the SCED Process. - The need to immediately procure Ancillary Services from existing offers - ERCOT may instruct TOs to reconfigure transmission elements as necessary to improve the reliability of the system - ERCOT may require information from QSEs representing Resources regarding the Resources’ fuel capabilities. Requests for this type of information shall be for a time period of no more than seven days from the date of the request |
| ### Emergency Notice |  |
| 1 | As instructed by the Shift Supervisor or when appropriate, issue an Emergency Notice. The Emergency Notice can be issued for any of the following reasons or to obtain additional information from Market Participants. - Loss of Primary Control Center functionality - Load Resource deployment for North-Houston voltage stability - ERCOT cannot maintain minimum reliability standards (for reasons including fuel shortages) during the Operating Period utilizing every Resource practically obtainable from the market - Immediate action cannot be taken to avoid or relieve a Transmission Element operating above its Emergency Rating - ERCOT forecasts an inability to meet applicable Reliability Standards and has exercised all other reasonable options - A transmission condition has been identified that requires emergency energy from any of the DC-Ties or curtailment of schedules - The Transmission Grid is such that a violation of security criteria as defined in the Operating Guides presents the threat of uncontrolled separation or cascading outages, large-scale service disruption to Load (other than Load being served from a radial transmission line) and/or overload of Transmission Elements, and no timely solution is obtainable through SCED or CMPs - When extreme cold weather is beginning to have an adverse impact on the System - When extreme hot weather is beginning to have an adverse impact on the System - When Hurricane / Tropical Storm is in the ERCOT Region and is beginning to have an adverse impact on the System |
| ### Operating Condition Script |  |
| Hotline | Communications must specify the severity of the situation, the area affected, the areas potentially affected, and the anticipated duration of the Emergency Condition. Notify QSEs: Q#46 - Typical Hotline Script for Operating Condition [OCN/Advisory/Watch/Emergency] |
| Post | - All notices must be posted on MIS Public. - For “free form” messages, the “Notice Priority” will be specified as follows: - Operational Information/OCN type messages – low priority - Advisory/Watch type messages – medium priority - Emergency type messages – high priority |
| Hotline Cancellation | Q#47 - Typical Hotline Script to Cancel Operating Condition [OCN/Advisory/Watch/Emergency] |
| Log | Log all actions. |
| ### Specific Scripts for Transmission Operator [State Estimator/RTCA/VSAT] |  |
| NOTE | - At times, the Transmission operator takes the lead on the issuance of Hotline calls for specific procedures they have. The following scripts are to help guide you when specific procedures don’t exist for the Real-Time operator. |
| State Estimator/ RTCA Not Solved In 30 MIN | - Q#48 - Typical Hotline Script for Advisory for State Estimator / RTCA not solved in 30 Min - Q#49 - Typical Hotline Script to Cancel Advisory for State Estimator / RTCA now solving |
| VSAT Not Solved In 30 MIN | Q#50 - Typical Hotline Script for Advisory for VSAT not solved in 30 Min: Q#51 - Typical Hotline Script Cancel Advisory for VSAT now solving |
| Qualifying Facility Instructed to Operate below LSL | Q#52 - Typical Hotline Script for Emergency Notice for instructing Qualifying Facility to operate offline/below LSL Q#53 - Typical Hotline Script to Cancel Emergency Notice for Qualifying Facility to operate offline/below LSL |
| New GTC | Q#54 - Typical Hotline Script for OCN for a new Generic Transmission Constraint |
| Transmission Watch | Q#55 - Typical Hotline Script for Transmission Watch for Post-Contingency Overload Q#56 - Typical Hotline Script Cancel Transmission Watch for Post-Contingency Overload |

## 5.5	Restoration of Primary Control Center Functionality

Procedure Purpose: To be performed once the Real-Time Operator has arrived at ACC.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| ### Version: 1 | Revision: 7 | Effective Date: June 30, 2016 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | Before normal operation can be restored, be sure to communicate with the other desks to determine the current state of the grid and any communications that may have taken place with Market Participants. |
| Restoring Frequency Control | WHEN: - SCED is functional; THEN: - Remove the QSE that was instructed on constant frequency by ending the VDI. - Put ERCOT AGC into “ON” mode. |
| Return to Normal QSE Notification | When ready to resume normal operations: - Check with RUC Operator on desk status to include in hotline call if appropriate - Place the following Hotline call to the QSEs: - Q#57 - Typical Hotline Script to Cancel Emergency Notice and Restore primary control center: |
| Log | Log all actions. |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Frosch, Hartmann, Stone, and Barcalow | Prepares | November 10 , 2010 |
| Frosch and Hartmann | Procedure writers and editors | November 29, 2010 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2010 |
| Frosch, Foster and Hartmann | Procedure writers and editors | January 3, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 26, 2011 |
| Frosch and Hartmann | Procedure writers and editors | March 23, 2011 |
| Frosch and Hartmann | Procedure writers and editors | April 20, 2011 |
| Frosch and Hartmann | Procedure writers and editors | June 6, 2011 |
| Frosch and Hartmann | Procedure writers and editors | July 18, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 1, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 30, 2011 |
| Frosch and Hartmann | Procedure writers and editors | September 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | October 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 16, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | April 25, 2012 |
| Frosch and Hartmann | Procedure writers and editors | May 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | May 30, 2012 |
| Barcalow, Frosch and Hartmann | Procedure writers and editors | July 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | August 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | October 26, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 26, 2013 |
| Frosch and Hartmann | Procedure writers and editors | May 28, 2013 |
| Frosch and Hartmann | Procedure writers and editors | July 8, 2013 |
| Frosch and Hartmann | Procedure writers and editors | August 7, 2013 |
| Frosch and Hartmann | Procedure writers and editors | September 25, 2013 |
| Frosch and Hartmann | Procedure writers and editors | December 11, 2013 |
| Frosch and Hartmann | Procedure writers and editors | December 20, 2013 |
| Frosch, Gaddy, Hartmann and Solis | Procedure writers and editors | April 1, 2014 |
| Frosch, Gaddy and Hartmann | Procedure writers and editors | May 27, 2014 |
| Frosch and Hartmann | Procedure writers and editors | July 29, 2014 |
| Frosch and Hartmann | Procedure writers and editors | September 29, 2014 |
| Drummond, Frosch and Hartmann | Procedure writers and editors | December 10, 2014 |
| Frosch and Thompson | Procedure writers and editors | December 19, 2014 |
| Frosch and Hartmann | Procedure writers and editors | February 25, 2015 |
| Frosch and Hartmann | Procedure writers and editors | March 25, 2015 |
| Frosch and Hartmann | Procedure writers and editors | April 29, 2015 |
| Frosch, Hartmann and Gaddy | Procedure writers and editors | July 13, 2015 |
| Hartmann and Gaddy | Procedure writers and editors | December 22, 2015 |
| Hartmann, Gaddy and Frosch | Procedure writers and editors | February 23, 2016 |
| Hartmann and Gaddy | Procedure writers and editors | April 22, 2016 |
| Hartmann, Gaddy and Frosch | Procedure writers and editors | June 24, 2016 |

Manual Change History

| Procedure | Ver/Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All Sections | 1.0 / 0 | New procedures for all sections for Nodal implementation | November 28, 2010 |
| 2.4 3.1 3.2 3.4 3.5 3.6 4.2 5.3 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Updated Categories and Priorities Updated Response to High Frequency steps 15, 20 and 25 minutes and Response to Low Frequency step 15 Updated steps Failure Indication/Issues and QSE Capacity Issues Updated steps AGC/RLC Issues, System Wide Capacity Issue and AGC/RLC Issues Resolved Updated step 1 Updated step Capacity Surplus Updated step 2, 3, 4 and 5 Updated all steps of “Implement Level 2B” | December 1, 2010 |
| 4.1 4.2 5.2 | 1.0 / 1 1.0 / 2 1.0 / 1 | Updated step “MP unable to Override” Updated step 1 & 2 Updated step 1 in sections WATCH and Advisory | December 15, 2010 |
| 3.1 3.2 3.3 3.4 4.1 5.1 5.4 | 1.0 / 2 1.0 / 2 1.0 / 1 1.0 / 2 1.0 / 2 1.0 / 1 1.0 / 1 | Updated step “BAAL” Updated step “AGC Issues Resolved” Updated step “Hotline” Updated step “Failure Indications, AGC/RLC Issues, System Wide Capacity Issue, AGC/RLC Issues Resolved” Updated step 2 in “Workflow Controller Messages”, added new procedure “Exceeding West – North Stability Limit”, updated Note in “Generation Resource Shut-down/Start-up Process” Updated step 1 in “Watch” and step Hotline in “Scripts” Updated step 1 in “Move from EEA level 3 to EEA lever 2B” | January 5, 2011 |
| 2.4 2.5 2.6 2.7 3.1 3.2 3.3 3.4 3.5 4.1 4.2 5.1 5.2 5.3 5.4 5.5 6.1 6.2 6.3 | 1.0 / 0 1.0 / 2 1.0 / 0 1.0 / 0 1.0 / 3 1.0 / 3 1.0 / 2 1.0 / 2 1.0 / 1 1.0 / 3 1.0 / 3 1.0 / 2 1.0 / 2 1.0 / 2 1.0 / 2 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Added new procedure Changed procedure number Added new procedure Added new procedure Updated sections “Maintain System Frequency”, “Response to High Frequency”, “Response to Low Frequency” and “Actions when Frequency Telemetry in Incorrect. Combined sections 3.3, 3.4 & 4.2 into 3.2 Changed 3.5 “Potential DCS Event” to 3.3 & updated whole procedure Changed 3.6 “Monitor Capacity Reserves & Respond to Capacity Issues to 3.4 Changed 3.7 “Monitor and Control Time Error Correction to 3.5 & updated script Deleted Exceeding West-North Stability Limit Deleted Procedure Updated script Updated step 1 in “Advisory” and “Watch” Updated all steps Updated all steps Updated all steps Updated all steps Updated all steps Updated OCN | January 31, 2011 |
| 2.6 3.2 3.3 3.4 3.6 5.1 5.2 | 1.0 / 1 1.0 / 4 1.0 / 3 - / 3 1.0 / 0 1.0 / 3 1.0 / 3 | Updated step Site Failovers Updated step 3 in SCED Failure, step 4 in RLC Failure, Note in LFC (AGC) Failure and step 2 in EMS (LFC and RLC/SCED Failure Updated step 3 Updated step Capacity Shortage Added new procedure Updated Watch and Emergency Notice All step 1’s | March 25, 2011 |
| 2.6 3.1 3.2 3.3 3.6 5.1 5.4 5.5 | 1.0 / 2 1.0 / 4 1.0 / 5 1.0 / 4 1.0 / 1 - / 4 1.0 / 3 1.0 / 2 | Added steps and updated whole procedure Added new step to Maintain System Frequency and updated Response to High Frequency & Response to Low Frequency Updated steps 2, 3, 5 in SCED Failure; steps 2, 3, 4, 6 in RLC Failure; steps 1, 3 in LFC (AGC) Failure; steps 2, 5 in EMS (LFC and RLC/SCED) Failure Updated NERC Recovery Criteria, step 1 & 4 Updated 1st script Updated step 1 in Watch and Emergency Notice and step Post Updated 1st and 2nd script in Restore Firm Load, Updated 1st in Move From EEA Level 3 to EEA Level 2B Updated step 3 | April 22, 2011 |
| 3.3 5.1 5.3 5.4 6.1 6.2 6.3 6.4 | 1.0 / 5 1.0 / 5 1.0 / 3 1.0 / 4 1.0 / 2 1.0 / 0 1.0 / 2 1.0 / 2 | Updated step NERC Recovery Criteria Updated all step 1’s Updated step 1 in Implement EEA Level 1, step 1 in Implement EEA Level 2A, added note and updated step 2 in Implement EEA Level 2B, step 1 in Implement EEA Level 3 Updated all step 1’s Updated all steps Added new procedure Updated section number and all steps Updated section number and all steps | June 8, 2011 |
| 2.6 3.1 5.1 5.2 5.3 5.4 8.1 | 1.0 / 3 1.0 / 5 1.0 / 6 1.0 / 4 1.0 / 4 1.0 / 5 1.0 / 1 | Added step If EBPs are needed”, updated step IF EBPs are needed and W-N was Active before site failover started Added step Hydro, updated step Frequency Deviations Updated step Watch Updated all steps Updated 1st note, step 1 in EEA level 1 & 2A Updated step 1 in Move for EEA level 1 to 0 Added Market Participant Backup Control Center Transfer procedure | July 20, 2011 |
| 3.1 3.2 3.4 4.1 6.4 6.5 | 1.0 / 6 1.0 / 6 1.0 / 4 1.0 / 4 1.0 / 0 1.0 / 3 | Updated step Monitor, 15 minutes, 20 minutes and 25 minutes in Response to High Frequency Updated step 2 in LFC Failure, step 4 & 5in EMS Failure Updated step Capacity Surplus Updated step 2 in Workflow Controller Messages Added new procedure “Extreme Hot Weather” Changed section number | August 3, 2011 |
| 2.7 3.1 5.1 5.2 5.3 5.4 6.4 7.1 | 1.0 / 1 1.0/ 7 1.0 / 7 1.0 / 5 1.0 / 5 1.0 / 6 1.0 / 1 1.0 / 1 | Updated step Hotline Call Updated NERC Standard reference table Added projected reserve capacity shortage and Extreme Hot Weather in Watch Updated step 1 in Advisory & Watch Updated 2nd Note, step 1 in Implement EEA 1, step Media Appeal & 1 in Implement EEA 2A, 1st Note & step 2 in Implement EEA 2B Added Note to Move From EEA 3 to EEA 2B and Move From EEA 2A to EEA 1 Updated temperature from 102 to 103 Updated 4th note and step 1 | September 1, 2011 |
| 3.2 5.3 5.4 | 1.0 / 7 1.0 / 6 1.0 / 7 | Updated SCED Failure step 2 and 3, RLC Failure step 3 and LFC (AGC) Failure step 3 Combined EEA 2A & B per NPRR 379 Combined EEA 2 A & B per NPRR 379 | October 1, 2011 |
| 3.2 | 1.0 / 8 | Updated script for LFC and EMS Failure | November 1, 2011 |
| 2.4 2.6 4.1 5.1 6.3 | 1.0 / 1 1.0 / 4 1.0 / 5 1.0 / 8 1.0 / 3 | Added step Review, Updated “Site Failover with W-N Active” Added Note to Large Resource Trips or Runbacks Updated Post in “Scripts” Updated “OCN” and “Advisory” All procedures in this manual have been reviewed. | December 15, 2011 |
| 1.2 3.1 4.1 8.1 | 1.0 / 1 1.0 / 7 1.0 / 6 - / 2 | Updated Scope Updated Response to High Frequency & Response to Low Frequency Updated Large Resource Trips or Runbacks, Quick Start Generation Resource Updated Market Participant Backup Control Center Transfer | January 19, 2012 |
| 2.1 3.1 5.1 5.3 7.1 8.1 | 1.0 / 1 1.0 / 8 1.0 / 7 1.0 / 9 1.0 / 7 1.0 / 2 1.0 / 3 | Updated paragraph 4 Updated BAAL Updated Desktop Guide reference & step QSE Override & QSE unable to Override Updated step 1 in Watch Updated Step 1 in Implement EEA Level 1 Updated Desktop Guide references Changed title names, updated steps 1 & 3 & step Power System Stabilizers (PSS) & Automatic Voltage Regulators (AVR) | March 1, 2012 |
| 2.1 3.1 3.2 3.3 3.5 4.1 5.1 6.2 6.3 6.4 8.1 | 1.0 / 2 1.0 / 9 1.0 / 9 1.0 / 6 1.0 / 2 1.0 / 8 1.0 / 10 1.0 / 4 1.0 / 2 1.0 / 4 1.0 / 4 | Changed TSO, DSP to TO Changed Shift Engineer to Operations Support Engineer, removed Automatic SCED Runs & Hydro Generation in Fast Response Mode, updated Note, Monitor/Deploy, 15 minutes, 20 minutes in Response to Low Frequency Updated step 2, 4 & 5, added SCED Data Input Failure, updated RLC Failure, LFC Failure, & EMMS Failure sections Updated Nerc Recovery Criteria step & step 3 Updated Requirements and Notes Changed Shift Engineer to Operations Support Engineer, deleted Large Resource Trips or Runbacks section Updated OCN, Advisory, Watch, Emergency Notice sections Deleted Cold Weather, replaced with Extreme Cold Weather Section changed to Extreme Hot Weather, added OCN and Emergency Notice steps Section number changed Changed Shift Engineer to Operations Support Engineer | May 1, 2012 |
| 3.1 3.4 5.2 | 1.0 / 10 1.0 / 5 1.0 / 6 | Added back step Hydro Generation Operating in Synchronous Condenser Fast Response Mode Updated to reflect changes in the TAC approved Non-Spin document Updated to reflect changes in the TAC approved Non-Spin document | May 14, 2012 |
| 2.6 5.3 5.4 6.3 | 1.0 / 5 1.0 / 8 1.0 / 8 1.0 / 3 | Updated Site Failover step Updated EILS to ERS per NPRR 451 Updated EILS to ERS per NPRR 451 Updated EILS to ERS per NPRR 451 | June 1, 2012 |
| 1.3 2.6 5.1 5.3 5.4 6.2 6.3 7.1 | 1.0 / 1 1.0 / 6 1.0 / 11 1.0 / 9 1.0 / 9 1.0 / 5 1.0 / 4 1.0 / 3 | Removed ERCOT Shift Supervisor paragraph Updated all steps Updated all step 1’s Updated 2nd note, added TCEQ, & XML for ERS Clarified LR and ERS recalls Updated script for Emergency Notice Updated script for Emergency Notice Updated 4th note | July 16, 2012 |
| 2.6 3.1 4.1 5.3 | 1.0 / 7 1.0 / 11 1.0 / 9 1.0 / 10 | Added note to step Database Load Updated Frequency Deviations and Monitor Frequency for the Loss of EMS or Site Failover Incorporated NPRR348 Added 30 MIN ERS and updated steps 1, 2 & 3 on Implement EEA Level 1 | August 29, 2012 |
| 2.2 2.5 3.5 4.1 5.3 | 1.0 / 1 1.0 / 3 1.0 / 3 1.0 / 10 1.0 / 11 | Added Hotline Call Communication Updated step 3 Updated per NOGRR100 Added Note to Shut-down/Start-up Process and new Combine Cycle Generation Resources section Updated ERS scripts All procedures in this manual have been reviewed. | November 1, 2012 |
| 2.5 3.1 3.2 3.3 3.4 3.5 3.6 3.7 5.4 | 1.0 / 4 1.0 / 12 1.0 / 0 1.0 / 10 1.0 / 7 1.0 / 6 1.0 / 4 1.0 / 2 1.0 / 10 | Updated step 3 Updated BAAL New procedure, Monitor Large Ramp Events Updated section # & SCED failure step 2 Updated section # Updated section # Updated section # Updated section # Updated Cancel Watch All procedures in this manual have been reviewed. | March 1, 2013 |
| 2.6 2.7 3.1 3.2 3.3 3.4 3.7 4.1 5.1 5.2 5.3 5.4 5.5 6.1 6.2 6.3 6.4 | 1.0 / 8 1.0 / 2 1.0 / 13 1.0 / 1 1.0 / 11 1.0 / 8 1.0 / 3 1.0 / 11 1.0 / 12 1.0 / 8 1.0 / 12 1.0 / 11 1.0 / 3 1.0 / 3 1.0 / 6 1.0 / 5 1.0 /5 | Updated scripts Updated scripts Updated Monitor Frequency for the Loss of EMS or Site Failover & Actions when Frequency Telemetry is Incorrect Updated scripts Updated scripts Updated script Updated scripts Added QSGR Decommitment step to QSGR Added Generic and Specific scripts Updated Note and scripts Updated TCEQ section and scripts Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts Correct spelling and updated script | June 1, 2013 |
| 2.6 3.1 3.2 3.8 5.1 5.3 5.4 | 1.0 / 9 1.0 / 14 1.0 / 2 1.0 / 0 1.0 / 13 1.0 / 13 1.0 / 12 | Changed title name & updated step EMS Changes & added MMS Changes Updated steps Base Point Deviation & 10 Minutes Updated 1st note Moved procedures from Resource desk Updated step 1 in Watch & Emergency Notice Updated step Pilot Project WS ERS Updated step Reserves | July 15, 2013 |
| 2.6 3.2 3.8 4.1 | 1.0 / 10 1.0 / 3 1.0 / 1 1.0 / 12 | Updated MMS Changes Updated 1st Note Updated Unit & Load RRS Shortage & Not Dispatchable to SCED Updated Shutdown/Startup | August 9, 2013 |
| 3.8 | 1.0 / 2 | Updated Unit RRS Shortage, Load RRS Shortage, REG Shortage, & added Real-Time Non-Spin Shortage | September 27, 2013 |
| 2.4 3.1 3.2 3.3 3.4 3.5 3.7 4.1 5.1 5.2 5.3 5.4 5.5 6.1 6.2 6.3 6.4 7.1 8.1 | 1.0 / 2 1.0 / 15 1.0 / 4 1.0 / 12 1.0 / 9 1.0 / 7 1.0 / 4 1.0 / 13 1.0 / 14 1.0 / 9 1.0 / 14 1.0 / 13 1.0 / 4 1.0 / 4 1.0 / 7 1.0 / 6 1.0 / 6 1.0 / 4 1.0 / 5 | Updated step Log Updated step Frequency Deviations & step Log Updated step Log Updated step Log Updated step Log Added step RMR & updated step Log Updated step Log Updated step Log Updated step Log Updated step Log Updated step Log Updated step Log Updated step Log Updated step Log Updated step Log Updated step Log Updated note and step Log Updated step Log Added & updated step Log All procedures in this manual have been reviewed | December 13, 2013 |
| 2.6 3.3 5.1 | 1.0 / 11 1.0 / 13 1.0 / 15 | Updated for NPRR542 Updated for NPRR542 Updated for NPRR542, deleted West to North GTL and updated procedure for North to Houston to a new GTL | January 1, 2014 |
| 2.6 3.1 3.3 3.5 3.6 4.1 5.3 5.4 6.4 8.1 | 1.0 / 12 1.0 / 16 1.0 / 14 1.0 / 8 1.0 / 5 1.0 / 14 1.0 / 15 1.0 / 14 1.0 / 7 1.0 / 6 | Updated Site Failover Complete Updated VDI information, step Monitor/Deploy & step 10 Minutes in Response to Low Frequency Updated VDI information Updated VDI information Updated step Terminating Time Error Correction Updated VDI information Updated ERS, Media appeal, TCEQ and VDI information Updated steps Reserves and 1 in Restore firm load and step 2 in Move From EEA Level 2 to EEA Level 1 Updated Note Updated Requests to Decommit Self-committed Resource in Operating Period | April 4, 2014 |
| 2.2 3.1 3.3 4.1 5.1 5.2 6.2 6.3 | 1.0 / 2 1.0 / 17 1.0 / 15 1.0 / 15 1.0 / 16 1.0 / 10 1.0 / 8 1.0 / 7 | Added VDIs to Master QSEs Updated step BAAL Updated SCED Failure & SCED Data Input Failure steps Updated QSGR in Quick Start Generation Resource Added Note, updated Market Notices Advisory & Watch Updated Watch steps Updated Emergency Notice step Updated Emergency Notice step | June 1, 2014 |
| 3.5 5.3 | 1.0 /9 1.0 / 16 | Updated Deploying Non-Spin, added HASL Release & Recall Added Media Appeal | August 1, 2014 |
| 4.1 5.1 5.3 | 1.0 / 16 1.0 / 17 1.0 / 17 | Updated Reference section step 2 Updated Generic Script Added HASL Release step | October 1, 2014 |
| 2.3 2.4 2.6 3.3 3.5 5.1 5.3 | 1.0 / 1 1.0 / 3 1.0 / 13 1.0 / 16 1.0 / 10 1.0 / 18 1.0 / 18 | Updated all steps Updated step Send E-mail Deleted Site Failover with W-N Active & updated step If EBPs are Needed Updated 1st note & updated scripts Added new procedure, “Valley Generation” Updated GMD scripts Updated scripts to consolidate All procedures in this manual have been reviewed | December 15, 2014 |
| 6.2 | 1.0 / 9 | Updated Note and scripts | December 22, 2014 |
| 2.2 3.1 3.2 3.5 3.9 6.2 | 1.0 / 3 1.0 / 181.0 / 5 1.0 / 11 1.0 / 0 1.0 / 10 | Added Dispatch and VDI definitions Updated Objective and BAAL Updated procedure Updated step 1 and added Log on Valley Generation Added new procedure for NOGRR136 Updated scripts | March 1, 2015 |
| 3.1 3.3 3.5 3.10 4.1 5.1 | 1.0 / 19 1.0 / 17 1.0 / 12 1.0 / 0 1.0 / 17 1.0 / 19 | Clarification to step Frequency Deviation & Hydro Operating in Synch. Condenser Mode Updated Dispatch Instruction scripts Clarification to step HASL Release Manually Deploy RRS New GMD procedure Updated Dispatch Instruction scripts Deleted script for GMD | March 30, 2015 |
| 2.6 2.7 3.2 3.3 3.4 3.63.7 3.10 5.1 5.2 5.3 5.4 5.5 6.1 6.2 6.3 6.4 | 1.0 / 14 1.0 / 3 1.0 / 6 1.0 / 18 1.0 / 10 1.0 / 6 1.0 / 5 1.0 / 1 1.0 / 20 1.0 / 11 1.0 / 19 1.0 / 15 1.0 / 5 1.0 / 5 1.0 / 11 1.0 / 8 1.0 / 8 | Moved scripts to new script procedure Moved scripts to new script procedure Updated 1st note and moved scripts to new script procedure Updated step 2 on SCED Data Input Failure & moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Updated 4th bullet on Emergency Notice & moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure | May 1, 2015 |
| All Sections 2.6 3.5 3.9 3.10 5.1 5.2 6.3 | 1.0 / 1 1.0 / 15 1.0 / 13 1.0 / 1 1.0 / 2 1.0 / 21 1.0 / 12 1.0 / 9 | Added a “Q” for numbered QSE scripts Renamed section to Site Failovers and Database Loads Updated link for Monitor in the Valley Generation Updated 1st Note Updated Procedure Purpose and removed script Updated Specific Scripts, New GTC Updated Q#1, Q#2, Q#3, & Q#4 Script titles Removed Watch script | July 15, 2015 |
| 2.6 3.2 3.3 3.4 3.6 3.7 3.9 3.10 5.1 5.2 5.3 5.4 5.5 6.1 6.2 6.3 6.4 | 1.0 / 16 1.0 / 7 1.0 / 19 1.0 / 11 1.0 / 7 1.0 / 6 1.0 /2 1.0 / 3 1.0 / 21 1.0 / 13 1.0 / 20 1.0 / 16 1.0 / 6 1.0 / 6 1.0 / 12 1.0 / 10 1.0 / 9 | Updated step MMS Changes Typical Script Q#19 Updated step Site Failover Q#20 Updated step Site Failover Complete Q#21 Updated Step If EBP’s are needed Q#22 Updated step Site Failover Complete If EBP’s were needed Q#23 Updated step 2 Q#26 Updated SCED Failure step 2 Q#27 & step 4 Q#28 Updated SCED Data Input Failure step 1 Q#29 Updated RLC Failure step 2 Q#30 & step 4 Q#31 Updated LFC (AGC) Failure step 1 Typical Script step 2 Q#32, step 4 Typical script & Q#33 Updated EMMS (LFC and RLC/SCED) Failure step 1 Typical Script, step 2 Q#34, step 5 Typical Script & Q#35 Updated step 3 Q#36 Updated step Initiating Time Error Correction Q#37 Updated step Terminating Time Error Correction Q#38 Updated step Issue Watch and Deploy Non-Spin Q#39 Updated step Issue Emergency Notice & Deploy Load Resources Q#40 Updated step Recall Load Resources Q#41 Updated step Recall Non-Spin Q#42 Updated step Start CFC Test & End CFC Test Typical Scripts Updated step 1 Q#43 Updated step K Level Increases/Decreases Q#44 Updated step Cancel Q#45 Updated Title Operating Condition Script Updated step Hotline Q#46 Updated step Hotline Cancellation Q#47 Updated Title Specific Scripts for Transmission Operator [State Estimator/RTCA/VSAT] Updated step State Estimator/RTCA Not Solved In 30 MIN Q#48 & Q#49 Updated step VSAT Not Solved In 30 MIN Q#50 & Q#51 Updated step Qualifying Facility Directed to Operate Below LSL Q#52 & Q#53 Updated step New GTC Q#54 Updated step Transmission Watch Q#55 & Q#56 Updated Advisory step Issue Advisory Q#1 Updated Advisory step Cancel Advisory Q#2 Updated Watch step Issue Watch Q#3 Updated Watch step Cancel Watch Q#4 First Note, Updated Implement EEA Level 1 step EEA 1 PRC <2300 Q#5 & Q#6 Updated Implement EEA Level 2 step ERS Resources Q#7 Updated Implement EEA Level 2 step Load Resources Q#8 Updated Implement EEA Level 2 step When ERS Business Hours Change Q#9 Updated Implement EEA Level 3 step When ERS Business Hours Change Q#12, and Implement NPRR708 for EEAUpdated Restore Firm Load step 1 Q#13 Updated Move From EEA Level 3 to EEA Level 2 step 1 Q#14 Updated Move From EEA Level 2 to EEA Level 1 step 1 Q#15 Updated Move From EEA Level 1 to EEA Level 0 step 1 Q#16 Updated Cancel Watch step 1 Q#17 Updated step Return to Normal QSE Notification Q#57 Updated step Emergency Notice Q#61 Updated step Emergency Notice Q#65 Updated step Emergency Notice Q#69 Updated step OCN/Advisory/Watch Q#70 All procedures in this manual have been reviewed | December 31, 2015 |
| 1.3 2.1 3.3 5.1 | 1.0 / 2 1.0 / 3 1.0 / 20 1.0 / 22 | Removed Interchange Coordinator Updated System Operator Responsibility and Authority Updated SCED Failure Note Corrected spelling Qualifying Facility Directed to Operate below LSL Q#52 | March 1, 2016 |
| 2.4 3.1 3.2 4.1 | 1.0 / 4 1.0 / 20 1.0 / 8 1.0 / 18 | Added 2nd Send E-Mail Updated Frequency bias and BAAL step Updated Down Ramp Event step 2 Updated QSGR Qualification Test | April 29, 2016 |
| 2.1 2.2 3.1 3.3 3.5 3.9 4.1 5.1 5.5 | 1.0 / 4 1.0 / 4 1.0 / 21 1.0 / 21 1.0 / 14 1.0 / 3 1.0 / 19 1.0 / 23 1.0 / 7 | Updated for COM-002-4 Updated for COM-002-4 Updated for BAL-001-2 and COM-002-4 Updated for COM-002-4 Updated Deploying Non-Spin step Updated for COM-002-4 Updated for COM-002-4 Updated for COM-002-4 Updated for COM-002-4 | June 30, 2016 |