## Power Operations Bulletin # 749

ERCOT has posted/revised the Reliability Unit Commitment manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

## http://www.ercot.com/mktrules/guides/procedures/index.html

# 2.	General

## 2.1	System Operator Responsibility and Authority

Procedure Purpose: To ensure the System Operators know their roles, responsibility and authority.

| Protocol Reference | 6.5.1.1 | 6.5.1.2(3) | 6.5.2 | 6.5.3(1) |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.5.2(1) |  |  |  |
| NERC Standard | EOP-002-3.1 R1 | IRO-001-1.1 R3 | PER-001-0.2 R1 | TOP-001-1a R1 |

| Version: 1 | Revision: 4 | Effective Date: , 2016 |
| --- | --- | --- |

The System Operator (SO) shall, in accordance with NERC Reliability Standards, have clear decision-making authority to act and to direct actions to be taken by Transmission Operators, Generator Operators, and Transmission Service Providers within its Reliability Coordination Area to preserve the integrity and reliability of the Bulk Electric System during both normal and emergency conditions.  These actions shall be taken without delay, but not longer than 30 minutes which may include the shedding of firm load without obtaining approval from higher-level personnel.  The ERCOT System Operator represents the following NERC functional entities collectively for the ERCOT ISO at any time:

- Reliability Coordinator

- Balancing Authority

- Transmission Operator

The SO on duty is, in accordance with the ERCOT Protocols, Operating Guides, and NERC Reliability Standards, and acting as the Balancing Authority, Transmission Operator, and Reliability Coordinator shall request and receive information required to continually monitor the operating conditions and request that individual Market Participants (MPs) make changes, which will assure the Security and Reliability of the ERCOT System.

The SO issues Dispatch Instructions for the Real-Time Operation of Transmission Facilities to a TO, and to a QSE for the Real-Time Operation of a Resource.

The SO shall, on an ERCOT-wide basis, coordinate the ERCOT System Restoration (Black Start) Plan.  The SO shall implement the Black Start Plan and shall direct the reconnection efforts of the islands, established by restoration activities.  The SO shall coordinate the mutual assistance activities of the ERCOT Participants during system restoration activities.

The SO shall consider all equipment operating limits when issuing Dispatch Instructions except as stated in Protocol Section 6.5.9, Emergency Operations, if a Dispatch Instruction conflicts with a restriction that may be placed on equipment from time to time by a TO, or a Generation Resource’s QSE to protect the integrity of equipment, ERCOT shall honor the restriction.

The SO performs security analyses on a Day Ahead and Real-Time basis and ensures that all Forced Outages are entered into the Outage Scheduler. The SO shall obtain or arrange to provide Emergency Energy over the DC Tie(s) on behalf of ERCOT.

The SO shall issue appropriate OCN’s, Advisories, Watches, and Emergency Notices, and coordinate the reduction or cancellation of clearances, re-dispatch of generation, and request, order, or take other action(s) that the SO determines necessary to maintain safe and reliable operating conditions on the ERCOT System in accordance with ERCOT Protocols, Operating Guides, and NERC Reliability Standards.  The SO will implement and terminate ERCOT Time Corrections, and will determine the need for and implement the operation of a Qualified Scheduling Entity (QSE) on Constant Frequency Control for loss of ERCOT’s Load Frequency Control System.

As the Reliability Coordinator, ERCOT ISO shall comply with its Regional Reliability Plan which has been approved by the NERC Operating Committee.

## 2.2	Communication

Procedure Purpose:  To improve communication to reduce the possibility of miscommunicaiotn that could lead to action or inaction harmful to the reliability of the grid..

| Protocol Reference | 6.5.7.8 | 6.5.8 |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 3.1.3 |  |  |  |
| NERC Standard | COM-002-4 |  |  |  |

| Version: 1 | Revision: 4 | Effective Date: |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Three-Part Communication |
| NOTE | Operating Instructions and Dispatch Instructions are synonymous and both require ‘three-pat communication’. Refer to the Communications Protocols document for requirements. |
| 1 | When issuing Operating Instructions, use three-part communication: Issue the Operating Instruction Receive a correct repeat back Give an acknowledgement |
| 2 | Many scripts have been placed throughout the procedures as a reminder of three-part communication. However, a script cannot be provided for every scenario. Effective three-part communication skills are mandatory. |
| Hotline Call Communication |
| 1 | When making Hotline calls, verify that every QSE has answered. IF: Not every QSE answered the Hotline; THEN: Contact them using their OPX line or LD line to provide them with the message Inquire why they were not on the Hotline call Open a Help ticket if ERCOT’s Telecommunications department is needed to investigate. |
| VDI to Master QSE |
| 1 | Issue the VDI to the Master QSE of a Generation Resource that has been split to function as two or more Split Generation Resources as deemed necessary by ERCOT to effectuate actions for the total Generation Resource for instances when electronic Dispatch Instructions are not feasible. |
| LOG | Log all actions. |

## 2.4	RMR Resource Commitment

Procedure Purpose: This task is performed to notify ERCOT Market Operations of RMR resources that are required, in the Day-Ahead, to maintain system security/stability of the ERCOT Interconnection.

| Protocol Reference | 4.2.1.1(5) | 4.3(2) | 4.4.8 | 5.5.3 |
| --- | --- | --- | --- | --- |
|  | 6.3.2 (3) (c) | 6.4.2 (2) | 6.4.4 (2) | 6.5.1.1(d) |
|  | 6.5.9.4.1 |  |  |  |
| Guide Reference |  |  |  |  |
| NERC Standard | TOP-002-2.1b R1 |  |  |  |

| Version: 1 | Revision: 4 | Effective Date: June 27, 2016 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | ERCOT shall notify the QSE representing a RMR Unit for any unit that is being committed in DAM or DRUC at the same time that the DAM and DRUC participants are notified of the results of that respective process. |
| NOTE | ERCOT currently has one RMR contract. Greens Bayou Unit G5 is available for RMR service and may be required for voltage support, stability or management of localized transmission constraints under Credible Single Contingency criteria where market solutions do not exist. |
| NOTE | ERCOT will minimize the use of the RMR Resources for capacity purposes. The following RMR can only be committed [Greens Bayou Unit 5 (GBY_G5)] when there is no market solution to meet demand needs first. In conditions where ERCOT indicates a capacity reserve shortage with no market Resources available, and with a risk of an EEA event, then the RMR Resource will be committed under Reliability Unit Commitment (RUC). RMR Resources will only be dispatched from the Hourly Reliability Unit Commitment (HRUC). |
| Resources | Greens Bayou Unit 5 (GBY_G5) QSEs will show a COP status of OFF when Resources are available. |
| 1 | Each day: DETERMINE, by referring to the system area requirements, if the GBY_G5 RMR Resource may be required for congestion or to provide local voltage support for any hour of the next operating day. Consult the Daily Outage Notes for indications of required RMR generation need. Note: Changes in system configuration in the area due to planned or forced outages may also create the need to schedule RMR generation. This can also be evaluated through STNET studies, DRUC and HRUC studies. |
| 2 | IF: The GBY_G5 RMR Resource is needed; THEN: Follow the Tasks prior to Execution of HRUC Procedure and COMMIT the Resource. REFER to 3.1 Tasks prior to Execution of HRUC |
| 3 | Log actions taken. |

# 3.	Hourly RUC

## 3.1	Tasks prior to Execution of HRUC

Procedure Purpose:  To make manual corrections for bad/suspect telemetry, load forecast modifications, or to commit/de-commit Resources prior to running the RUC process.

| Protocol Reference | 3.12.1(3) | 5.1 | 5.2.2.2(11) | 5.3(3) |
| --- | --- | --- | --- | --- |
|  | 5.5.1 | 5.5.2(9) |  |  |
| Guide Reference |  |  |  |  |
| NERC Standard | TOP-002-2.1b R1 & R11 |  |  |  |

| Version: 1 | Revision: 7 | Effective Date: June 27, 2016 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Tasks prior to execution of HRUC |
| NOTE | The RUC Study Period for DRUC is the next Operating Day. The RUC Study Period for HRUC is the balance of the current Operating Day plus the next Operating Day if the DRUC for the Operating Day has been solved or after 18:00 if DRUC did not solve. |
| Continuous Monitoring | REVIEW REFERENCE DISPLAY: Market Operation>EMS Interface>EMSI Workflow Parameters Market Operation>EMS Interface>EMSI Workflow IF: The EMSI Workflow Parameters does not indicate EMSI has run in the last hour and Load Forecast are NOT running (should be continuous); THEN: Open EMSI Workflow, select “Start up”. When start up is complete, select “Run”. IF: EMSI Workflow does not complete; THEN: Notify Helpdesk and Control Room staff. |
| Load Forecast | Periodically monitor the Load Forecast to ensure it is accurate: IF: Adjustments need to be made, they will be done in the EMS and updated to the MMS; THEN: Adjust (Refer to Desktop Guide RUC Section 2.17). |
| Wind Forecast Updates | Periodically monitor the Wind Forecast and verify data is updating: IF: Wind forecast is not updating; THEN: Notify Supply Integration & Grid Application group, Be aware that this could skew HRUC results. |
| RMR Consideration | All other generation resources should be considered prior to a RMR commitment for capacity purposes: IF: An RMR unit needs to be considered in HRUC; THEN: Ensure COP status is “OFF”. IF: An RMR unit is needed but is not to be considered in HRUC; THEN: Commit unit before HRUC is executed, Follow 3.2 Review, Approve and Post HRUC Results step RMR Commitment. |
| COP Validation | REVIEW REFERENCE DISPLAY: Market Participation>Monitoring>Event Manager>Events>filter Event Name for COP Validation IF: A Resource Forced Outage has occurred and the QSE has not update their COP, OR COP Validation ERROR; THEN: Select “START-NOW" in the Status column, Be aware that the results may be skewed and determine the need for procuring equivalent MW capacity elsewhere. |
| Review AS Differences | REVIEW REFERENCE DISPLAYS: Market Participation>Physical Market>SASM Market>AS Responsibility – QSE Market Participation>Monitoring>Event Manager>Events IF: AS Differences exist; THEN: Notify the Resource Operator. |
| Bad/Suspect Telemetry | Periodically monitor: IF: Notified of bad/suspect telemetry; THEN: Determine if issues will be resolved for next HRUC run, Discuss with Shift Supervisor if the HRUC should be run or delayed until the issues can be resolved, Consider requesting Operations Support Engineer to manual over-ride SCADA values (be aware that this could skew the results), If it is determined to delay HRUC, follow the “HRUC Failure/Timeline Deviation” procedure. |
| E-Tags | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment> HRUC Displays> DSI Displays> DSI Data Processes> DSI DC Tie Schedule Market Operation>Reliability Unit Commitment> HRUC Displays> DSI Displays> External Input Data> MI COP Verify that E-tags are being imported into the MMS: IF: Individual schedules need to be reviewed; THEN: Go to the MI COP display and filter ‘ERCOT’ as the QSE name. |
| Verify | REVIEW REFERENCE DISPLAYS: Market Operation>EMS Interface>EMSI Workflow Parameters Market Operation>EMS Interface>EMSI Workflow Messages EMSI has completed successfully within the last hour Market Operation>Reliability Unit Commitment>HRUC Displays>UC Displays>HRUC UC Execution Control Parameters Market Operation>Reliability Unit Commitment>HRUC Displays>NSM Displays>NSM Execution Control Parameters Market Operation>Reliability Unit Commitment>HRUC Displays>DSI Displays>DSI Execution Control Parameters “Retrieve MF Interface Data” flag set to “Yes”. “Retrieve MI Interface Data” flag set to “Yes”. “Retrieve EMS Interface Data” flag set to “Yes”. “Check Market Status set to “Yes”, “Use Save case set to “No” |
| DSI | EXECUTE: The DSI sequence; VERIFY: For error or warning messages and take necessary action if needed to correct the errors, The input data is properly transferred. If NOT: Contact Help Desk immediately to determine the cause and expected time of resolution. |
| Manual Commitment | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP RUC Commitment/Decommitment Summary Market Operation>Reliability Unit Commitment>HRUC Displays>DSI Displays> External Input Data>MF Generator Parameters Market Operations>Reliability Unit Commitment>HRUC Displays>DSI Displays>DSI Data Processes> DSI Operator Manual Commitment Market Operations>Reliability Unit Commitment>HRUC Displays>DSI Displays>External Input Data> MF Generator Parameter All other generation resources should be considered prior to a RMR commitment for capacity purposes: IF: An RMR unit is needed and is not to be considered in HRUC; THEN: Commit unit before HRUC is executed, Follow 3.2 Review, Approve and Post HRUC Results step RMR Commitment. IF: Additional resources are needed to solve for transmission congestion; THEN: Consult with the Operations Support Engineer and/or the Transmission and Security Desk Operator to determine which resources should be committed, AND Determine the temporal constraints for each of the units. IF: The resource start-up time doesn’t allow enough time to re-evaluate the need for its commitment in future HRUC Study Periods; THEN: Change ‘blank’ to ‘Commit’, List reason. |
| Deselect Contingencies | IF: It has been determined with the help of Operations Support Engineer that a contingency known to cause errors or that otherwise result in inconclusive study output in RUC; THEN: After the Operations Support Engineer has deselected the contingency, Post to the MIS Secure with the contingency that was deselected with the reason and no later than one hour after deselection. Typical MIS posting: Contingency (name) was deselected in RUC due to (reason). WHEN: Contingency is re-enabled in RUC; THEN: Cancel posting |
| NOTE | If a RMR unit was committed in DSI Operator Manual Commitment and it is the only change since the DSI was last run the next step is not necessary. |
| Verify | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>DSI Displays>DSI Execution Control Parameters IF: Manual changes have been made to the HRUC input data; CHANGE: The appropriate flags are set to prevent the data from being over-written. “Retrieve MF Interface Data set to No”, “Retrieve MI Interface Data set to No”, “Retrieve EMS Interface Data set to No”, OR “Use Save case set to “Yes” |
| Verify HRUC executed at XX: 03 |
| 1 | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>HRUC Displays>Workflow>HRUC Workflow Market Operation>Reliability Unit Commitment>HRUC Displays>Workflow>HRUC Workflow Messages Verify execution of the HRUC sequence. |

## 3.2	Review, Approve and Post HRUC Results

Procedure Purpose:  Monitor RUC applications to determine if systems are functioning properly.  Verify results and correct for any warning or error messages.  Review and approve final results for market posting.

| Protocol Reference | 4.4.8 | 5.1 | 5.3(3) | 5.5.1 |
| --- | --- | --- | --- | --- |
|  | 5.5.2 | 5.5.3 | 6.1(2) | 6.4.9.1.2 |
| Guide Reference |  |  |  |  |
| NERC Standard | EOP-002-3.1 R4 | IRO-002-2 R7 | IRO-008-1 R3 | TOP-002-2.1b R1, R4, R5, R6, R7, R8, R9, R10, R11 |
|  | TOP-008-1 R4 |  |  |  |

| Version: 1 | Revision: 23 | Effective Date: June 30, 2016 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | See Desktop Guide Common to Multiple Desks Section 2.16 if the savecase function fails when running RUC |
| Monitor | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>HRUC Displays>Workflow>HRUC Workflow Market Operation>Reliability Unit Commitment>HRUC Displays>Workflow>HRUC Workflow Messages Monitor the HRUC Workflow display to determine when it is complete, ENSURE: The workflow has completed before the study is approved and published. IF: The study is approved before it completes, Incorrect RUC deployments are sent to QSE’s THEN: Make hotline call to notify QSE’s that deployments for HRUC are invalid, Notify the Manager, ERCOT may use information from the DAM processes as decision support during the HRUC processes. |
| System Summary | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>UC Displays>Output Display Menu>System Outputs>Summary IF: All load forecasts seem unreasonable; THEN: Select the most reasonable forecast, AND Call the Load Forecasting group for guidance on updating the weather or load forecast Notify by e-mail the following distribution lists of the issue: Load Forecasting & Analysis 1 ERCOT Shift Supervisors |
| Excess Generation | During periods of low load and excess generation: PERIODICALLY REVIEW: OpsMon Dashboard Viewer under the MOS_DEV folder: “Last Approved HRUC Capacity” which is based on the last ran HRUC solution VERIFY: TOTAL_LOAD is less than SS_LASL, IF: Load forecast is reasonable AND the decision needs to be made in the near future, THEN: Decommit generation from the HRUC next study, Priority should be on WGR’s or Resources that resolve congestion; IF: The decision needs to be made immediately, THEN: Issue an electronic Dispatch Instruction confirmation (priority should be given to WGRs and Resources that resolve congestion Choose “DECOMMIT” as the Instruction Type from Resource tab Enter “ERCOT requested decommit/capacity surplus” in Other Information. When issuing a VDI or confirmation, ensure the use of three-part communication: Issue the Operating Instruction Receive a correct repeat back Give an acknowledgement |
| A/S Infeasibility | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP Undeliverable Ancillary Service Capacity Summary Market Participation>Physical Market>SASM Market>AS Infeasibility Market Participation>Physical Market>SASM Market>AS Replacement IF: Undeliverable Ancillary Service are indicated; THEN: Determine if the infeasibility is valid IF: Valid; THEN: Notify the affected QSE for the following information the amount of A/S that must be reduced, and the start and stop times of the reduction. The QSE can substitute or ERCOT can open a SASM IF: The QSE elects to substitute; THEN: Determine the feasibility of the substitution. If deemed infeasible, a SASM can be opened Notify the Resource Operator of possible infeasibility issue. |
| A/S Insufficiency from SASM | If a SASM market has been previously run, the following display will indicate if additional A/S Insufficiencies exist: REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP Decision Support for Ancillary Service Deployment IF: A/S Insufficiency; THEN If deemed necessary, commit the necessary Resources that are qualified to provide the service that is deficient while honoring temporal constraints, Refer to Desktop Guide RUC Section 2.18. |
| Undeliverable A/S Capacity | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP Undeliverable Ancillary Service Capacity Summary IF: Undeliverable A/S due to transmission constraints; THEN: Notify the Resource Operator. |
| STNET Study | Each hour run a STNET study for four hours out (example it is 0100, run study for 0500) to review voltage violations. IF: Voltage contingencies or unsolved contingencies exist; THEN: Check “Voltage Tracking Issues spreadsheet” on Sharepoint to ensure the contingency is not listed. If not listed, convey the voltage violations to the Transmission and Security Operator Create a savecase, use naming convention “SC_RUC(HE)_(DATE) Make at least one detailed log entry per shift that the studies are being executed. If any new voltage violations are identified that do not have a solution, log the information and notify the Transmission and Security Operator of the new violation(s). |
| Violated Constraints | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP Binding Constraint Summary Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP Constraint Summary REVIEW: Violated constraints. If needed, notify Operations Support Engineer to determine the validity; IF: Invalid, no further action is required; IF: Valid; AND Related to a phase shifter tap settings, THEN: Notify Operations Support Engineer to determine and determine if adjusting a Phase Shifter would reduce the flow, Create Suggestion Plan for Constraint, Manually commit resources as needed Refer to Desktop Guide RUC Section 2.14. |
| HRUC Committed Units | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>DSI Displays>External Input Data>MF Generator Parameter IF: HRUC recommends the commitment of any unit; THEN: Determine the validity, Determine the temporal constraints for each of the units. IF: The resource start-up time allows enough time to re-evaluate the need for its commitment in future HRUC Study Periods, and There is no reliability reason requiring the resource commitment decision to be made immediately; THEN: De-select the resource prior to approving the HRUC study by changing ‘Commit’ to ‘blank’ and list reason, IF: There is a reliability reason requiring the resource commitment decision to be made immediately; Resources returning from outages Congestion or Capacity deficiencies that are creating HRUC performance issues THEN: Log the reason for not de-selecting the resource. NOTE: A reason must be entered for commit, decommit, and uncommitting, otherwise a message window will pop up in DSP approval process. Examples below: Evaluate later (should be used when waiting until the last possible hour to commit) Short start (should be used for units that can start within 1 hour) Voltage support Valley import Capacity Constraint name (SLWSCRL5) * Do not use special characters Give a courtesy call to the QSE when commitments are made. |
| RMR Resources | QSEs will show a COP status of OFF when Resources are available. RMR Resources will only be dispatched from the Hourly Reliability Unit Commitment (HRUC). |
| RMR Commitment | WHEN: HRUC recommends a RMR unit, AND A capacity reserve shortage is projected and no market Resources are available to meet the projected system demand, and there is a risk of an EEA event; THEN: Determine if an RMR Resource will need to be considered in HRUC Study Period; ISSUE: Watch for projected reserve capacity shortage with no market solution; THEN: Ensure COP status is “OFF” and the resource start-up time allows enough time to procure the RMR for the hours showing to be deficient with risk of an EEA event; SELECT: Commit Resource before HRUC is approved Commit Resource, List reason (RMR for Capacity). Call QSE with any modification to the Delivery Plan as a result of a commitment. |
| Hotline | Q#77 - Typical Hotline Script for Watch for projected reserve capacity shortage Notify Transmission Operator to make Hotline call to TOs. |
| Post | Typical MIS posting: ERCOT issued a Watch for a projected reserve capacity shortage with no market solution available. HRUC recommended RMR Resources have been committed. |
| Cancel | WHEN: Committed RMR Resources are off-line THEN: Making hotline call to QSEs Cancelling MIS posting Notify Transmission Operator to make hotline call to TOs. Q#78 - Typical Hotline Script for canceling Watch for projected reserve capacity shortage |
| Manual Commitment | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP RUC Commitment/Decommitment Summary Market Operation>Reliability Unit Commitment>HRUC Displays>DSI Displays> External Input Data>MF Generator Parameters IF: Additional resources are needed to solve for transmission issues (such as for voltage support) and were not picked up in the HRUC run; THEN: Commit unit before HRUC is approved Change ‘blank’ to ‘Commit’, List reason (constraint name, valley import or voltage support), a message window will pop up in DSP approval process if no reason is provided. Give courtesy call to QSE when commitments are made |
| NOTE | Resources cannot be decommitted for just a portion of a DAM-Committed Interval, which is a one-hour interval. ERCOT may only decommit a Resource to resolve transmission constraints that are otherwise unsolvable or to maintain the reliability of the ERCOT System. Qualifying Facilities (QFs) may be decommitted only after all other types of Resources have been assessed for decommitment. If ERCOT communicates HRUC commitments and decommitments verbally to a QSE, then the same Resource attributes communicated programmatically must be communicated when ERCOT gives a verbal Resource commitment or decommitment. QSE’s shall acknowledge the notice of commit or decommit by updating their COP. |
| HRUC Decommitted Resources | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP RUC Commitment/Decommitment Summary IF: If HRUC recommends decommitments; Determine if: Outage related, Possible Network Model error/ Normal Breaker status variances, COP error for Combine Cycle configurations / JOU, Qualifying Facilities should be de-committed ONLY as a last resort, THEN: If this is a true decommitment: Confirm Decommitment List reason (most likely reason is ‘transmission outage’), a message window will pop up in DSP approval process if no reason is provided If Decommitment is error related: No action is required |
| Canceling RUC Commitments | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>DSI Displays>DSI Data Processes>DSI Operator Manual Commitment IF: A Resource is RUC committed that needs to be canceled; Only cancel RUC commits if the ERCOT Operator Resource commitment was unintended. THEN: Issue electronic Dispatch Instruction to cancel the RUC instruction Choose “CANCEL RUC COMMIT” as the Instruction Type Enter “unintended commitment” in other information When issuing a VDI or confirmation, ensure the use of three-part communication: Issue the Operating Instructuion Receive a correct repeat back Give an acknowledgement Remove unintended RUC commit from DSI Operator Commitment by changing (AUTO) to (OFF) for the hours in question. |
| VSAT and RUC perform AC Analysis |
| NOTE | IF: RUC cannot complete the process; THEN: Notify the Transmission & Security Operator and additional personnel as required. |
| Validate | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>UC Displays>Output Display Menu>System Outputs>Summary VERIFY: Input data Updated Time Results are reasonable |
| Approval | HRUC must be approved by XX:50 REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP Execution Control Parameters IF: The HRUC results are reasonable and after all necessary modifications have been made; THEN: Approve the results (all RUC commitment, operator manual commitment/decommit/blank out must have a reason, otherwise a message window will pop up), OR IF: The results are unacceptable; THEN: Click on Disapprove button, AND Follow the Manage HRUC Timeline Failure in the next section. IF: Disapprove button was selected in error; THEN: Contact Helpdesk to open ticket for EMMS Production Support to correct it. |
| After Approval | AFTER: Approval button is pushed; THEN: Double check display Market Participation>Physical Market>Market Results>HRUC> HRUC Results, Make sure the records in this display matches data in display Market Operation>Reliability Unit Commitment>HRUC Displays >DSP Displays>DSP RUC Commitment/Decommitment Summary. IF: Displays are different, the RUC commitments thought to be blanked out were sent out; THEN: Notify the Helpdesk to call the On-Call EMMS Production support, and Issue electronic Dispatch Instructions to cancel RUC instructions When issuing a VDI or confirmation, ensure the use of three-part communication: Issue the Operating Instruction Receive a correct repeat back Give an acknowledgement |
| Log | Log actions taken. |

## 3.3	HRUC Failure/Timeline Deviation

Procedure Purpose:  To address situations in which the HRUC process has failed.  Failures can be identified by software failure, results not approved in a timely manner or certain conditions.

| Protocol Reference | 6.5.9.1(2) | 6.5.9.3.3(2)(e) |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | IRO-002-2 R7 |  |  |  |

| Version: 1 | Revision: 15 | Effective Date: June 30, 2016 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Logs | Document decisions made and actions taken within this procedure in the Operator Logs. |
| HRUC Failure/Timeline Deviation |
| Failure | IF: HRUC solved with invalid solution, Time does not allow for full review of results, OR HRUC software fails without expectation of timely repair; THEN: Notify Help Desk and Control Room Staff, Issue a Watch by making a Hotline call to QSEs Make posting on MIS Public. Notify Transmission Operator to make Hotline call to TOs Q#79 - Typical Hotline Script for Watch for HRUC failure/timeline deviation WHEN: HRUC is operating properly; THEN: Making hotline call to QSEs Cancelling MIS posting Notify Transmission Operator to make hotline call to TOs. Q#80 - Typical Hotline Script to Cancel Watch for HRUC failure/timeline deviation |
| Create Save Case | IF: HRUC is aborted or shut down; THEN: Go to display System Administration > Savecase Management. Choose File Type as HRUC. Fill in File Name (no spaces allowed) Fill in Description. Push Create Button. The message will show up in the Text field. Refresh the display (F5), make sure the savecase name will show up in the File Name Field. Also refer to Desktop Guide Common to Multiple Desks Section 2.16, if needed. Contact Helpdesk to notify EMMS Production Support that HRUC was aborted or shut down and a Savecase was created. |
| NOTE | IF: HRUC is having trouble solving in the required timeline due to transmission/capacity violations in the study; THEN: Have Operations Support Engineer check validity of violation AND if correct, Consider committing Resource(s) sooner instead of waiting to evaluate later. |
| Commit/ De-Commit Resources By VDI | IF Needed: Commit/De-Commit Resources by issuing electronic Dispatch Instructions for the following: Choose COMMIT or DECOMMIT as the Instruction Type from the RES Level, Enter reason (capacity, capacity surplus or contingency name) in “other information” When issuing a VDI or confirmation, ensure the use of three-part communication: Issue the Operating Instruction Receive a correct repeat back Give an acknowledgement |

## 3.6   Assigning Ancillary Services

## Procedure Purpose: Process for assigning Ancillary Services when the DAM, SASM, RUC processes have failed to procure the needed A/S for on-line generation.

| Protocol Reference | 4.5.2(2) | 6.5.9.3.3 |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 1 | Effective Date:June 30, 2016 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | If there is A/S insufficiencies in DAM and shortage is large enough to cause a reliability concern, SASM will be used to procure the insufficiencies. If the SASM process is not sufficient, HRUC will be used to commit the necessary Resources to provide the needed A/S. If HRUC is not sufficient, Ancillary Services will be prorated among QSEs representing On-line capacity not already reserved for AS in a way that maximizes the distribution of the assignments. Assignments will be on a QSE level, the QSE will assign to the Resource(s) of choice. |
| A/S Insufficiency Offers | IF: There is insufficient A/S after the DAM, SASM, and the HRUC processes, AND Reliability concerns exists; VERIFY: A Watch due to insufficient A/S offers has been issued; Q#81 - Typical Hotline Script for Watch for insufficient A/S THEN: Assign A/S to QSEs with On-Line Resources |
| OPSMON Display | Refer to OpsMon display 014 Emergency AS Assignment It is sorted with the greatest amount of capacity at top AS_PRC is the percentage of qualified AS capacity that is already assigned AS (total of Reg-Up, Reg-Down and RRS) in the COP |
| REG Up | SELECT: Up to 10 QSEs with the most available capacity and carrying the least amount of A/S; If assigning Reg-Up, select the same QSEs for both services if Reg-Down is needed and available, NOTIFY: Each QSE of their assigned obligation Example: 100 MW of Reg-Up being assigned, each QSE is assigned 10 MW. Resource telemetry must be place on ONREG |
| REG Down | SELECT: Up to 10 QSEs with the most available capacity and carrying the least amount of A/S; If assigning Reg-Down, select the same QSEs for both services if Reg-Up is needed and available, NOTIFY: Each QSE of their assigned obligation Example: 100 MW of Reg-Down being assigned, each QSE is assigned 10 MW. Resource telemetry must be place on ONREG |
| Responsive Reserve | SELECT: Up to 10 QSEs with the most available capacity and carrying the least amount of A/S; If assigning Reg-Up or Reg-Down, the same QSEs can be selected for RRS, NOTIFY: Notify each QSE of their assigned obligation Example: 100 MW of RRS being assigned, each QSE is assigned 10 MW. Resource telemetry must be place on RRS |
| Issue VDIs | ISSUE: Electronic VDIs QSE Level Instruction Type: Other for QSE Other Information: Specify A/S type, amount and reasons for this VDI When issuing a VDI or confirmation, ensure the use of three-part communication: Issue the Operating Instruction Receive a correct repeat back Give an acknowledgement |
| Cancellation | A QSE may request cancellation of the assignment of Ancillary Services to its On-Line Resources if there are equipment or Resource control issues which limit the ability of the Resources to provide the Ancillary Services. IF: ERCOT accepts the cancellation; ERCOT may require QSEs to submit supporting information describing the Resource control issues. |
| Non-Spin | Non-Spin will not be assigned. |
| REG/RRS Assigned Shortages | WHEN: A/S offers are Assigned; THEN: Make hotline call to QSEs Cancel MIS posting Notify Transmission Operator to make hotline call to TOs. Q#82 - Typical Hotline Script Cancel Watch for insufficient A/S |
| Log | Log actions taken. |

## 3.7	Manual Dispatch of Resources

Procedure Purpose:  Manually Dispatch Resources as necessary to ensure system security when HRUC can not be used.

| Protocol Reference | 5.1(12) | 5.5.3(3) | 6.5.9 (3) |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | EOP-002-3.1 R4 | IRO-006-TRE-1 R1 | TOP-001-1a R8 |  |

| Version: 1 | Revision: 7 | Effective Date: June 30, 2016 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | ERCOT shall honor all Resource operating parameters in Dispatch Instruction under normal conditions and Emergency Condition. During Emergency Conditions, ERCOT may verbally request QSE’s to operate its Resources outside normal operating parameters. If such request is received by a QSE, the QSE shall discuss the request with ERCOT in good faith and may choose to comply with the request A QSE can self-commit by setting the COP Resource Status to ONOPTOUT for the first SCED run that the Resource is On-Line and available for SCED dispatch during the first hour of a contiguous block of RUC-Committed Hours If a QSE-committed Resource experiences a Forced Outage or Startup Loading Failure in an hour for which another Resource under the control of the same QSE is committed by a RUC instruction, the QSE may opt out of the RUC instruction by self-committing the Resource as described above |
| Manual Commit of a Resource |
| 1 | IF: It has been determined that a Resource is needed in real-time for a transmission condition after the close of the Adjustment Period; THEN: Issue an electronic Dispatch Instruction to commit the Resource, Choose “COMMIT” as the Instruction Type from Resource level Enter reason, such as contingency name or capacity in “other information” Confirm with QSE that the electronic Dispatch Instruction was received The same Resource attributes communicated programmatically must be communicated when giving a VDI. When issuing a VDI or confirmation, ensure the use of three-part communication: Issue the Operating Instruction Receive a correct repeat back Give an acknowledgement See Desktop Guide Common to Multiple Desks Section 2.3 for additional information to submit a correct electronic Dispatch Instruction. |
| LOG | Log all actions. |
| Manual Dispatch to take a Unit Off-Line |
| 1 | IF: A manual dispatch instruction will result in the unit being dispatched off-line (i.e., less than the minimum operating limit for that Resource); THEN: Issue an electronic Dispatch Instruction taking the Resource to zero until it can be released, Choose “DECOMMIT” as the Instruction Type from Resource level Enter contingency name in “other information” When issuing a VDI or confirmation, ensure the use of three-part communication: Issue the Operating Instruction Receive a correct repeat back Give an acknowledgement Ensure QSE updates telemetry. |
| Manual Dispatch to take a Unit of a Combined Cycle Off-line |
| 1 | IF: System conditions require one unit of a Combined Cycle Plant to be manually dispatched off-line; THEN: Contact the QSE and request which unit the QSE would like to shutdown, Request the planned/current CC configuration and then the CC configuration that the Resource will need to be operating, Issue an electronic Dispatch Instruction confirmation to “COMMIT” the QSE to their CC configuration. All data must be entered but pay attention to the following details. Choose the proper QSE from the Participant name Select the CC configuration that you are instructing the Resource to operate in from the Resource name Choose “COMMIT” as the Instruction Type from Resource level Enter contingency name in “other information” When issuing a VDI or confirmation, ensure the use of three-part communication: Issue the Operating Instruction Receive a correct repeat back Give an acknowledgement Log the above information. |
| Manual Dispatch to bring a Unit of a Combined Cycle On-line |
| 1 | IF: System conditions require a unit of a Combined Cycle Plant to be manually dispatched on-line; THEN: Contact the QSE and notify which unit will be committed, Request the planned/current CC configuration and then the CC configuration that the Resource will need to be operating, Issue an electronic Dispatch Instruction to “COMMIT” the QSE to their CC configuration. All data must be entered but pay attention to the following details. Choose the proper QSE from the Participant name Select the CC configuration that you are instructing the Resource to operate in from the Resource name Choose “COMMIT” as the Instruction Type from Resource level Enter contingency name in “other information” When issuing a VDI or confirmation, ensure the use of three-part communication: Issue the Operating Instruction Receive a correct repeat back Give an acknowledgement Log the above information. |
| Canceling RUC Commitments |
| 1 | IF: A Resource is RUC committed that needs to be canceled; Only cancel RUC commits if the ERCOT Operator Resource commitment was unintended. THEN: Issue an electronic Dispatch Instruction to cancel the RUC instruction Choose “CANCEL RUC COMMIT” as the Instruction Type Enter “unintended commitment” in other information |
| LOG | Log all actions. |

## 4.3	Review, Approve and Post DRUC Results

Procedure Purpose:  To work collaboratively with Market Operations Support Personnel in reviewing, and if necessary, modifying DRUC data, to approve and post the final DRUC results.

| Protocol Reference | 4.4.8 | 5.1 (9) | 5.3(3) | 5.5.1(9) |
| --- | --- | --- | --- | --- |
|  | 5.5.2 | 5.5.3(2) | 6.4.9.1(3) |  |
| Guide Reference |  |  |  |  |
| NERC Standard | IRO-002-2 R7 | IRO-008-1 R1, R3 | TOP-002-2.1b R1, R4, R5, R6 R7, R8, R9, R10, R11 | TOP-008-1 R4 |

| Version: 1 | Revision: 25 | Effective Date: June 30, 2016 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | See Desktop Guide Common to Multiple Desks Section 2.16 if the savecase function fails when running RUC |
| Monitor | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>DRUC Displays>Workflow>DRUC Workflow Market Operation>Reliability Unit Commitment>DRUC Displays>Workflow>DRUC Workflow Messages |
| Review | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>DRUC Displays>UC Displays>Output Display Menu>System Outputs>Summary When DRUC has completed. If necessary, work with Market Operations and Operations Support Engineer to review the results. Monitor the DRUC Workflow display to determine when it is complete, ENSURE: The workflow has completed before the study is approved and published, IF: The study is approved before it completes, Incorrect RUC deployments are sent to QSE’s THEN: Make hotline call to notify QSE’s that deployments for DRUC are invalid, Notify the Manager of System Operations and/or Control Room Operations Manager immediately, Abnormal system condition in the summary display after IUC (Initial Unit Commitment component of MMS) and NCUC (Network Constrained Unit Commitment component of MMS). For Under Generation, prepare for following “Manage Capacity Insufficiency” section of this procedure For Over generation, check for COP or Load Forecast errors For System Lambda greater than $10, check intermediate NSM (Network Security Manager Component of MMS) results for constraint violation. For abnormal constraints in the NSM outputs and abnormal commitments in IUC and NCUC outputs, refer to Desktop Guide RUC Section 2.6, step 5. |
| NOTE | Resources with NO Current Operating Plan (COP) entry are considered as “Unavailable” in RUC. Resources with “EMR” Resource status can only be committed during Emergency conditions. |
| System Summary | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>DRUC Displays>UC Displays>Output Display Menu>System Outputs>Summary Market Operation>Reliability Unit Commitment>DRUC Displays>UC Displays>Output Display Menu>System Outputs>Summary Line Flow DETERMINE IF: The load forecast is reasonable for each hour, Any under/over generation; THEN: Be aware of these when running HRUC. |
| A/S Insufficiency from DAM | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP Decision Support for Ancillary Service Deployment Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP RUC Commitment/Decommitment Summary IF: Notified from Market Operations of A/S Insufficiency from DAM; THEN Issue a Watch to QSEs Notify Transmission Operator to make Hotline call to TOs Verify Market Operations has posted message on MIS Public Refer to Desktop Guide RUC Section 2.1. Q#85 - Typical Hotline Script for Watch for A/S insufficiency in DAM, procuring in DRUC WHEN: A/S offers are committed in DRUC; THEN: Making hotline call to QSEs Cancelling MIS posting Notify Transmission Operator to make hotline call to TOs. Q#86 - Typical Hotline Script Cancel Watch for A/S insufficiency in DAM |
| Undeliverable A/S Capacity | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP Undeliverable Ancillary Service Capacity Summary IF: Undeliverable A/S due to Transmission Constraints and Reliability issues exist; THEN: Notify the QSEs and provide the following information: The amount of its Resource capacity that does not qualify to provide A/S The projected hours Notify the Resource Desk Operator. |
| Violated Constraints | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP Binding Constraint Summary Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP Constraint Summary REVIEW: Violated constraints. If needed, notify Operations Support Engineer to determine the validity; IF: Invalid, no further action is required, Valid; THEN Locate the constraint on the DSP Constraint Summary display, Create a Suggestion Plan for the identified violated constraint Review the temporal constraints of the suggested resources If resource start-up time allows enough time to re-evaluate the need for its commitment, be aware of these conditions when running HRUC, Commit resources as needed prior to DRUC approval if needed due to temporal constraints. |
| NOTE | RUC Operators can decide to postpone a commitment if the startup time is well into the future. It will be left up to future HRUC solutions to actually commit the unit. |
| DRUC Committed Units | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>DRUC Displays>DSI Displays>External Input Data>MF Generator Parameter Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays>DSP RUC Commitment/Decommitment Summary IF: DRUC recommends the commitment of any unit; THEN Determine the validity, Determine the temporal constraints for each of the units, IF: The resource start-up time allows enough time to re-evaluate the need for its commitment in future HRUC Study Period, AND There is no reliability reason requiring the resource commitment decision to be made immediately; THEN: De-select the resource prior to approving the DRUC study by changing ‘Commit’ to ‘blank’ and list reason. IF: There is reliability reason requiring the resource commitment decision to be made immediately; Resources with long start-up times Resources returning from outages Congestion or Capacity deficiencies that may create HRUC performance issues THEN: Log the reason for not de-selecting the resource. NOTE: A reason must be entered for commit, decommit, uncommitting, examples below: Evaluate later (should be used when waiting until the last possible hour to commit) Short start (should be used for units that can start within 1 hour) Voltage support Valley import Constraint name (SLWSCRL5) * Do not use special characters Give a courtesy call to the QSE when commitments are made. |
| Excess Generation | During periods of low load and excess generation: PERIODICALLY REVIEW: OpsMon Dashboard Viewer under the MOS_DEV folder: “6 DRUC Capacity” which is based on the last ran DRUC VERIFY: TOTAL_LOAD is less than SS_LASL, IF: Load forecast is reasonable AND the decision can be made in the future, THEN: Issue OCN for Excess Reserve Capacity Notify Transmission Operator to make Hotline call to TOs Post message on MIS Public Q#87 - Typical Hotline Script for OCN for Excess Capacity Typical MIS Posting: ERCOT issued an OCN due to a projected excess reserve capacity for [HE XX – HE XX]. WHEN: Projected excess reserve capacity; THEN: Making hotline call to QSEs Cancelling MIS posting Notify Transmission Operator to make hotline call to TOs. Q#88 - Typical Hotline Script to Cancel OCN for Excess Capacity |
| DRUC Committed For Capacity Shortage | IF: DRUC recommends Resource(s) for capacity; THEN Determine if start-up time allows enough time to re-evaluate, and De-select the Resource(s) prior to approving the DRUC, After DRUC is approved: Issue an OCN for projected reserve capacity shortage Notify Transmission Operator to make Hotline call to TOs Post message on MIS Public Q#89 - Typical Hotline Script for OCN for commiting capacity in DRUC Typical MIS Posting: ERCOT issued an OCN due to a projected capacity shortage for [HE XX – HE XX]. WHEN: Projected reserve capacity shortage no longer exist; THEN: Making hotline call to QSEs Cancel MIS posting Notify Transmission Operator to make hotline call to TOs. Q#90 - Typical Hotline Script cancellation for OCN for commiting capacity in DRUC |
| Manual Commitment | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP RUC Commitment/Decommitment Summary IF: Additional resources are needed to solve for transmission issues (such as voltage support) and were not picked up in the DRUC run, The resource start-up time doesn’t allow enough time to re-evaluate the need for its commitment in the HRUC Study Period, OR A Resource was given a WRUC instruction and chose not to self-commit for all hours needed; THEN: Change ‘blank’ to ‘Commit’ List reason (capacity, constraint name or voltage issue). Give courtesy call to QSE when commitments are made |
| NOTE | Resources cannot be decommitted for just a portion of a DAM-Committed Interval, which is a one-hour interval. ERCOT may only decommit a Resource to resolve transmission constraints that otherwise cannot be resolved. Qualifying Facilities (QFs) may be decommitted only after all other types of Resources have been assessed for decommitment. |
| DRUC Decommitted Resources | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP RUC Commitment/Decommitment Summary IF: If RUC recommends commitments/decommitments; DETERMINE IF: Outage related’ Possible Network Model error’ COP error for Combine Cycle configurations / JOU, Qualifying Facilities should be de-committed ONLY as a last resort; THEN: If this is a true decommitment: Confirm Decommitment List reason (most likely reason is ‘transmission outage’) If Decommitment is error related: No action is required |
| NOTE | Once you have completed your review of DRUC, consult with Market Operations to ensure they see no issues before approving. |
| Validate | REVIEW REFERENCE DISPLAY: Market Participation>Physical Market>SASM Market>AS Responsibility - QSE Market Operation>Reliability Unit Commitment>DRUC Displays>UC Displays>Output Display Menu>System Outputs>Summary VERIFY: Input data Updated Time Results are reasonable |
| Approval | DRUC must be approved by 1600 REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP Execution Control Parameters IF: The DRUC results are reasonable after all necessary modifications have been made; THEN: Approve the results, OR IF: The results are unacceptable; THEN: Click on Disapprove button Follow the Manage DRUC Failure/Timeline Deviation procedure. IF: Disapprove button was selected in error; THEN: Contact Helpdesk to open ticket for EMMS Production Support to correct it. |
| NOTE | If the Operator disapproves the results, the results will be saved in the database for future analysis and will not be published to the MPs. |
| After Approval | AFTER: Approval button is pushed; THEN: Double check display Market Participation>Physical Market>Market Results>DRUC> DRUC Results, Make sure the records in this display matches data in display Market Operation>Reliability Unit Commitment>DRUC Displays >DSP Displays>DSP RUC Commitment/Decommitment Summary. IF: Displays are different, the RUC commitments thought to be blanked out were sent out; THEN: Notify the Helpdesk to call the On-Call EMMS Production support, and Issue VDIs to cancel RUC instructions When issuing a VDI or confirmation, ensure the use of three-part communication: Issue the Operating Instruction Receive a correct repeat back Give an acknowledgement |
| Canceling RUC Commitments | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>DSI Displays>DSI Data Processes>DSI Operator Manual Commitment IF: A Resource is RUC committed and needs to be canceled; Only cancel RUC commits if the ERCOT Operator Resource commitment was unintended. THEN: Issue an electronic Dispatch Instruction confirmation to cancel the RUC instruction Choose “CANCEL RUC COMMIT” as the Instruction Type Enter “unintended commitment” in other information When issuing a VDI or confirmation, ensure the use of three-part communication: Issue the Operating Instruction Receive a correct repeat back Give an acknowledgement Remove unintended RUC commit from DSI Operator Commitment by changing (AUTO) to (OFF) for the hours in question. |

## 5.2	Review WRUC Results

Procedure Purpose:  To identify commitments with a long lead time and develop a list of violated/binding constraints that have a high-probability of being binding in SCED or DAM.

| Protocol Reference | 5.1 |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 10 | Effective Date: June 30, 2016 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | WRUC does not send commitments or Dispatch Instructions to QSEs. WRUC does not retrieve any QSE-submitted Three-Part Supply Offers. WRUC relies exclusively on the QSE-submitted COPs. |
| Monitor | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>WRUC Displays>Workflow>WRUC Workflow Market Operation>Reliability Unit Commitment>WRUC Displays>Workflow>WRUC Workflow Messages |
| Violated Constraints | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>WRUC Displays>DSP Displays> DSP Binding Constraint Summary Market Operation>Reliability Unit Commitment>WRUC Displays>DSP Displays> DSP Constraint Summary REVIEW: Violated constraints; IF: WRUC identifies a Resource with a lead-time greater than the DRUC time-line and it is confirmed in the Outage Notes or a gap study; THEN: Instruct the QSE that their Resource needs to be On-line by [date] at [time] and they have the option of: Self-committing the Resource by updating the COP before the DRUC process execution, or ERCOT will commit the Resource in the DRUC process. |
| Electronic Dispatch Instruction | When instructing a QSE their resource needs to be On-line by [date] at [time]: Commit Resources by issuing electronic Dispatch Instructions for the following: Choose the proper QSE from the Participant name Choose COMMIT as the Instruction Type from the RES Level, Enter reason (capacity, or contingency name) in “other information” When issuing a VDI or confirmation, ensure the use of three-part communication: Issue the Operating Instruction Receive a correct repeat back Give an acknowledgement |
| Disapprove | IF: WRUC completes the 7 days successfully, disapprove the study IF: WRUC fails to complete the 7 days, rerun with 5 days. When it completes successfully, disapprove the study. If fails to complete the 7 days, send e-mail to “Shiftsupv” to make notification that WRUC was unable to complete the 7 days. Provide error message in e-mail. If fails to complete the 5 days, send e-mail to “Shiftsupv” to make notification that WRUC was unable to complete the 5 days. Provide error message in e-mail. |
| Create Save Case | IF: WRUC is aborted or shut down; THEN: Go to display System Administration > Savecase Management. Choose File Type as WRUC. Fill in File Name (no spaces allowed) Fill in Description. Push Create Button. The message will show up in the Text field. Refresh the display (F5), make sure the savecase name will show up in the File Name Field. Notify Helpdesk and send e-mail to “shiftsupv” for back office to follow up. Also refer to Desktop Guide Common to Multiple Desks Section 2.16, if needed. |
| Log | Log actions taken. |

# 6.	Emergency Operations

## 6.1	Market Notices

Procedure Purpose: Guidelines for issuing Emergency Conditions and the four possible levels: Operating Condition Notices (OCN), Advisories, Watches, and Emergency Notices.

| Protocol Reference | 6.3.3 | 6.5.9.3 | 6.5.9.3.1 | 6.5.9.3.2 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.3.3 | 6.5.9.3.4 |  |  |
| Guide Reference | 4.2.1 | 4.2.2 | 4.2.3 | 4.2.4 |
| NERC Standard | EOP-001-2.1b R3.1 |  |  |  |

| Version: 1 | Revision: 18 | Effective Date: June 30, 2016 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| OCN |
| NOTE | Consider the severity of the potential Emergency Condition. The severity of the Emergency Condition could be limited to an isolated local area, or the condition might cover large areas affecting several entities, or the condition might be an ERCOT-wide condition potentially affecting the entire ERCOT System. |
| 1 | As instructed by the Shift Supervisor or when appropriate, issue an Operating Condition Notice (OCN). The OCN can be issued for any of the following reasons or to obtain additional information from Market Participants. There is a projected reserve capacity shortage that could affect reliability and may require more Resources When extreme cold weather is forecasted approximately 5 days away When extreme hot weather is forecasted approximately 5 days away When an approaching Hurricane / Tropical Storm is approximately 5 days away Unplanned transmission Outages that may impact reliability When adverse weather conditions are expected, ERCOT may confer with TOs and QSEs regarding the potential for adverse reliability impacts and contingency preparedness |
| ADVISORY |
| 1 | As instructed by the Shift Supervisor or when appropriate, issue an Advisory. The Advisory can be issued for any of the following reasons or to obtain additional information from Market Participants. When an approaching Hurricane / Tropical Storm is approximately 3 days away When extreme cold weather is forecasted approximately 3 days away When extreme hot weather is forecasted approximately 1 to 3 days away When conditions are developing or have changed and more Ancillary Services will be needed to maintain current or near-term reliability ERCOT may exercise its authority to increase Ancillary Service requirements above the quantities originally specified in the Day-Ahead Market (DAM) in accordance with ERCOT Procedures When extreme weather or conditions require more lead-time than the normal Day-Ahead Market (DAM) allows Transmission system conditions are such that operations within security criteria are not likely or possible because of Forced Outages or other conditions unless a CMP exists Loss of communications or control condition is anticipated or significantly limited ERCOT may require information from QSEs representing Resources regarding the Resources’ fuel capabilities. Requests for this type of information shall be for a time period of no more than seven days from the date of the request |
| WATCH |
| 1 | As instructed by the Shift Supervisor or when appropriate, issue a Watch. The Watch can be issued for any of the following reasons or to obtain additional information from Market Participants. A projected reserve capacity shortage is projected with no market solution available that could affect reliability When an approaching Hurricane / Tropical Storm is approximately 1 day away When extreme cold weather is projected for next day or current day When extreme hot weather is projected for next day or current day Conditions have developed such that additional Ancillary Services are needed in the Operating Period Insufficient Ancillary Services or Energy Offers in the DAM Market-based congestion management techniques embedded in SCED will not be adequate to resolve transmission security violations Forced Outages or other abnormal operating conditions have occurred, or may occur that require ERCOT to operate with active transmission violations of security criteria as defined in the Operating Guides unless a CMP exists The SCED process fails to reach a solution, whether or not ERCOT is using one the measures in Failure of the SCED Process. The need to immediately procure Ancillary Services from existing offers ERCOT may instruct TOs to reconfigure transmission elements as necessary to improve the reliability of the system |
| EMERGENCY NOTICE |
| 1 | As instructed by the Shift Supervisor or when appropriate, issue an Emergency Notice. The Emergency Notice can be issued for any of the following reasons or to obtain additional information from Market Participants. Loss of Primary Control Center functionality Load Resource deployment for North-Houston voltage stability ERCOT cannot maintain minimum reliability standards (for reasons including fuel shortages) during the Operating Period using every Resource practically obtainable from the market Immediate action cannot be taken to avoid or relive a Transmission Element operating above its Emergency Rating ERCOT forecasts an inability to meet applicable reliability standards and it has exercised all other reasonable options A transmission condition has been identified that requires emergency energy from any of the DC-Ties or curtailment of schedules The Transmission Grid is such that a violation of security criteria as defined in the Operating Guides presents the threat of uncontrolled separation or cascading outages, large-scale service disruption to Load (other than Load being served from a radial transmission line) and/or overload of Transmission Elements and no timely solution is obtainable through SCED or CMP When extreme cold weather is beginning to have an adverse impact on the System When extreme hot weather is beginning to have an adverse impact on the System When Hurricane / Tropical Storm is in the ERCOT Region and is beginning to have an adverse impact on the System |
| Operating Condition Script |
| Hotline | Notify QSEs of Notice #46 - Typical Hotline Script for Operating Condition [OCN/Advisory/Watch/Emergency] . |
| Post | All notices must be posted on MIS. For “free form” messages, the “Notice Priority” will be specified as follows: Operational Information/OCN type messages – low priority Advisory/Watch type messages – medium priority Emergency type messages – high priority |
| Hotline Cancellation | #47 - Typical Hotline Script to Cancel Operating Condition [OCN/Advisory/Watch/Emergency] |
| Log | Make log entry. |

## 6.2	EEA

Procedure Purpose: To commit Resource that can be brought On-Line within the timeframe of the emergency.

| Protocol Reference | 3.9.1 | 6.5.9.4 | 6.5.9.4.1 | 6.5.9.4.2 |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.5.3.1 |  |  |  |
| NERC Standard | EOP-001-2.1b R2.1, R3.1, R3.2, R4 | EOP-002-3.1 R2, R6.1, R8 |  |  |

| Version: 1 | Revision: 3 | Effective Date: June 30, 2016 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| 1 | IF: A Generation Resource (without Non-Spin obligation) which has a unit status of OFF or EMR and can be brought On-line within the timeframe of the emergency; THEN: Issue an electronic Dispatch Instruction to commit the Resource Choose “Commit” as the Instruction Type from Resource level VDIs need a start/stop time (issue one hour at a time) Enter “capacity” in “other information” When issuing a VDI or confirmation, ensure the use of three-part communication: Issue the Operating Instruction Receive a correct repeat back Give an acknowledgement |
| 2 | IF: If Frontera can be switch from CFE into ERCOT within the timeframe needed; THEN: Notify QSE for Frontera of the need to switch the generation from CFE into ERCOT Issue RUC instruction |
| 3 | IF: A Generation Resource was scheduled to come Off-line before the start of the emergency and requests to come Off-line; THEN: Issue an electronic Dispatch Instruction to commit the Resource Choose “Commit” as the Instruction Type from Resource level VDIs need a start/stop time (issue one hour at a time) Enter “capacity” in “other information” When issuing a VDI or confirmation, ensure the use of three-part communication: Issue the Operating Instruction Receive a correct repeat back Give an acknowledgement |
| Log | Log all actions. |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Frosch, Hartmann, Barcalow, Lowrie, and Stone | Preparers | November 10, 2010 |
| Frosch and Hartmann | Procedure writers and editors | November 29, 2010 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2010 |
| Frosch and Hartmann | Procedure writers and editors | January 26, 2011 |
| Frosch and Hartmann | Procedure writers and editors | March 23, 2011 |
| Frosch and Hartmann | Procedure writers and editors | April 20, 2011 |
| Frosch and Hartmann | Procedure writers and editors | June 6, 2011 |
| Frosch and Hartmann | Procedure writers and editors | July 18, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 22, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 30, 2011 |
| Frosch and Hartmann | Procedure writers and editors | October 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 16, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | April 25, 2012 |
| Frosch and Hartmann | Procedure writers and editors | July 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | October 26, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 26, 2013 |
| Frosch and Hartmann | Procedure writers and editors | May 28, 2013 |
| Frosch and Hartmann | Procedure writers and editors | July 8, 2013 |
| Cheng, Frosch and Hartmann | Procedure writers and editors | August 7, 2013 |
| Frosch and Hartmann | Procedure writers and editors | December 11, 2013 |
| Frosch and Hartmann | Procedure writers and editors | December 20, 2013 |
| Frosch, Gaddy and Hartmann | Procedure writers and editors | April 1, 2014 |
| Frosch, Gaddy and Hartmann | Procedure writers and editors | May 27, 2014 |
| Frosch and Hartmann | Procedure writers and editors | September 29, 2014 |
| Frosch and Hartmann | Procedure writers and editors | December 10, 2014 |
| Frosch and Hartmann | Procedure writers and editors | February 25, 2015 |
| Frosch and Hartmann | Procedure writers and editors | April 29, 2015 |
| Hartmann and Gaddy | Procedure writers and editors | July 13, 2015 |
| Hartmann and Gaddy | Procedure writers and editors | September 25, 2015 |
| Hartmann and Gaddy | Procedure writers and editors | December 22, 2015 |
| Frosch, Hartmann and Gaddy | Procedure writers and editors | January 22, 2016 |
| Hartmann and Gaddy | Procedure writers and editors | February 23, 2016 |
| Frosch, Hartmann and Gaddy | Procedure writers and editors | June 24, 2016 |

Manual Change History

| Procedure | Ver/Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All Sections | 1.0 / 0 | New procedures for all sections for Nodal implementation | November 28, 2010 |
| 2.3 2.4 3.2 3.3 4.3 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Added new procedure “Phase Shifter Tap Settings” Updated Note Updated step “Monitor” Updated steps “Commit/De-Commit”, “Violated Constraints” and “HRUC Committed” Updated step “Review”, “A/S Insufficiency from DAM” and “DRUC Committed” | December 1, 2010 |
| 2.3 4.2 4.3 4.4 | 1.0 / 2 1.0 / 1 1.0 / 2 1.0 / 1 | Updated “Review Weather Data Information” step 2 Added steps “DRUC Committed for Capacity Shortage” and “Projected Reserve Capacity Shortage” Updated steps “DAM Timeline Deviation, DAM Failure, DRUC Delay & Software Failure” change to step 1 | December 15, 2010 |
| 3.2 4.3 4.1 4.4 6.1 | 1.0 / 2 1.0 / 3 1.0 / 2 / 2 1.0 / 1 | Updated step “HRUC Committed Units”, “Manual Commitment”, added steps “Excess Generation” and “Canceling RUC commitments” Updated step DRUC Committed Units”, “Manual Commitment, added steps “Excess Generation” and “Canceling RUC commitments” Updated step “DAM Timeline Deviation”, DAM Failure”, DRUC Delay” Updated scripts Updated script | January 31, 2011 |
| 3.2 3.3 3.5 4.3 4.4 6.1 | 1.0 / 3 1.0 / 2 / 0 /4 / 3 1.0 / 2 | Updated step Canceling RUC Commitments Deleted HRUC Timeline Deviation and updated HRUC Failure/Timeline Deviation Added new section Updated step Canceling RUC Commitments Updated step DAM Timeline Deviation in DAM Timeline Deviation/Failure Timeline not Met in section DRUC Timeline Deviation/Failure Updated Watch and Emergency Notice | March 25, 2011 |
| 2.5 3.2 3.3 4.3 6.1 6.2 | 1.0 / 1 1.0 / 4 1.0 / 3 1.0 / 5 1.0 / 3 1.0 / 1 | Updated Monthly MIS Posting Updated step Canceling RUC Commitments Updated step Failure Updated step Canceling RUC Commitments Updated step 1 in Watch and Emergency Notice Updated step & removed step Market Notification | April 22, 2011 |
| 3.2 3.5 4.3 4.4 5.2 6.1 | 1.0 / 5 1.0 / 1 1.0 / 6 1.0 / 4 1.0 / 1 1.0 / 4 | Updated steps HRUC Committed Units and Approval Updated all steps Updated step Approval Updated step DAM Timeline Deviation Updated step Long Lead Times Updated all steps | June 8, 2011 |
| 2.3 3.1 3.2 3.5 4.2 4.3 4.4 4.5 | 1.0 / 3 1.0 / 1 1.0 / 6 1.0 / 2 1.0 / 2 1.0 / 7 1.0 / 5 1.0 / 1 | Added steps for Publish A/S Requirements Updated Load Forecast step Updated steps Excess Generation, A/S Insufficiency from SASM, Violated Constraints and Approval Corrected title to match TOC and updated 1st note Updated Load Forecast step Updated Approval step Added subtitles, step DRUC Delay & step 1 Moved section 2.6 to 4.5 | July 20, 2011 |
| 2.3 2.4 3.2 3.3 4.3 6.1 7.1 | 1.0 / 4 / 1 1.0 / 7 1.0 / 4 1.0 / 8 1.0 / 5 1.0 / 1 | Added Note to Increasing A/S Requirements before A/S Obligations Publish Added information on RMR Resource Commitment Updated step Excess Generation, added RMR Resources, RMR Commitment and Canceling RUC Commitments Updated step Commit/Decommit Resources by VDI Updated step Canceling RUC Commitments Added Projected Reserve Capacity Shortage to Watch Updated 4th note | August 24, 2011 |
| 3.2 4.2 4.3 6.1 7.1 | 1.0 / 8 1.0 / 3 1.0 / 9 1.0 / 6 1.0 / 2 | Added Note, updated step Hotline, Post and added step Cancel Deleted step RMR, updated Manual Commitment, deleted Note Updated Note Added Extreme Hot Weather in Watch Updated 3rd note and step 1 | September 1, 2011 |
| 2.3 2.4 3.1 3.2 4.3 4.4 4.5 4.6 4.5 Original | 1.0 / 5 1.0 / 2 1.0 / 2 1.0 / 9 1.0 / 10 1.0 / 6 1.0/ 0 1.0 / 0 1.0 / 2 | Deleted Phase Shifter Tap Settings Deleted step Resources Updated step Manual Commitment in Tasks prior to execution of HRUC Updated step RMR Resources and Canceling RUC Commitments Updated step for Canceling RUC Commitments Moved A/S Insufficiency in DAM to section 4.5 & DAM Failure to section 4.6 Moved A/S Insufficiency in DAM to section 4.5 & deleted Increase A/S Capacity needs about Day-Ahead Requirements Moved from section 4.5 Deleted procedure (was section 4.5), duplicate | November 1, 2011 |
| 2.3 6.1 | / 6 1.0 / 7 | Removed Invalid SPS/RAP due to Outage Updated Post in “Notifications” All procedures in this manual have been reviewed. | December 15, 2011 |
| 1.2 3.5 4.3 4.6 | 1.0 / 1 1.0 / 3 1.0 / 11 1.0 / 3 | Updated Scope Updated all steps Updated A/S Insufficiency from DAM Updated desktop guide section | January 19, 2012 |
| 2.1 2.3 2.5 3.1 3.2 3.3 3.7 4.2 4.3 4.4 4.5 4.6 5.2 6.1 7.1 | 1.0 / 1 1.0 / 7 1.0 / 2 1.0 / 3 1.0 / 10 1.0 / 5 1.0 / 0 1.0 / 4 1.0 / 12 / 7 1.0 / 3 1.0 / 4 1.0 / 2 1.0 / 8 1.0 / 3 | Updated 4th Paragraph Updated Desktop Guide reference Updated Monthly MIS Posting Updated Desktop Guide reference Updated Desktop Guide references and step After Approval Added step Create Save Case Added new procedure Projected Capacity Reserve Shortage with no Market Solution Updated Desktop Guide references Updated Desktop Guide references and added step After Approval Added step 2 Updated Desktop Guide reference Updated Desktop Guide reference Added step Create Save Case Updated step 1 of Watch Updated Desktop Guide references | March 1, 2012 |
| 1.1 2.1 3.1 3.2 3.3 4.2 4.3 5.1 5.2 6.1 8.1 | 1.0 / 1 1.0 / 2 1.0 / 4 1.0 / 11 1.0 / 6 1.0 / 5 1.0 / 13 1.0 / 1 1.0 / 3 1.0 / 9 1.0 / 1 | Changed Shift Engineer to Operations Support Engineer Changed TSP,DSP to TO Changed Shift Engineer to Operations Support Engineer Changed Shift Engineer to Operations Support Engineer Changed Shift Engineer to Operations Support Engineer Changed Shift Engineer to Operations Support Engineer and added WRUC Changed Shift Engineer to Operations Support Engineer and Manual Commitment Changed Shift Engineer to Operations Support Engineer Changed Shift Engineer to Operations Support Engineer and updated step Long Lead Times for NPRR402 Updated OCN, Advisory, Watch, Emergency Notice sections Changed Shift Engineer to Operations Support Engineer | May 1, 2012 |
| 1.1 1.3 2.3 3.1 3.2 3.3 4.2 4.3 4.4 5.2 6.1 7.1 | 1.0 / 2 1.0 / 1 1.0 / 8 1.0 / 5 / 12 / 7 / 6 / 14 / 8 1.0 / 4 1.0 / 10 1.0 / 4 | Updated last paragraph, HRUC Removed ERCOT Shift Supervisor paragraph Updated step 3, added Fuel Switching and Optimize Fuel Supply & 2nd note Changed Shift Engineer to Operations Support Engineer Updated HRUC Committed Units Updated Create Save Case Updated Manual Commitment on 14:30 each day Updated DRUC Committed Units Updated step 2 in Delay of DRUC Updated Create Save Case Updated all step 1’s Updated 4th note | July 16, 2012 |
| 2.2 3.2 4.3 | 1.0 / 1 1.0 / 13 1.0 / 15 | Added Hotline Call Communication Updated Manual Commitment and Validate Updated Manual Commitment and Validate All procedures in this manual have been reviewed. | November 1, 2012 |
| 2.3 4.3 4.6 | 1.0 / 9 1.0 / 16 1.0 / 5 | Added Blackstart Availability Updated Review Updated steps SASM not able to Procure all A/S Requested & Cancel Emergency Notice | March 1, 2013 |
| 3.1 3.2 3.3 3.5 3.7 4.3 4.4 4.5 4.6 5.2 6.1 | 1.0 / 6 1.0 / 14 1.0 / 8 1.0 / 4 1.0 / 1 1.0 / 17 1.0 / 9 1.0 / 4 1.0 / 6 1.0 / 5 1.0 / 11 | Updated step Deselect Contingencies Updated step Monitor, Excess Generation, Hotline, & Cancel Updated step Failure & Create Save Case Updated step REG/RRS Updated all steps Updated 1st Note, A/S Insufficiency from DAM, Excess Generation &DRUC Committed from Capacity Shortage Updated all steps Updated all steps Updated all steps Updated step Create Save Case Updated Notifications | June 1, 2013 |
| 3.5 4.3 4.4 4.6 6.1 | 1.0 / 5 1.0 / 18 1.0 / 10 1.0 / 7 1.0 / 12 | Correct typo in script Correct typo’s in scripts Updated Delay of DRUC steps Corrected reference in desktop guide Updated step 1 in Watch & Emergency Notice | July 15, 2013 |
| 3.2 3.3 | 1.0 / 15 1.0 / 9 | Updated step HRUC Committed Units, Manual Commitment, HRUC Decommitted Resources & Approval Updated step Create Save Case | August 9, 2013 |
| 3.2 4.3 5.1 5.2 | 1.0 / 16 1.0 / 19 1.0 / 2 1.0 / 6 | Updated steps Violated Constraints, HRUC Committed Units, RMR Commitment & Manual Commitment Updated steps Violated Constraints, DRUC Committed Units & Manual Commitment Updated titles Updated Violated Constraints, Disapprove & Log. Deleted Long Lead Times, All procedures in this manual have been reviewed. | December 13, 2013 |
| 3.3 4.4 4.6 6.1 | 1.0 / 10 1.0 / 11 1.0 / 8 1.0 / 13 | Updated for NPRR542 Updated for NPRR542 Updated for NPRR542 Updated for NPRR542 and 529 | January 1, 2014 |
| 2.3 3.2 3.3 3.6 4.3 6.2 6.3 | 1.0 / 10 1.0 / 17 / 11 1.0 / 1 1.0 / 20 1.0 / 0 1.0 / 2 | Updated Review and Select Load Forecast Updated step System Summary, HRUC Committed Units & VDI information Updated VDI information Added Manual Commit of a Resource & Canceling RUC Commitments Updated VDI information Updated DRUC Committed Units & VDI information Added new EEA procedure Change section number from 6.2 to 6.3 | April 4, 2014 |
| 2.2 2.3 2.4 2.5 3.2 3.6 4.5 4.6 5.2 6.1 | 1.0 / 2 1.0 / 11 1.0 / 3 1.0 / 3 1.0 / 18 1.0 / 2 1.0 / 5 1.0 / 9 1.0 / 7 1.0 / 14 | Added VDIs to Master QSEs Added Note to Increasing A/S before Publishing Added Note Updated Monthly MIS Posting step Updated step A/S Infeasibility Updated step 1 Updated step A/S Insufficiency Offers Updated DAM Failure Updated step Disapprove Added Note, updated Advisory & Watch | June 1, 2014 |
| 3.2 6.1 | 1.0 / 19 1.0 / 15 | Updated Undeliverable A/S Capacity, added STNET Study and title change on VSAT and RUC perform AC Analysis Updated Generic Script | October 1, 2014 |
| 3.2 3.2 4.3 6.2 | 1.0 / 20 1.0 / 20 1.0 / 21 1.0 / 1 | Updated step STNET Study, HRUC Committed Units & Manual Commitment Updated STNET Study, HRUC Committed Units & Manual Commitment Updated step DRUC Committed Units & Manual Commitment Added step All procedures in this manual have been reviewed | December 15, 2014 |
| 2.2 2.3 3.2 3.3 3.6 4.3 4.4 6.2 | 1.0 / 3 1.0 / 12 1.0 / 21 1.0 / 12 1.0 / 3 1.0 / 22 1.0 / 12 1.0 / 2 | Added Dispatch & Verbal Dispatch Instruction Deleted Meterlogix number. Updated Priority Outages Corrected VDI vs. Dispatch Instruction and Manual Commitment Corrected VDI vs. Dispatch Instruction Corrected VDI vs. Dispatch Instruction Updated step Manual Commitment & corrected VDI vs. Dispatch Instruction Updated DAM Timeline Deviation Corrected VDI vs. Dispatch Instruction | March 1, 2015 |
| 3.2 3.3 3.5 3.6 3.7 4.3 4.4 4.5 4.6 6.1 | 1.0 / 22 1.0 / 13 1.0 / 6 1.0 / 4 1.0 / 2 1.0 / 23 1.0 / 13 1.0 / 6 1.0 / 10 1.0 / 16 | Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Updated to implement NPRR679 Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure | May 1, 2015 |
| All Sections 5.2 | 1.0 / 1 1.0 / 8 | Added a “Q” for QSE scripts Updated Disapprove with email notification | July 15, 2015 |
| 3.6 | 1.0 / 5 | Updated 1st note | October 1, 2015 |
| 2.5 3.3 3.5 3.7 4.3 4.4 4.5 4.6 6.1 | 1.0 / 4 1.0 / 14 1.0 / 7 1.0 / 3 1.0 / 24 1.0 / 14 1.0 / 7 1.0 / 11 1.0 / 17 | Updated Monthly MIS Posting Added step After 20th of the month Updated step Last Day of the Month Updated HRUC Failure/Timeline Deviation step Failure Q#79 & Q#80 Updated step REG/RRS – RUC Committed Shortages Q#81& Q#82 Updated step Hotline Q#83 Updated step Cancel Q#84 Updated step A/S Insufficiency from DAM Q#86 Updated step Excess Generation Typical Script Q#87 & Q#88 Updated DAM Timeline Deviation step DAM Timeline Deviation Q#92 Updated Title DRUC Delay Updated DRUC Delay step DRUC Completes By 18:00 Q#94 Updated DRUC Delay step 2 Typical Script Q#96 Updated step A/S Insufficiency Offers Q#97 Updated step DAM Complete with A/S Q#98 Updated step Cancel Watch Q#99 Updated step DAM Failure Q#100 Updated step Cancel Watch Q#101 Updated Title Operating Condition Script Updated Operating Condition Script step Hotline Q#46 Updated Operating Condition Script step Hotline Cancellation Q#47 All procedures in this manual have been reviewed | December 31, 2015 |
| 2.1 3.6 3.6 3.7 | 1.0 / 3 1.0 / 0 1.0 / 6 1.0 / 4 | Updated System Operator Responsibility and Authority Added new Assigning Ancillary Services procedure Change section number from 3.6 to 3.7 Change section number from 3.7 to 3.8 Updated Hotline Q#83 Updated Cancel Q#84 | February 10, 2016 |
| 1.3 5.2 | 1.0 / 2 1.0 / 9 | Removed Interchange Coordinator Added step EDI step | March 1, 2016 |
| 2.1 2.2 2.4 3.1 3.2 3.3 3.6 3.74.3 5.2 6.1 6.2 | 1.0 / 4 1.0 / 4 1.0 / 4 1.0 / 7 1.0 / 23 1.0 / 15 1.0 / 1 1.0 / 71.0 / 25 1.0 / 10 1.0 / 18 1.0 / 3 | Updated for COM-002-4 Updated for COM-002-4 Added steps Note, Resources, 1, 2, & 3 Updated RMR Consideration &Manual Commitment steps Updated for COM-002-4 Updated for COM-002-4 Updated for COM-002-4 Updated for COM-002-4 & noteUpdated for COM-002-4 Updated for COM-002-4 Updated for COM-002-4 Updated for COM-002-4 | June 30, 2016 |