- Power Operations Bulletin # 753

ERCOT has posted/revised the Transmission and Security manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

- http://www.ercot.com/mktrules/guides/procedures/index.html

# 2.	General

## 2.1	System Operator Responsibility and Authority

Procedure Purpose: To ensure the System Operators know their roles, responsibility and authority.

| Protocol Reference | 6.5.1.1 | 6.5.1.2(3) | 6.5.2 | 6.5.3(1) |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.5.2(1) |  |  |  |
| NERC Standard | EOP-002-3.1 R1 | IRO-001-1.1 R3 | PER-001-0.2 R1 | TOP-001-1a R1 |

| Version: 1 | Revision: 4 | Effective Date: June 30, 2016 |
| --- | --- | --- |

The System Operator (SO) shall, in accordance with NERC Reliability Standards, have clear decision-making authority to act and to direct actions to be taken by Transmission Operators, Generator Operators, and Transmission Service Providers within its Reliability Coordination Area to preserve the integrity and reliability of the Bulk Electric System during both normal and emergency conditions.  These actions shall be taken without delay, but not longer than 30 minutes which may include shedding of firm load without obtaining approval from higher-level personnel.  The ERCOT System Operator represents the following NERC functional entities collectively for the ERCOT ISO at any time:

- Reliability Coordinator

- Balancing Authority

- Transmission Operator

- The SO on duty is, in accordance with the ERCOT Protocols, Operating Guides, and NERC Reliability Standards, and acting as the Balancing Authority, Transmission Operator, and Reliability Coordinator shall request and receive information required to continually monitor the operating conditions and request that individual Market Participants (MPs) make changes, which will assure security and reliability of the ERCOT system.

- The SO issues Dispatch Instructions for the Real-Time operation of Transmission Facilities to a TO, and to a QSE for the Real-Time operation of a Resource.

- The SO shall, on an ERCOT-wide basis, coordinate the ERCOT System Restoration (Black Start) Plan.  The SO shall implement the Black Start Plan and shall direct the reconnection efforts of the islands, established by restoration activities.  The SO shall coordinate the mutual assistance activities of the ERCOT participants during system restoration activities.

- The SO shall consider all equipment operating limits when issuing Dispatch Instructions except as stated in Protocol Section 6.5.9, Emergency Operations, if a Dispatch Instruction conflicts with a restriction that may be placed on equipment from time to time by a TO, or a Generation Resource’s QSE to protect the integrity of equipment, ERCOT shall honor the restriction.

- The SO performs security analyses on a Day Ahead and real-time basis and ensures all Forced Outages are entered into the Outage Scheduler. The SO shall obtain or arrange to provide emergency energy over the DC Tie(s) on behalf of ERCOT.

- The SO shall issue appropriate OCN’s, Advisories, Watches, and Emergency Notices, and coordinate the reduction or cancellation of clearances, re-dispatch of generation, and request, order, or take other action(s) that the SO determines is necessary to maintain safe and reliable operating conditions on the ERCOT system in accordance with ERCOT Protocols, Operating Guides, and NERC Reliability Standards.  The SO will implement and terminate ERCOT Time Corrections, and will determine the need for and implement the operation of a Qualified Scheduling Entity (QSE) on Constant Frequency Control for loss of ERCOT’s load frequency control system.

- As the Reliability Coordinator, ERCOT ISO shall comply with its Regional Reliability Plan that has been approved by the NERC Operating Committee.

# 2.2	Communication

Procedure Purpose:  To improve communication to reduce the possibility of miscommunication that could lead to action or inaction harmful to the reliability of the grid.

| Protocol Reference | 6.5.7.8 | 6.5.8 |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 3.1.3 |  |  |  |
| NERC Standard | COM-002-4 |  |  |  |

| Version: 1 | Revision: 4 | Effective Date: June 30, 2016 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ## Three-Part Communication |  |
| NOTE | - Operating Instructions and Dispatch Instructions are synonymous and both require ‘three-part communication’. - Refer to the Communications Protocols document for requirements. |
| 1 | When issuing Operating Instructions, use three-part communication: - Issue the Operating Instruction - Receive a correct repeat back - Give an acknowledgement |
| 2 | Many scripts have been placed throughout the procedures as a reminder for the three-part communication. However, a script cannot be provided for every scenario. Effective three-part communication skills are mandatory. |
| ## Hotline Call Communication |  |
| 1 | When making Hotline calls, verify that every TO has answered. IF: - Not every TO answered the Hotline; THEN: - Contact them using their OPX line or LD line to provide them with the message - Inquire why they were not on the Hotline call - Open a Help ticket if ERCOT’s Telecommunications department is needed to investigate. |
| ## Master QSE |  |
| 1 | Issue the VDI to the Master QSE of a Generation Resource that has been split to function as two or more Split Generation Resources as deemed necessary by ERCOT to effectuate actions for the total Generation Resource for instances when electronic Dispatch Instructions are not feasible. |
| LOG | Log all actions. |

# 4.	Manage Transmission Congestion

## 4.1	Transmission Congestion Management

Procedure Purpose:  To verify and take corrective action for post-contingency overloads for various conditions.

| Protocol Reference | 3.10.4(2) | 6.5.1.1 | 6.5.5.2 (1) |  |
| --- | --- | --- | --- | --- |
|  | 6.5.7.1.10 | 6.5.7.1.11 | 6.5.7.8 | 6.5.9 (2) |
|  | 6.5.9.2(3)(c)&(e) | 6.5.9.3.3(2)(c) | 6.5.9.3.4(2) | 6.5.9.3.4(5) |
| Guide Reference | 2.2.2 |  |  |  |
| NERC Standard | IRO-002-2 R5, R7 | IRO-003-2 R1, R2 | IRO-005-3.1a R1.2, R1.3, R1.7, R1.10, R6, R12 | IRO-006-TRE-1 R1, R2 |
|  | IRO-008-1 R2 | PER-004-2 R2 | TOP-004-2 R1, R3, R4, R6, R6.4 | TOP-006-2 R5 |
|  | TOP-007-0 R4 | TOP-008-1 R1, R2, R4 |  |  |

| Version: 1 | Revision: 39 | Effective Date: June 30, 2016 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | Although the steps within the procedure are numbered, the numbering is for indexing purposes and are not sequential in nature. The system operator will determine the sequence of steps, exclude steps, or take any additional actions required to ensure system security based on the information and situational awareness available during both normal and emergency conditions. |
| Authority | ERCOT System Operators have the authority to take or direct timely and appropriate real-time action, up to and including shedding firm load to alleviate System Operating Limit (SOL) violations. Following a separation from the Interconnection, and following automatic under-frequency load shedding, System Operators will also instruct TOs to shed additional load manually when there is insufficient capacity to restore system frequency. To include directing physical operation of the ERCOT Transmission Grid, including circuit breakers, switches, voltage control equipment, and Load-shedding equipment. |
| Unknown State | When in an unknown operating state (any state for which valid operating limits have not been determined), it will be considered to be an emergency and ERCOT shall restore operations to respect proven reliable power system limits within 30 minutes. |
| CAUTION | IF: - At any time, the prescribed measures within this procedure fail to resolve the congestion, AND - The transmission system is in an unreliable state (see Section 4.2 if a DC-Tie has a shift factor) THEN: - Issue an Emergency Notice - See Generic Script in Section 7.1 - Notify Real-Time operator to make hotline call to QSEs. |
| Critical Facilities | Critical facilities are the ERCOT defined contingencies that show up after running Real Time Contingency Analysis (RTCA) as a post-contingency overload. This list is located in the EMS and an electronic copy is located on the MIS Secure site: Select: Grid>Generation>Reliability Unit Commitment>Standard Contingency List’ Select “Standard Contingency List” Open the zip file>Open the CIM file>Select the Standard_Contingency_List tab and view the contingencies. A potential critical facility becomes a critical facility when the contingency appears in RTCA as a post-contingency overload. |
| NOTE | Congestion Management techniques consist of: - SCED - Phase Shifters (shift factors are on the TCM display) - Remedial Action Plan (RAP) - Pre-Contingency Action Plan (PCAP) - Mitigation Plan (MP) – enacted Post-Contingency - Temporary Outage Action Plans (TOAP) - Building a manual constraint - Non-Spin The electronic and hard copy for the RAPs, PCAPs, and MPs are to be considered current. Should a conflict exist between the electronic and hard copy, the electronic version is to be used. - This data can be viewed at ERCOT SharePoint > System Operations – Control Center > Quick Links > Special Protection Systems (SPS) and/or MP/PCAP/RAP , - OCTOAPs are located in the daily Outage Notes. |
| Constraint Shift Factor Cut Off | Basecase and post-contingency constraints which do not have generator shift factors for units greater than or equal to 2% as indicated in EMS or indicate NOSCED are not activated in SCED. See Section 4.6 Mitigation Plan for additional details. |
| ### Review Planned Outage Notes |  |
| Non-Cascading Condition | Review daily outage notes: IF: - Studies indicate a high post-contingency overload (125% of Emergency rating or greater) due to a Planned outage AND it is not a cascading condition; THEN: - Allow the outage - Activate the constraint and step the constraint down by adjusting the %Rating (increments of 5%) |
| Cascading Condition | IF: - Studies indicate a high post-contingency overload (125% of Emergency rating or greater), OR it is a cascading condition, OR - An unsolved contingency, OR - A Basecase overload; THEN: - Take pre-posturing measures to reduce the flow before the outage is taken - Use RTMONI if available on a GTC, OR - Have a manual constraint created if needed IF: - Constraint is ineffective THEN: - Use HDL/LDL override as last resort - Post message on MIS Public Typical MIS Posting Script: ERCOT is taking manual actions to pre-posture for XXXX outage ONCE: - Studies show that the post-contingency is below 125% of Emergency rating - Give approval for the outage, - Activate constraint, and - Release manual override after SCED runs - Cancel MIS posting. |
| Log | Log all actions. |
| ### Evaluate Real Time Contingency Analysis (RTCA) Results |  |
| 1 | IF: - A major topology change has occurred; THEN: - Re-run RTCA and VSAT. IF: - A constraint needs to be controlled before the next SCED run THEN: - Manually run RTCA after activating the constraint, AND - Manually execute the SCED process |
| Log | Log all actions. |
| ### Post-Contingency Overloads |  |
| 1 | IF: - A post-contingency overload is approaching 98% of its Emergency Rating; THEN: - Verify the contingency definition associated with the constraint is accurate and appropriate given the current state of the grid - Verify SCADA is of similar magnitude to the pre-contingency value (MW and MVAR flows) - Review the limits in DYNRTG static table in order to ensure that the telemetry of the lines is within the acceptable range. |
| 2 | IF: - Inaccurate, - Indicate NOSCED, OR - There is not a unit with at least a 2% shift factor; THEN: - DO NOT employ congestion management techniques, - Notify the Shift Supervisor and Operations Support Engineer to investigate or create a CMP. - Acknowledge the constraint and list a reason using the drop down box, - The comment field should be used for additional information |
| 3 | IF: - Accurate, AND - There is a unit with at least a 2% shift factor; THEN: - Verify no SPS (identified as RAS in EMS), or RAP exist - Activate constraint - Lower the value in the % Rating column in TCM to tighten the constraint as needed (minimum of 95%, excluding GTCs) IF: - A PST can help solve the congestion; THEN: - Activate the constraint until the PST is studied and moved. |
| 4 | IF: - A post-contingency overload of 98% or greater of the Load Shed Rating exist with a RAP in place; THEN: - Activate the constraint to reduce the predicted post-contingency loading to no more than 98% of the Load Shed Rating; IF: - Constraint needs to be controlled within the next 5 minutes; THEN: - Manually run RTCA after activating the constraint, - Manually execute the SCED process, - Refer to “Managing Constraints in SCED”. |
| ### Basecase Overloads |  |
| 1 | IF: - A Basecase exists THEN: - Verify SCADA is of similar magnitude to the Actual Basecase value (MW and MVAR flows) - Example: Review the SCADA value with Actual (state estimation value) |
| 2 | IF: - Inaccurate, - Indicate NOSCED, OR - There is not a unit with at least a 2% shift factor; THEN: - DO NOT employ congestion management techniques, - Notify the Shift Supervisor and Operations Support Engineer to investigate or create a CMP. - Acknowledge the constraint and list a reason using the drop down box, - The comment field should be used for additional information |
| 3 | IF: - Accurate, AND - There is a unit with at least a 2% shift factor; THEN: - Activate constraint - Lower the value in the % Rating column in TCM to tighten the constraint as needed (minimum of 95%, excluding GTCs) IF: - A PST can help solve the congestion; THEN: - Activate the constraint until the PST is studied and moved. |
| ONTEST | Resources with a Resource Status of ONTEST, may not be issued dispatch instructions except: - For Dispatch Instructions that are a part of the testing; or - During conditions when the Resource is the only alternative for solving a transmission constraint (would need QSE to change Resource Status); or - During Force Majeure Events that threaten the reliability of the ERCOT System. |
| QSGR | Market Operation>Real-Time Market>SCED Displays>DSI Displays>DSI Data Processes>DSI Operator Manual Overide HDL And LDL IF: - A QSGR is needed for voltage support or an unsolved contingency; THEN: - Override LDL to a level greater than or equal to the COP LSL - DO NOT override while SCED is running, - Notify QSE as time permits - Post message on MIS Typical MIS Posting Script: ERCOT is taking manual actions for XXXX constraint. - These Resources can be viewed at ERCOT SharePoint > System Operations – Control Center > Quick Links > Approved Quick Start (QSGR) Resources |
| Not Dispatchable to SCED | REVIEW REFERENCE DISPLAY: EMS Applications>Generation Control>Resource Limit Calculation>RLC Unit Input Data and RLC Unit Output Data IF: - A QSE has telemetered more A/S on a specific Resource that is greater than their HSL, OR - A Resource is generating more than their telemetered HSL; THEN: - SCED will set the HDL=LDL=MW making the Resource undispatchable, - Request the QSE to make corrections to telemetry (Resource status, Resource limits, A/S responsibilities, etc.) - Disregard IRRs unless transmission constraint is active. |
| Qualifying Facilities | A list of Qualifying Facilities can be found in Desktop Guide Common to Multiple Desk section 2.20 IF: - A Qualifying Facility (QF) is needed to operate below its LSL, or be ordered off-line to solve congestion; THEN: - Issue an electronic Dispatch Instruction confirmation to the appropriate QSE, - Choose “DECOMMIT or ERCOT REQUESTED QF OPERATE BELOW LSL” as the Instruction Type from Resource level - Enter contingency name in “other information” When issuing a VDI or confirmation, ensure the use of three-part communication: - Issue the Operating Instruction - Receive a correct repeat back - Give an acknowledgement - Issue an Emergency Notification via Hotline call to TOs, - Instruct the Real-Time Operator to make Hotline call to QSEs, - Post message to MIS Public. T#28 - Typical Hotline Script for Emergency Notice for instructing Qualifying Facility to operate offline/below LSL |
| Log | Log all actions. If known, log the outage that is causing the congestion. |
| ### Post-Contingency Overloads on Private Use Networks (PUNs) or Customer Owned Equipment behind the Meter |  |
| 1 | IF: - A post-contingency overload is 100% of its Emergency Rating on a PUN or customer owned equipment; THEN: - Contact the appropriate QSE/PUN to alert them of the post-contingency overload, VERIFY: - There is a plan to mitigate the overload if the contingency were to occur. |
| 2 | IF: - It is determined that the QSE/PUN has no way to mitigate or correct the congestion; THEN: - Instruct the QSE/PUN to take action such as lower/raise generation or load (verbal Operating Instruction only, do not override HDL/LDL or activate constraint in SCED) and - Acknowledge the post-contingency overload in TCM. |
| 3 | IF: - The contingency occurs; THEN: - Notify the QSE/PUN to ensure action is being taken on the plan. |
| 4 | IF: - A post-contingency overload of 98% or greater of its Emergency Rating on transmission equipment (non-PUN or customer owned equipment), and the only shift factor of 2% or more is a PUN unit; THEN: - Activate the constraint. |
| Log | Log all actions. |
| ### Managing Constraints in SCED |  |
| NOTE | One of the key tasks is to properly monitor and manage transmission constraints. Keep track of non-binding constraints that have flows approaching their limits and be prepared to take action as the constraint approaches its rating. |
| Output Displays | REVIEW REFERENCE DISPLAY: Market Operation>Real-Time Market>SCED Displays>DSP Displays>DSP Constraint Summary Once SCED has completed its run, check the validity of the binding/exceeded constraints, limits, shadow price, and current real-time flows. |
| In Series | It is common for series elements to have nearly identical shift factors for a given contingency. If post-contingency loading of 98% or greater occurs for multiple elements which have been identified as being in series with each other, only the most limiting constraints should be activated to mitigate all the series element congestion. Example: Contingency A overloads X, Contingency A overloads Y |
| Same Element | If post-contingency loading of 98% or greater occurs on the same element for multiple contingencies and they have nearly identical shift factors, only one of the most limiting constraints should be activated to mitigate the congestion. Example: Contingency A overloads X, Contingency B overloads X |
| 1 | Verify that the SCED executions are reducing the flows on each constraint that is binding. |
| 2 | When a constraint becomes violated in SCED, which is when it has reached its max shadow price and is exceeding its Emergency rating, review the following bullets to take the appropriate action(s): - Confirm that pre-determined relevant RAPs are properly modeled in the EMS, - Ensure base points are being followed , - Remove Resource from ONTEST , - Remove A/S to increase capacity available to SCED (see procedure below), - Determine if a unit carrying Off-line Non-Spin could be used, - Ask Resource Operator to deploy Non-Spin for the specific unit - The telemetered Non-Spin schedule must be changed to 0 for SCED to dispatch the Resource - Determine if additional units could be committed/decommitted, - Confirm SCED is balancing conflicting constraints - Ensure reactive devices are being utilized |
| 3 | IF: - All applicable steps above have been completed, AND constraint is still exceeding its Emergency Rating; THEN: - Seek to determine what unforeseen change in system condition has arisen and where possible, seek to reverse the action, - Instruct Operations Support Engineer to develop a mitigation plan, AND - Contact Manager, System Operations and/or Control Room Operations Manager to investigate further - Refer to Section 4.3, Closely Monitored SOLs |
| NOTE | EMP Applications>TCM-Transmission Constraint Manager>Related Displays>Message Log for CAM IF: - No shift factors are passed for the constraint; THEN: - Contact Help Desk to issue a ticket to EMMS Production to fix immediately. |
| Log | Log all action taken including the following: - Reason for doing a manual override - Any security violations that were ≥ 125% of the Emergency Rating |
| ### Remove A/S to Increase Capacity available to SCED |  |
| 1 | RLC Unit Input Data display IF: - A/S needs to be removed from a specific unit in order to increase capacity to SCED; THEN: - Instruct the QSE to remove the A/S by updating their telemetry to ON to free that capacity to SCED - Notify Resource Operator with undeliverable A/S type, amount and approximate hours. |
| LOG | Log all actions. |
| ### Unsolved Contingencies |  |
| 1 | Periodically check the “Contingency Solution Results” display: IF: - An unsolved contingency exist; THEN: - Run the State Estimator again, - If unsolved contingency remains, notify the Operations Support Engineer to investigate IF: - Generation needs to be re-dispatched to solve the contingency - Use HDL/LDL override - Post message on MIS Public (only if a manual override is used) Typical MIS Posting Script: ERCOT is taking manual actions for an unsolved contingency. WHEN: - Constraint solves and the contingency comes into RTCA - Activate constraint, and - Release manual override after SCED runs - Cancel MIS posting. |
| LOG | Log all action taken including the following: - Reason for unsolved contingency - Actions taken to resolve |
| ### Model Inconsistencies/Updates |  |
| 1 | IF: - Any inconsistencies in ratings, impedance changes, etc. are found; THEN: - Notify Operations Support Engineer so that they can work with the TO to confirm the correct information and if required, correct it through the NOMCR process. |
| 2 | IF: - There is a difference in line ratings between ERCOT and a TO; THEN: - The most limiting rating will be used until the correct rating can be determined - Notify Operations Support Engineer so that they can work with the TO to confirm the correct information and if required correct it through the NOMCR process. |
| LOG | Log all actions. |
| ### QSE Requests to Decommit a Resource |  |
| 1 | IF: - Notified by the Resource/RUC Operator of a request to decommit a self-scheduled Resource; THEN: - Perform a real-time study (if necessary) to determine that no violation of security criteria exist with the Resource off-line and no additional active constraints for SCED will occur, - Notify the Resource/RUC Operator with determination. |

## 4.2	Transmission Congestion in the Rio Grande Valley

Procedure Purpose:  To verify and take corrective action for post-contingency overloads and/or voltage conditions.

| Protocol Reference | 4.4.4(10) |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 2.2.2 |  |  |  |
| NERC Stadard | EOP-001-2.1b R2.2, R2.3, R3.1, R3.2, R3.3, R4, R6.3 | EOP-003-2 R1, R8 | IRO-002-2 R5, R7 | IRO-003-2 R1 |
|  | IRO-005-3.1a R1.2, R1.3, R6, R12 | IRO-006-TRE-1 R1, R2 | PER-004-2 R2 | TOP-001-1a R2 |
|  | TOP-007-0 R4 | TOP-008-1 R1, R2 |  |  |

| Version: 1 | Revision: 24 | Effective Date: June 30, 2016 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Rio Grande Valley |  |
| NOTE | DC Tie exports shall not be curtailed during the Adjustment Period, or for more than one hour at a time, except for the purpose of maintaining reliability. |
| RUC/ Future Studies | IF: - HRUC or off-line studies indicate the need to commit Valley Resources, THEN: - Commit for time-frame needed IF: - If studies show high probability of load shed with all available Valley Resources committed, exports on DC-R curtailed, available emergency energy from DC-R, and any outages that can be returned to service within time-frame needed; THEN: - Issue a transmission emergency for the hours projected to be in this condition - Notify QSE for Frontera of the need to switch the generation from CFE into ERCOT - QSE will need to update COP for RUC to be provided |
| Topology Change | IF: - A topology change occurs; THEN: - Re-run RTCA and VSAT. IF: - A constraint needs to be controlled before the next SCED run THEN: - Manually run RTCA after activating the constraint, AND - Manually execute the SCED process |
| Reliability Margin ≤250 MW | Request TOs in the affected areas to coordinate with generators and TOs to increase voltages by placing capacitor banks in-service and turning off reactors near the weak busses that are available without exceeding high Voltage SOLs. |
| 1 | IF: - A post-contingency overload is approaching 98% of the Emergency Rating with shift factors for a DC-Tie export; THEN: - Activate the constraint if a 2% or more shift factor exists. IF: - Shift factors exists for a DC-Tie export only or if activating the constraint does not fully resolve the congestion; THEN: - Ensure appropriate Resources have been committed, - Ensure a Mitigation Plan exists for the contingency and review with TO, - If no Mitigation Plan exists, notify Operations Engineer to create one. |
| 2 | WHEN: - VSAT runs and provides an updated limit for the Valley Import; THEN: - Update RTMONI. WHEN: - The Valley Import is approaching 85% of the limit, OR - The Reliability margin is approaching 150; THEN: - Activate the Valley Import constraint. OR WHEN: - There is a transmission outage on a 345kV into the Valley (refer to Operations Support Engineer for limit); THEN: - Ensure RTMONI is updated with the limit. WHEN: - The Valley Import is approaching 85% of the limit, THEN: - Activate the Valley Import constraint. Note: For an unsolved contingency scenario, activate the Valley Import constraint to get the contingency to solve. This may require setting the %Rating lower than 85%. |
| 3 | IF: - One of the following conditions exist without a generation solution: - Unsolved contingency - Post-contingency loss of a 345kV to the Valley overloads a 345kV - Post-contingency overload above 125% - Valley import is above 90% - Reliability margin is below 95; THEN: - Issue a Transmission Emergency Notice - Make Hotline call to TOs - Posting message on MIS Public - Notify Real-Time Desk to make Hotline call to QSEs T#29 - Typical Hotline Script for Transmission Emergency for the Rio Grande Valley or Laredo Area Typical MIS Posting Script: Transmission Emergency Notice has been issued for the Rio Grande Valley due to [state issue used in hotline call]. Edit script as needed to fit situation. |
| NOTE | IF: - If there is a high probability of activating the mitigation plan; THEN: - Notify QSE for Frontera of the need to switch the generation from CFE into ERCOT. |
| 4 | IF: - The Transmission Emergency is issued, AND - One of the following conditions exist without a generation solution: - Unsolved contingency - Post-contingency loss of a 345kV to the Valley overloads a 345kV - Post-contingency overload above 125% - Valley import is above 90% - Reliability margin is below 95; THEN: - Request Resource Operator to deploy Load Resources in the Valley that have an obligation. |
| 5 | IF: - The Transmission Emergency is issued, AND - One of the following conditions exist without a generation solution: - Unsolved contingency - Post-contingency loss of a 345kV to the Valley overloads a 345kV - Post-contingency overload above 125% - Valley import is above 95% - Reliability margin is below 85; THEN: - Request DC-Tie Operator to curtail any exports on the Railroad DC-Tie - Request emergency energy from the appropriate DC-Tie Operator across the Railroad DC-Tie. IF: - CFE is able to send emergency - Notify ERCOT DC-Tie Operator |
| 6 | IF: - There are no exports schedules to curtail or exports have been curtailed and the transmission area is in an unreliable condition without a generation solution and includes one of the following: - Unsolved contingency - Post-contingency loss of a 345kV to the Valley overloads a 345kV - Post-contingency overload above 125% - Valley import is above 100% - Reliability margin is below 25; THEN: - Follow mitigation plan |
| LOG | Log all actions. |
| ### Transmission/Capacity Issues within the CFE Area |  |
| NOTE | On the CFE side of the Railroad DC-Tie, there is an automatic runback scheme that runs back the DC-Tie under CFE contingency conditions. |
| 1 | IF: - Notified by a DC-Tie Operator that CFE is unable to maintain reliability and needs to curtail an E-Tag; THEN: - Verify the MW amount, DC-Tie and time of the curtailment, - Notify ERCOT DC-Tie operator with information. |
| 2 | IF: - Notified by a DC-Tie Operator that CFE is requesting emergency energy; THEN: - Determine which DC-Tie(s) and amount being requested, - Determine or have Operations Support Engineer determine that sending emergency energy to CFE would not put ERCOT in an emergency condition IF: - ERCOT is able to send CFE emergency energy; THEN: - Notify ERCOT DC Tie Operator with information and request they issue an electronic Dispatch Instruction. |
| 3 | WHEN: - Notified by a DC-Tie Operator that CFE no longer is in need of emergency energy; THEN: - Notify the ERCOT DC Tie Operator with information. |
| LOG | Log all actions. |

## 4.3	Closely Monitored SOLs

Procedure Purpose: To identify SOLs that should be closely monitored.

| Protocol Reference | 3.10.4(2) | 6.5.7.1.10(2)(b) | 6.5.7.1.11 | 6.5.9 (2) |
| --- | --- | --- | --- | --- |
|  | 6.5.9.2(3)(e) |  |  |  |
| Guide Reference | 2.2.2 | 4.5.2(2)(b) |  |  |
| NERC Standard | EOP-001-2.1b R2.2, R2.3 | IRO-002-2 R5 | IRO-003-2 R1 | IRO-005-3.1a R12 |
|  | IRO-006-TRE-1 R1, R2 | TOP-004-2 R1, R3 | TOP-007-0 R4 | TOP-008-1 R1 |
|  | VAR-001-4.1 R3 |  |  |  |

| Version: 1 | Revision: 13 | Effective Date: June 30, 2016 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Cascading Outages | Uncontrolled successive loss of system elements – widespread electric service interruption that cannot be restrained from sequentially spreading beyond an area predetermined by studies. |
| SOL Turns Into IROL | An SOL is an IROL if: - Loss of load (manual or auto) is greater than 6% of the ERCOT load level used in the study - Triggers automatic under-frequency load shedding - Observable inter-area oscillation with damping ratio less than 3% |
| NOTE | Monitor for any of the following conditions: - Post-contingent rating exceedance in excess of 125% of the Emergency Rating - Basecase exceedance greater than 100% of the Normal Rating - An unsolved contingency - A divergent case in VSAT/TSAT - Under-voltage condition characterized by bus voltages of less than 90% across three or more related BES facilities - Over-voltage condition greater than 110% across three or more BES facilities |
| 1 | IF: - Any of the above exists; THEN: - Confirm the appropriate transmission congestion procedures have been completed, - Notify the Operations Support Engineer to perform cascading outage studies |
| Studies | If a facility approaches 125% of Emergency Rating, a study for the loss of the contingency element and the overloaded facility will be conducted: - If the study results indicate no additional facilities will be overloaded over 125% of their Emergency rating, this is determined to be a localized event and no additional pre-contingency actions will be taken - If the study results in an additional facility(s) over 125% of its Emergency rating, continue the analysis to also trip the additional circuits. This analysis will be performed tripping a maximum of 5 facilities. If the study indicates either a non-converged case OR continues to show facilities exceeding 125% of their Emergency ratings, this will be considered a potential cascade condition. |
| Localized Event | IF: - It is determined to be a localized event; THEN: - A Mitigation Plan should be developed and reviewed with the affected TO(s) |
| Cascading Condition | IF: - It is determined to be a cascading condition (not a local radial load pocket); VERIFY (time permitting): All of the following relevant actions have been implemented: - All available generation has been brought online - All generation redispatch options have been utilized - No switching action is available - All available load resources have been deployed - All available reactive devices have been deployed or adjusted without exceeding voltage limits - All available load management programs have been deployed by the ERCOT TO (if available) - All DC Tie transactions have been curtailed that negatively impacts - Emergency Energy has been requested or is being imported - Any Distribution Voltage Reduction has been implemented - All necessary Public Appeals have been made THEN: - Proceed to the next procedure “Pre-contingency Load Shedding to avoid Post-contingency cascading”. |
| ### Pre-contingency Load Shedding to avoid Post-contingency cascading |  |
| 1 | IF: - Load shed is the only option to prevent a cascading condition; THEN: - Obtain the necessary information from the Operations Support Engineer and review with the affected TO - The amount of load shed should be enough to remain below the load shed rating of the first overloaded facility - Verify if load shed needed to be location specific - Inform TO that a Transmission Emergency will be issued - Issue Operating Instruction for load shed |
| 2 | IF: - Load shed is 100 MW or greater; THEN: - Notify the Operations Support Engineer and Shift Supervisor to initiate the NXT for load shed (SO Request for Firm Load) |
| 3 | Issue a Transmission Emergency: - Make a Hotline call to TOs - Post message on MIS Public. - Notify Real-Time operator to make hotline call to QSEs T#30 - Typical Hotline Script for Transmission Emergency for Cascading Condition Typical MIS Posting Script: “ERCOT issued a Transmission Emergency for an expected cascading condition in the [area] with the contingency loss of [constraint name].” |
| 4 | WHEN: - Load can be restored; THEN: - Issue Operating Instruction to restore the load - Make Hotline call to end the Transmission Emergency - Notify Real-Time Operator to make hotline call to QSES - Cancel message on MIS - Notify the Operations Support Engineer and Shift Supervisor to initiate the NXT for restoration of load shed (SO Requested Firm Load restoration) |
| Log | Log all actions. |

## 4. 4	North-Houston Voltage Stability Limit

Procedure Purpose:  Maintain transmission Stability between the North and Houston. The North-Houston is a Generic Transmission Constraint (GTC).

| Protocol Reference | 6.5.9.1(1)(e) | 6.5.9.3.4(4) |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.2.4(1) | 4.5.2(2)(b) |  |  |
| NERC Standard | EOP-001-2.1b R2.2, R2,3, R3.2, R4 | EOP-003-2 R1, R8 | IRO-002-2 R5 | IRO-003-2 R1 |
|  | IRO-005-3.1a R1.2, 1.3, R12 | IRO-006-TRE-1 R1, R2 | IRO-008-1 R2, R3 | IRO-009-2 R1, R2, R3, R4 |
|  | PER-004-2 R2 | TOP-004-2 R1, R2, R6.4 | TOP-007-0 R2, R3, R4 | TOP-008-1 R1, R2 |

| Version: 1 | Revision: 27 | Effective Date: June 30, 2016 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| IROL | The North – Houston VSAT voltage stability limit is an IROL; the actual flow should not be allowed to exceed the limit, and MUST NOT exceed the limit for more than 30 minutes. If necessary, the System Operator has the authority to instruct load shedding before this IROL has been exceeded. |
| NOTE | Although the steps within the procedure are numbered, the numbering is for indexing purposes and are not sequential in nature. The system operator will determine the sequence of steps, exclude steps, or take any additional actions required to ensure system security based on the information and situational awareness available during both normal and emergency conditions. |
| VSAT | WHEN: - VSAT runs and provides an updated limit for the North to Houston; THEN: - Update RTMONI. WHEN: - The North to Houston flow is approaching 90% of the limit; THEN: - Activate the North to Houston constraint. |
| North-Houston 345kV Circuit Outage | IF: - Any of the 345kV lines going into the Houston area has a forced outage; THEN: - Manually run the entire sequence of RTNET, RTCA, and RTDCP (VSA) immediately and proceed to the Monitor Step in this procedure. |
| Monitor | Monitor each of the following Reliability Margins: - N-H G - N-H L If any of these Reliability Margins fall below the following pre-defined limits, take the appropriate corrective action for each limit and notify the Shift Supervisor. |
| ≤500MW | - Request TOs in the affected areas to increase voltages by placing capacitor banks in-service and turning off reactors near the weak busses that are available without exceeding high Voltage SOLs. |
| ≤400MW | - Activate the appropriate constraint |
| ≤300MW | Instruct Resource Operator to deploy Non-Spin in the Coast Weather Zone (WZ_COAST) - Issue a Transmission Watch by making a Hotline call and posting on MIS Public - Notify Real-Time Operator to make Hotline notification to QSEs T#31 - Typical Hotline Script for Watch for North to Houston Interface |
| NOTE | When the Non-Spin Resource is on-line, they must change their Non-Spin schedule to 0 in order for SCED to dispatch them. |
| ≤200MW | VDI QSGR in the Houston area that were not bid in as Non-Spin. Determine QSGR in the Coast Weather Zone (WZ_COAST) - Request RUC Operator to issue electronic Dispatch Instruction to commit |
| ≤100MW | - Instruct the Resource Desk Operator to deploy Load Resources providing RRS in Houston - Issue a Transmission Emergency Notice by making a Hotline call and posting on MIS Public - Notify Real-Time Operator to make Hotline notification to QSEs T#32 - Typical Hotline Script for Emergency Notice for North to Houston Interface |
| 0MW | - Instruct CenterPoint to drop firm load in 100 MW blocks. - Continue Transmission Emergency Notice by making a Hotline call and posting on MIS Public - Notify Shift Supervisor to make NXT notification Typical Script for CenterPoint: This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing CenterPoint an Operating Instruction to drop [*** MW] of firm load for the North – Houston interface. Notify ERCOT when this task is complete. Please repeat this back to me. That is correct, thank you.” T#33 - Typical Hotline Script for Emergency Notice for North to Houston Interface, Firm Load Shed: |
| Cancel | Make appropriate cancellations when back to normal operations. |
| Log | Log all actions. |

## 4.5	GTC Stability Limits

Procedure Purpose: Maintain transmission stability within the ERCOT region when there is a Generic Transmission Constraint (GTC).

| Protocol Reference | 6.5.9.1(1)(e) |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 2.2.2 | 4.5.2(2)(b) |  |  |
| NERC Standard | IRO-005-3.1a R12 | IRO-006-TRE-1 R1, R2 | TOP-008-1 R1 |  |

| Version: 1 | Revision: 11 | Effective Date: June 30, 2016 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ## Panhandle Stability |  |
| 1 | WHEN: - VSAT runs and provides an updated limit for the Panhandle Stability; THEN: - Update RTMONI. WHEN: - The BASECASE PNHNDL is approaching 85% of the limit; THEN: - Activate the BASECASE PNHNDL constraint in TCM. - Raise the BASECASE PNHNDL to 95% as the flow stabilizes. |
| NOTE | For an unsolved contingency scenario, activate the BASECASE PNHNDL constraint to get the contingency to solve. This may require setting the %Rating lower than 85%. |
| Topology Change | IF: - A topology change occurs; THEN: - Re-run RTCA and VSAT. IF: - A constraint needs to be controlled before the next SCED run THEN: - Manually run RTCA after activating the constraint, AND Manually execute the SCED process |
| Log | Log all actions. |
| ## Laredo Area Stability |  |
| 1 | WHEN: - All lines are in-service there is a local voltage stability issue in the Laredo area; WHEN: - VSAT runs and provides an updated limit for the Laredo Area Stability; THEN: - Update RTMONI. WHEN: - The BASECASE LAREDO flow is approaching 90% of the limit in TCM; THEN: - Activate the constraint if a 2% or more shift factor exists - The constraint activates AND; - Raise the BASECASE LAREDO to 95% as the flow stabilizes. |
| Topology Change | IF: - A topology change occurs; THEN: - Re-run RTCA and VSAT. IF: - A constraint needs to be controlled before the next SCED run THEN: - Manually run RTCA after activating the constraint, AND - Manually execute the SCED process |
| 2 | Instruct Resource Operator to deploy Non-Spin in the Laredo area |
| NOTE | When the Non-Spin Resource is on-line, they must change their Non-Spin schedule to 0 in order for SCED to dispatch them. |
| 3 | VDI QSGR in the Laredo area that were not bid in as Non-Spin. Request: - RUC Operator to issue electronic Dispatch Instruction to commit |
| 4 | IF: - One of the following conditions exist without a generation solution: - Unsolved contingency - Post-contingency overload above 125% - Laredo area is above 100% THEN: - Issue a Transmission Emergency Notice - Make Hotline call to TOs - Posting message on MIS Public - Notify Real-Time Desk to make Hotline call to QSEs T#29 - Typical Hotline Script for Transmission Emergency for the Rio Grande Valley or Laredo Area Typical MIS Posting Script: Transmission Emergency Notice has been issued for the Laredo area due to [state issue used in hotline call]. Edit script as needed to fit situation. |
| 5 | IF: - The Transmission Emergency is issued, AND - One of the following conditions exist without a generation solution: - Unsolved contingency - Post-contingency overload above 125% - Laredo area is above 100% THEN: - Request DC-Tie Operator to curtail any exports on the Laredo DC-Tie - Request emergency energy from the appropriate DC-Tie Operator across the Laredo DC-Tie. |
| NOTE | DC Tie exports shall not be curtailed during the Adjustment Period, or for more than one hour at a time, except for the purpose of maintaining reliability. |
| LOG | Log all actions. |
| ## Zorrillo – Ajo 345kV Stability |  |
| 1 | WHEN: - All lines are in-service there is a local voltage stability issue in South Texas near Ajo; THEN: - Update RTMONI from table to set the value (identified in Desktop Guide Transmission Desk 2.12); WHEN: - The BASECASE ZO_AJO flow is approaching 85% of the limit in TCM; THEN: - Activate the constraint AND; - Raise the BASECASE ZO_AJO to 98% as the flow stabilizes. |
| 2 | IF: - An outage has occurred on any of the identified elements in the table; THEN: - Refer to the constraint limit, WHEN: - The BASECASE ZO_AJO is approaching 85% of the limit; THEN: - Activate the BASECASE ZO_AJO constraint in TCM |
| 3 | If there is more than one line out of service or AEP is unable to manage the reactors at Ajo to control voltages, use the most restrictive limit in RTMONI. With more than one line out of service, this becomes more of a thermal issue and RTCA will most likely be more binding than the GTC. |
| Log | Log all actions. |
| ## Liston Stability |  |
| 1 | WHEN: - All lines are in-service there is a local voltage stability issue near the Garza – J L Bates 138 kV line; THEN: - Update RTMONI from table to set the value (identified in Desktop Guide Transmission Desk 2.12); WHEN: - The BASECASE Liston flow is approaching 90% of the limit in TCM; THEN: - Activate the constraint - The constraint activates AND; - Raise the BASECASE Liston to 98% as the flow stabilizes. |
| 2 | IF: - An outage has occurred on any of the identified elements in the table; THEN: - Refer to the constraint limit, WHEN: - The BASECASE Liston is approaching 90% of the limit; THEN: - Activate the BASECASE Liston constraint in TCM |
| Log | Log all actions. |
| ## Molina Stability |  |
| NOTE | When all lines are in-service, there is no local voltage stability issue near the Laredo area on the Molina GTC with the Javelina wind farm (BORDAS) fast stop feature installed. If the turbine is on-line the feature is in service. |
| 1 | WHEN: - Instability is observed the Javelina wind farm will reduce output to 170 MW through the generator controls, and maintain that output until the contingent event that initiated the reduction in output is restored. IF: - A reduction in output has occurred; THEN: - Verify one of the identified elements in the PI alarm display initiating the fast stop detection action at BORDAS_JAVELINA wind farms, - Notify QSE the power output of the plant will remain limited until the ERCOT operator confirms that the power limitation can be removed. - Contact the applicable ERCOT Transmission Operator to determine the topology or cause of the fast stop activation; WHEN: - Outage has returned to service or operator determines power limitation can be removed; THEN: - Notify QSE of intent to release power limitation AND - Verify the QSE has reset the Javelina wind fast stop activation alarm. |
| 2 | IF: - An outage has occurred on the identified element in the table (identified in Desktop Guide Transmission Desk 2.12); THEN: - Instruct BORDAS_JAVELINA wind farms to 0 MW |
| Log | Log all actions. |

## 4.6	SPS, RAP, PCAP, MP, and TOAP

Procedure Purpose:  To verify and take corrective action for post-contingency overloads for various conditions.

| Protocol Reference | 6.5.1.1(1) | 6.5.7.1.10(3) | 6.5.9.3.3(2)(d) |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 2.2.2(3)(b) | 4.2.3(3) | 4.3.1 |  |
| NERC Standard | EOP-001-2.1b R2.2, R2.3, R3.2, R4 | EOP-003-2 R1, R3, R8 | IRO-005-3.1a R1.2, R1.3, R6, R12 | IRO-006-TRE-1 R1, R2 |
|  | PRC-001-1 R6 | TOP-004-2 R6 | TOP-008-1 R1, R2 |  |

| Version: 1 | Revision: 23 | Effective Date: June 30, 2016 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | MPs and PCAPs information is included in the EMS, refer to Desktop Guide Transmission Desk section 2.7 Electronic copies for the SPSs, RAPs, PCAPs, and MPs can be found on SharePoint. ERCOT SharePoint > System Operations – Control Center > Quick Links > Special Protection Systems (SPS) and/or MP/PCAP/RAP |
| NOTE | Special Protection Schemes (SPS) (identified as RAS in EMS) OR Remedial Action Plans (RAP) - EXAMINE the results of RTCA, - If the background has a color indicating a SPS or RAP, - Refer to Desktop Guide Transmission Desk Section 2.7 for explanation of colors and for actions to be taken based on the color of the background. |
| Log | Log all actions. |
| ### Special Protection Systems (SPS) (Identified as RAS in EMS) |  |
| NOTE | Real Time Contingency Analysis (RTCA) indicates a Post Contingent overload(s) on a Contingency in which the SPS will not mitigate all the overloaded elements automatically. In this case, Congestion Management techniques will be utilized to return the system to the state in which the SPS was designed to automatically relieve the overload. |
| NOTE | Use caution when the tolerance setting is <100% in RTCA. If the post-contingency loading on an element monitored by an SPS is above the tolerance threshold, but below the activation point of the SPS (100%), the contingency associated with the SPS will show in the Transmission Constraint Manager (TCM) display. When this occurs, the result will be a light blue highlighted background identifying the device ID on the TCM display. In this scenario, congestion management is not needed until the criteria in Desktop Guide Transmission Desk Section 2.7, is met. |
| Monitor | Each SPS will be displayed on the “Real Time Values” spreadsheet, as the SPS activation threshold increases the display changes color as follows: - Greater than 80% but less than 90% turns Orange - Greater than 90% turns Red |
| 1 | Typically SPSs are to solve post-contingency overloads on the Transmission System. IF: - The Transmission system topology has temporarily changed due to outages (planned or forced) that affects an SPS; THEN: - Utilize congestion management techniques to prevent any known SPS from operating in a pre-contingent state. |
| 2 | IF: - RTCA indicates a post-contingency overload(s) on a contingency in which the SPS will not mitigate all the overloaded elements automatically; Example: (Light blue or Salmon highlighted background and above 100% loading) THEN: - As system conditions warrant, activate congestion management techniques to relieve the overload. |
| 3 | IF: - No reliability issues will arise as a result of a SPS’s operation; THEN: - At the Operator’s discretion, allow the SPS to perform its function. |
| 4 | IF: - An SPS operates; THEN: - Notify affected TO to reset SPS as system conditions warrant |
| SPS Posting | All SPSs are considered in-service unless otherwise notified by the TO. IF: - An SPS is taken out of service and/or removed from RTCA; THEN: - Post the information on MIS Public WHEN: - The SPS is placed back in service, THEN: - Cancel the message. Typical MIS Posting: The [name] SPS has been [taken out of service/removed from RTCA]. |
| Status Change | If notified that an SPS has changed status (taken out or placed in service): - Send e-mail for notification and have RTCA updated, - “OPS Support Engineering” - “1 ERCOT System Operators” - “DAMTeam” |
| Basecase continuous SPS Triggering | Continual triggering of a SPS during Basecase operations should be managed utilizing manual constraints created in TCM (only applies to manual reset of SPS controls causing a reliability issue). IF: - An SPS is continually triggered during Basecase operations; THEN: - Verify that an associated manual constraint exists for this SPS in TCM, and activate the manual constraint in SCED. IF: - A manual constraint does not exist for this SPS in TCM; THEN: - Coordinate with the Operations Support Engineer to build a manual constraint for the SPS action in TCM. |
| LOG | Log all actions. |
| ### Remedial Action Plan (RAP) |  |
| 1 | IF: - A RAP exists for the contingency; THEN: - Confirm that the relevant RAP is properly modeled, - Review the RAP with the associated TO, - Notify the Shift Supervisor of the anticipated actions. |
| 2 | IF: - A RAP is used to alleviate the identified problem regardless of the contingency listed on the RAP; THEN: - Make log entry. |
| 3 | IF: - A RAP exists for the contingency AND does not solve the contingency OR the pre-RAP overload exceeds the 15 MN rating; THEN: - RTCA does not pass the 15MN (15 minute) rating to TCM, only the EMGY (2-hour emergency) rating. To properly constrain for RAP-associated elements, the % Rating column in TCM may need to be increased so that the constraint limit matches the 15MN value. - Increase the value in the % Rating column in TCM to loosen the constraint (maximum 100% of 15MN value). |
| 4 | IF: - RTCA indicates a post-contingency overload(s) on a contingency in which the RAP will not mitigate all the overloaded elements automatically; Example: (Light blue or Yellow highlighted background and above 100% loading) THEN: - Activate constraint if a 2% shift factor exists. |
| 5 | IF: - The contingency anticipated by the RAP takes place; THEN: - Instruct the implementation of the RAP, - Respond to requests made by the TO in accordance with the RAP, - If necessary, continue to use additional congestion management methods, - When the contingency clears, notify the TO as soon as possible. |
| LOG | Log all actions. |
| ### Pre-Contingency Action Plan (PCAP) |  |
| CAUTION | Pre-Contingency Action Plans (PCAPs) are designed to be enacted before the contingency occurs. |
| 1 | WHEN: - RTCA shows a post-contingency overload and a PCAP exists to resolve it; THEN: - Review the PCAP with the associated Transmission Operator, - Notify the Shift Supervisor of the anticipated actions, - Instruct the execution of the PCAP with the associated Transmission Operator. Typical Script to appropriate TO: “This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is giving an Operating Instruction [TO] to implement the ****PCAP and [open/close] [breaker(s)]. [TO] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| NOTE | If necessary, use congestion management methods for post contingency loading after initiating the PCAP. |
| 2 | IF: - Any PCAPs are still in use (reviewed each day between 0000 and 0500), AND - It is determined, in concurrence with the Shift Supervisor that it is no longer needed; THEN: - Instruct the associated Transmission Operator to return the system to: - Its normal status, OR - Its status prior to implementation of the PCAP. |
| 3 | IF: - A PCAP is used to alleviate the identified problem regardless of the contingency listed on the PCAP; THEN: - Make log entry. |
| LOG | Log all actions. |
| ### Mitigation Plan (MP) |  |
| NOTE | Mitigation Plans (MPs) are pre-determined actions to be taken associated with the occurrence of a specific contingency event if congestion management methods cannot resolve the post-contingency overload. MPs are designed to be enacted POST-Contingency. They are NOT pre-emptive congestion management actions. - A MP is developed when SCED cannot fully resolve the constraint, OR - A MP is developed when there are no generator shift factors greater than or equal to 2% as indicated in EMS, - If a MP is used to alleviate the identified problem regardless of the contingency listed on the MP, make a log entry. |
| SCED unable to fully resolve constraint | IF: - SCED is unable to resolve a constraint; THEN: - Keep constraint active in SCED, - Verify a MP or TOAP exists for the contingency, and review the MP or TOAP with the associated TO IF: - No MP or TOAP exists for the constraint; THEN: - Keep constraint active in SCED, - Coordinate with Operations Support Engineer to develop a MP - If constraint exists due to an outage, a TOAP should be developed (see TOAP procedure), - Issue a Transmission Watch if the MP or TOAP has not been developed within 30 minutes and the constraint remains violated in SCED. |
| < 2% Absolute Shift Factors | IF: - A constraint exists for which there are no generator shift factors greater than or equal to 2% as indicated in EMS; THEN: - DO NOT activate the constraint in SCED - Verify a MP or TOAP exists for the contingency, and review the MP or TOAP with the associated TO IF: - No MP or TOAP exists for the constraint; THEN: - Coordinate with the Operations Support Engineer to develop MP - If contingency exists due to an outage, a TOAP should be developed (see TOAP procedure) - Issue a Transmission Watch if the MP or TOAP has not been developed within 30 minutes. |
| TO Issue | IF: - Notified by a TO that it will take more time to implement the MP than is identified on the MP; THEN: - Notify the Operations Support Engineer to restudy and modify MP, - Log actions taken |
| Issue Watch | When issuing a Transmission Watch for an unsolved post-contingency overload (and waiting on MP or TOAP to be developed: - Make Hotline call to TOs - Instruct Real-Time Operator to call QSEs - Post message on MIS Public T#34 - Typical Hotline Script for Transmission Watch for Post-Contingency Overload Typical MIS Posting Script: At [xx:xx] a Transmission Watch was issued due to the post-contingency overload of [constraint name], a [mitigation plan/temporary outage action plan] is being developed. |
| Cancel Watch | When the MP or TOAP has been developed, cancel the Watch: - Make Hotline call to TOs - Instruct Real-Time Operator to call QSEs - Cancel message on MIS Public T#35 - Typical Hotline Script to Cancel Transmission Watch for Post-Contingency Overload |
| Contingency Occurs | IF: - The anticipated contingency takes place; THEN: - Instruct (if necessary) the implementation of the MP or TOAP to the associated TO, - Respond as quickly as possible to requests made by the TO in accordance with the MP, - If necessary, continue to use congestion management methods for post-contingency loading after initiating the MP. |
| LOG | Log all actions. |
| ### Temporary Outage Action Plan (TOAP) |  |
| NOTE | TOAPs are temporary since they are outage related - A TOAP is developed when there is no generation shift factors greater than or equal to 2% as indicated in EMS, OR - A TOAP is developed when SCED cannot fully resolve the constraint |
| Planned Outage | IF: - A post-contingency overload is due to a planned outage on a transmission line(s) or a transmission facility; THEN: - Locate the TOAP in the Outage Notes, - Follow the same process as a MP outlined above. |
| Forced Outage | IF: - A post-contingency overload is due to a forced outage or planned outage not recognized by Outage Coordination on a transmission line(s) or a transmission facility; THEN: - Follow the same process as a MP outlined above. |
| LOG | Log all actions. |

## 6.1	Voltage Control

Procedure Purpose:  Ensure adequate voltage levels are maintained throughout the ERCOT grid to prevent a potential voltage collapse.

| Protocol Reference | 3.15.1(3) | 6.5.1.1 | 6.5.7.1.10(3)(h) | 6.5.7.7(2) |
| --- | --- | --- | --- | --- |
| Guide Reference | 2.2.5(1) | 2.2.6(2) | 2.7.2 | 2.7.3 |
|  | 2.7.4 |  |  |  |
| NERC Standand | EOP-001-2.1b R2.2 | IRO-002-2 R7 | IRO-003-2 R1 | IRO-005-3.1a R1.1-R1.4, R1.7 |
|  | NUC-001-3 R4.2, R9.2 | TOP-002-2.1b R8 | TOP-003-1 R2 | TOP-004-2 R1, R3, R6 |
|  | TOP-006-2 R2 | TOP-008-1 R1, R2 | VAR-001-4.1 R2, R3 |  |

| Version: 1 | Revision: 27 | Effective Date: June 30, 2016 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | The intent of this procedure is to verify and take corrective action for voltage issues. Although the steps within the procedure are numbered, the numbering is for indexing purposes and are not sequential in nature. The system operator will determine the sequence of steps, or any additional actions required to prevent voltage collapse. |
| NOTE | ERCOT posts the "Seasonal Voltage Profiles" desired voltage for each generation interconnection. The current profiles for generators may be found in the ERCOT Market Information System (MIS) Secure site. Select: Grid> Transmission>Voltage and Dynamic Ratings>Voltage Profiles Select “Voltage Profiles” Open the current file>Open the xls file. |
| NOTE | All Operating Instructions shall be in a clear, concise, and definitive manner. Ensure the recipient of the Operating Instruction repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| ### Assist TOs with Voltage Issues at Nuclear Power Plants |  |
| NOTE | ERCOT and TOs shall maintain the switchyard voltage at each operating nuclear power plant at a nominal value that does not violate its licensing basis with the Nuclear Regulatory Commission. |
| Comanche Peak Voltage Table | For Comanche Peak: - System; - 345 kV; - 138kV. - Nominal Voltage; - 352 kV; - 141 kV. - Tolerance; - +2.56% or -3.40%; - +2.13% or -4.26%. - Maximum Voltage; - 361 kV; - 144 kV. - Minimum Voltage; - 340 kV; - 135 kV. Decordova and Wolf Hollow are points at which generation voltage adjustments can be expected to impact control of Comanche Peak voltage. |
| STP Voltage Table | For South Texas Project: - Plant Configuration; - Maximum kV; - Minimum kV. - Normal line up, through 12/31/2016; - 362.25; - 340. - Alternate line up, through 12/31/2016; - 362.25; - 347. - Alternate without Unit Auxiliary Transformer, through 12/31/2016; - 362.25; - 355. - All line ups, after 12/31/2016; - 362.25; - 331. The STP Switchyard Facilities’ steady state voltage, with both STP units off-line, should be maintained within the ranges above. Calaveras (Spruce), Braunig (Von Rosenberg), DOW, and WAP are points at which generation voltage adjustments can be expected to impact control of STP voltage. Note: It is the STP QSEs responsibility to notify ERCOT when STP is in an alternate line up. |
| 1 | IF: - Voltage levels exceed the maximum or minimum levels as stated above in the voltage tables; THEN: - Notify the appropriate Nuclear Plant’s QSE - Give an explanation of the event, if known and an estimate of when voltage is excepted to return to normal - Coordinate the appropriate voltage control action with the corresponding TO and QSE. |
| 2 | WHEN: - Voltage is back to normal range; THEN: - Notify the appropriate Nuclear Plant QSE. |
| ### Real-Time Voltage Issues |  |
| NOTE | - Post-Contingency low voltage alarms beyond the emergency operating low voltage limit could trigger Automatic Under-Voltage Load Shedding if the contingency were to occur. Detailed information on the amount of load on Automatic Under-Voltage Load Shedding Schemes (UVLS) can be found in Desktop Guide Transmission Section 2.9. - Generation Resources required to provide VSS may not reduce high reactive loading on individual units during abnormal conditions without the consent of ERCOT unless equipment damage is imminent. - Major transmission lines shall be kept in service during Light Load as much as possible. Lines should only be removed after all applicable reactive controls are implemented and studies are performed showing that reliability will not be degraded. |
| NOTE | ERCOT Nominal Voltage Levels are 345kV, 138kV, and 69kV. The general voltage guidelines are as follows (listed in kV): Nominal Voltage; Normal Operating Limits; Emergency Operating Limits; Ideal Voltage Range. 345; 327.75 – 362.25; 310.5 – 379.5; 345 – 359. 138; 131.1 – 144.9; 124.2 – 151.8; 138 – 144. 69; 65.55 – 72.45; 62.1 – 75.9; 69 – 71.5. Some TOs utilize different Normal (Basecase) and Emergency (Post-Contingency) voltage operating limits than the general voltage guidelines. These limits can be seen under the Network Limits display. |
| 1 | Monitor the voltage contingency violations and Basecase voltage violation displays in RTCA WHEN: - Indicated by SCADA alarms, RTCA or by a TO of voltage concerns; THEN: - Determine if the SCADA is of similar magnitude to the pre-contingency value. - Example: Review nearby kV measurements - Review “Voltage Tracking Issues Spreadsheet” on SharePoint to ensure the Basecase/contingency is not listed - If listed, no further action needed. IF: - Inaccurate; THEN: - Notify the Shift Supervisor and Operations Support Engineer to investigate. - Log in “Voltage Tracking Issues” on SharePoint - Make log entry. |
| 2 | IF: - Accurate; THEN: - Discuss the voltage concern with the appropriate TO - Has the TO utilized all static reactive power resources? (capacitors, reactors, change transformer taps) Typical Script to appropriate TO: “This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is instructing [TO] to [Raise/Lower] voltage at [specify bus] by [Closing/Opening/Adjusting] [Cap/Reactor/Transformer Tap] to resolve a [Basecase Voltage Violation/RTCA Voltage Contingency Violation]. [TO] please repeat this instruction back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. IF: - Additional reactive support or coordination is needed to clear the violation; THEN: - Discuss with the appropriate TO and come to an agreement as to the proper action. This could be transmission switching, adjusting voltage at a nearby Generation Resource, bringing on an additional Resource, returning a planned outage, or development of an CMP IF: - The TO needs assistance from ERCOT to get voltage adjusted at a Resource; THEN: - Instruct the appropriate QSE to raise or lower bus voltage, - The QSE should complete the requested in no more than five minutes. Typical Script to appropriate QSE: “This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is instructing [QSE] to [raise or lower] voltage at [specify bus] by [+1 or 2kV or -1 or 2kV] for a target of [target kV]. [QSE] please repeat this instruction back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| LOG | Log all actions. |
| ### Future Voltage Issues |  |
|  | WHEN: - Notified by the RUC Operator of future voltage violations; THEN: - Review the “Voltage Tracking Issues” on SharePoint. If it is reoccurring, the solution may be listed on the “Resolutions” tab IF: - Any capacitors or reactors are AVAILABLE that can address the violation; THEN: - Ensure the capacitor or reactor clears the violation IF: - Additional reactive support or coordination is needed to address the violation; THEN: - Discuss the identified future voltage violations with the appropriate TO and come to an agreement as to the proper action. This could be transmission switching, development of a CMP, making reactive devices available, or commitment of additional generation IF: - An Off-Line Resource is needed to resolve the voltage violation; THEN: - Instruct RUC Operator to commit the Resource |
| LOG | Log all actions. |
| ### ERCOT requesting Resource to operate beyond URL |  |
| Exceeding URL or Reducing Output | A Generation Resource providing VSS may not be requested to reduce MW output so as to provide additional MVAr, nor may they be requested to operate on a voltage schedule outside the URL specified by the QSE without a Dispatch Instruction. IF: - A QSE communicates that an ERCOT or TO voltage instruction requires the Generation Resource to exceed its Unit Reactive Limit (URL) or the Resource has to reduce MW; THEN: - Request the QSE to follow the instruction and inform them that Operations Analysis will make the verification and either an electronic Dispatch Instruction for settlements will be issued or a call with an explanation will be followed up on the next business day - Send e-mail to Operations Analysis and shiftsupv with the following information: - Resource name - Specific voltage set point. - Start time - End time |
| QSE Performance | Maintain a log of QSEs acknowledgements of Dispatch Instructions concerning scheduled voltage or scheduled Reactive output requests. QSEs responding in less than two minutes from the time of issuance shall be deemed satisfactory. |
| ### Voltage Security Assessment Tool (VSAT) |  |
| NOTE | VSAT and RUC perform full AC analysis of all contingencies. |
| 1 | IF: - Any of the monitored VSAT scenario results approaches the Reliability margins listed in the table below; THEN: - Manually rerun the entire sequence of RTNET, RTCA, and RTDCP (VSA) - Confirm VSAT indicates either “Normal” or “Pending” Reliability Margin Table. Scenario Name; Margin. LAREDO; 25MW. N-H_G; 200MW. N-H_L; 200MW. O-DFW_L; 200MW. PNHNDL; 50MW. O-VAL_L; 100MW. For N-H_G and N_H_L: Refer to section 4.4 North-Houston Voltage Stability Limit of this procedure. |
| 2 | IF: - VSAT indicates that a Reliability Margin may be exceeded; THEN: - Determine if the current Reliability Margin pre-contingency value is less than the Margin on the table in the previous step. - If no, no further action is required. - If yes, go to Step 3. |
| 3 | Determine the contingency status in RTCA (solved/unsolved). IF: - Solved, - Have Operations Support Engineer verify if the problem is real, - If real, request information on weak bus, - Request the TO in the affected area turn on capacitor banks and turn off reactors near the weak busses. - If not real, no further action is required. - Unsolved, - Notify Shift Supervisor and Operations Support Engineer - Manually dispatch fast ramp generators to increase generation in weak bus area. - If all online units are at maximum capacity - Instruct RUC Operator to commit additional resources in the weak bus area that are available. |
| 4 | WHEN: - Capacitor banks are placed in service; THEN: - Rerun VSAT with new topology. |
| 5 | Determine if the current Reliability Margin pre-contingency value is greater than the Margin Value from the table above. IF: - The current Reliability Margin pre-contingency value is greater than the Margin; THEN: - No further action is required. OR IF: - The current Reliability Margin pre-contingency value is less than the Margin; THEN: - Determine if there are more units available in the affected area, AND - Repeat the process starting with Step 3. If no additional generation is available, continue. |
| 6 | IF: - No additional generation is available; THEN: - Notify Operations Support Engineer to create a Mitigation Plan. |
| ### Power System Stabilizers (PSS) & Automatic Voltage Regulators (AVR) |  |
| NOTE | Each QSE’s Generation Resource providing VSS shall operate with the unit’s Automatic Voltage Regulator (AVR) in the voltage control mode unless specifically instructed to operate in manual mode by ERCOT. |
| NOTE | Operations Support will keep a spreadsheet with the current status of each PSS and AVR. This data can be viewed at ERCOT Realtime Drive >_Operations Official Spreadsheets > RAS_AVR_PSS_Spreadsheet |
| 1 | WHEN: - Notified by a QSE of a PSS or AVR in manual or in Power Factor Mode; THEN: - Instruct the QSE to manually adjust VAR output as required to maintain voltage set-point until the AVR is back in service, NOTIFY: - The appropriate TO of the status, if not already done so by QSE, - Enter the status change information into the ERCOT Logs, - Log type of either “PSS” or “AVR”. - Include the company name, the name of the person spoken with, and reason (if device is being placed in or taken out of service). - Include that the TO has been notified of change in status - Copy and paste the log entry into an e-mail and send to - “Operations Analysis” - “OPS Support Engineering” - “OPS Advanced Network Applications” - “1 ERCOT System Operators” |
| 2 | WHEN: - Notified by a QSE that the PSS or AVR is in Auto and back in service; NOTIFY: - The appropriate TO of the status, if not already done so by QSE, - Enter the status change information into the ERCOT Logs, - Log type of either “PSS” or “AVR”. - Include the company name, the name of the person spoken with, and reason (if device is being placed in or taken out of service). - Include that the TO has been notified of change in status - Copy and paste the log entry into an e-mail and send to - “Operations Analysis” - “OPS Support Engineering” - “OPS Advanced Network Applications” - “1 ERCOT System Operators” |

## 7.1	Market Notices

Procedure Purpose: Guidelines for issuing Emergency Conditions and the four possible levels: Operating Condition Notices (OCN), Advisories, Watches, and Emergency Notices.

| Protocol Reference | 6.3.3 | 6.5.9.3 | 6.5.9.3.1 | 6.5.9.3.2 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.3.3 | 6.5.9.3.4 |  |  |
| Guide Reference | 4.2.1 | 4.2.2 | 4.2.3 | 4.2.4 |
| NERC Standard | EOP-001-2.1b R3.1 | IRO-005-3.1a R4, R12 |  |  |

| Version: 1 | Revision: 25 | Effective Date: June 30, 2016 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### OCN |  |
| NOTE | Consider the severity of the potential Emergency Condition. The severity of the Emergency Condition could be limited to an isolated local area, or the condition might cover large areas affecting several entities, or the condition might be an ERCOT-wide condition potentially affecting the entire ERCOT System. |
| 1 | As instructed by the Shift Supervisor or when appropriate, issue an Operating Condition Notice (OCN). The OCN can be issued for any of the following reasons or to obtain additional information from Market Participants. - There is a projected reserve capacity shortage that could affect reliability and may require more Resources - When extreme cold weather is forecasted approximately 5 days away - When extreme hot weather is forecasted approximately 5 days away - When an approaching Hurricane / Tropical Storm is approximately 5 days away - Unplanned transmission Outages that may impact reliability - When adverse weather conditions are expected, ERCOT may confer with TOs and QSEs regarding the potential for adverse reliability impacts and contingency preparedness |
| ### Advisory |  |
| 1 | As instructed by the Shift Supervisor or when appropriate, issue an Advisory. The Advisory can be issued for any of the following reasons or to obtain additional information from Market Participants. - When an approaching Hurricane / Tropical Storm is approximately 3 days away - When extreme cold weather is forecasted approximately 3 days away - When extreme hot weather is forecasted approximately 1 to 3 days away - When conditions are developing or have changed and more Ancillary Services will be needed to maintain current or near-term reliability - ERCOT may exercise its authority to increase Ancillary Service requirements above the quantities originally specified in the Day-Ahead Market in accordance with ERCOT procedures - When extreme weather or conditions require more lead-time than the normal Day-Ahead Market allows - Transmission system conditions are such that operations within security criteria are not likely or possible due to Forced Outages or other conditions unless a CMP exists - Loss of communications or control condition is anticipated or significantly limited - ERCOT may require information from QSEs representing Resources regarding the Resources’ fuel capabilities. Requests for this type of information shall be for a time period of no more than seven days from the date of the request |
| ### Watch |  |
| 1 | As instructed by the Shift Supervisor or when appropriate, issue a Watch. The Watch can be issued for any of the following reasons or to obtain additional information from Market Participants. - A projected reserve capacity shortage is projected with no market solution available that could affect reliability. - When an approaching Hurricane / Tropical Storm is approximately 1 day away - When extreme cold weather is projected for next day or current day. - When extreme hot weather is projected for next day or current day - Conditions have developed such that additional Ancillary Services are needed in the Operating Period - Insufficient Ancillary Services or Energy Offers in the DAM - Market-based congestion management techniques embedded in SCED will not be adequate to resolve transmission security violations - Forced Outages or other abnormal operating conditions have occurred, or may occur that would require ERCOT to operate with active violations of security criteria as defined in the Operating Guides unless a CMP exists - ERCOT varies from timing requirements or omits one or more Day-Ahead or Adjustment Period and Real-Time procedures. - ERCOT varies from timing requirements or omits one or more scheduling procedures in the Real-Time process. - The SCED process fails to reach a solution, whether or not ERCOT is using one of the measures in Failure of the SCED Process. - The need to immediately procure Ancillary Services from existing offers - ERCOT may instruct TOs to reconfigure transmission elements as necessary to improve the reliability of the system - ERCOT may require information from QSEs representing Resources regarding the Resources’ fuel capabilities. Requests for this type of information shall be for a time period of no more than seven days from the date of the request |
| ### Emergency Notice |  |
| 1 | As instructed by the Shift Supervisor or when appropriate, issue an Emergency Notice. The Emergency Notice can be issued for any of the following reasons or to obtain additional information from Market Participants. - Loss of Primary Control Center Functionality - Load Resource deployment for North-Houston voltage stability - ERCOT cannot maintain minimum reliability standards (for reasons including fuel shortages) during the Operating Period using every Resource practically obtainable from the market - Immediate action cannot be taken to avoid or relieve a Transmission Element operating above its Emergency Rating - ERCOT forecasts an inability to meet applicable Reliability Standards and it has exercised all other reasonable options - A transmission condition has been identified that requires emergency energy from any of the DC-Ties or curtailment of schedules - The Transmission Grid is such that a violation of security criteria as defined in the Operating Guides presents the threat of uncontrolled separation or cascading outages, large-scale service disruption to load (other than Load being served from a radial transmission line) and/or overload of Transmission Elements, and no timely solution is obtainable through SCED or CMPs - When extreme cold weather is beginning to have an adverse impact on the System - When extreme hot weather is beginning to have an adverse impact of the System - When Hurricane / Tropical Storm is in the ERCOT Region and is beginning to have an adverse impact on the System |
| ### Operating Condition Scripts |  |
| Hotline | Communications must specify the severity of the situation, the area affected, the areas potentially affected, and the anticipated duration of the Emergency Condition. T#37 –Typical Hotline Script for Operating Condition [OCN/Advisory/Watch/Emergency] |
| Post | All notices must be posted on the MIS Public using Notice Builder. - For “free form” messages, the “Notice priority” will be specified as follows: - Operational Information/OCN type messages – low priority - Advisory/Watch type messages – medium priority - Emergency type messages – high priority |
| Hotline Cancellation | T#38 – Typical Hotline Script to Cancel Operating Condition [OCN/Advisory/Watch/Emergency] |
| Log | Log all actions. |
| ### Specific Scripts for QSE’s |  |
| NOTE | At times, the Real-Time, Resource or RUC operator takes the lead on the issuance of Hotline calls for specific procedures they have. The following scripts are to help guide you when specific procedures don’t exist for the T/S operator. |
| 30% Probability Of Down Ramp | T#39 - Typical Hotline Script for OCN for Forecasted Probability of a Large Down Ramp T#40 - Typical Hotline Script to Cancel OCN for Forecasted Probability of a Large Down Ramp |
| NOTE | Up ramps should be self-mitigating since a majority of the wind generators have governor response capabilities. |
| SCED Or RLC Failure | Note: RLC can fail independently of AGC; this same script will also be used for a RLC failure. If RLC is failed, SCED will have invalid results. T#41 - Typical Hotline Script for Watch for SCED/RLC Failure T#42 - Typical Hotline Script to Cancel Watch for SCED/RLC Failure |
| EMMS (LFC and RLC/SCED) Failure | T#43 - Typical Hotline Script for Emergency Notice for LFC and SCED Failure T#44 - Typical Hotline Script to Cancel Emergency Notice for LFC Functioning, SCED valid |
| Increasing Amount of Ancillary Services | T#45 - Typical Hotline Script for Watch to Increase Ancillary Services and Open SASM T#46 - Typical Hotline Script to Cancel Watch to Increase Ancillary Services |
| A/S Insufficiency Offers in DAM | T#47 - Typical Hotline Script for Watch for Insufficient AS Offers in DAM T#48 - Typical Hotline Script to Cancel Watch for Insufficient A/S Offers in DAM |
| A/S Insufficiency from DAM | T#49 - Typical Hotline Script for A/S insufficiency in DAM T#50 - Typical Hotline Script Cancellation |
| REG/ RRS - RUC Committed Shortages | T#51 - Typical Hotline Script for Watch for Insufficient A/S Offers T#52 - Typical Hotline Script to Cancel Watch for Insufficient A/S Offers |
| DAM Timeline Deviation | T#53 - Typical Hotline Script for Advisory for DAM Timeline Deviation T#54 - Typical Hotline Script to Cancel Advisory for DAM Timeline Deviation |
| DAM Failure | T#55 - Typical Hotline Script for Watch for DAM Failure T#56 - Typical Hotline Script to Cancel Watch for DAM Failure |
| DRUC Delay or Timeline Deviation | 57 - Typical Hotline Script for Advisory for DRUC Timeline Deviation T#58 - Typical Hotline Script to Cancel Advisory for DRUC Timeline Deviation |
| DRUC Timeline not Met | T#59 - Typical Hotline Script for Watch for DRUC not completing by 18:00 T#60 - Typical Hotline Script to Cancel Watch for DRUC not completing by 18:00 |
| HRUC Failure or Timeline Deviation | T#61 - Typical Hotline Script for Advisory for HRUC Failure / Timeline Deviation T#62 - Typical Hotline Script to Cancel Advisory for HRUC Failure/Timeline/Deviation |
| DRUC Committed For Capacity Shortage | T#63 - Typical Hotline Script for OCN for Projected Reserve Capacity Shortage T#64 - Typical Hotline Script to Cancel OCN for Projected Reserve Capacity Shortage |
| Excess Generation | T#65 - Typical Hotline Script for OCN for Projected Excess Reserve Capacity T#66 - Typical Hotline Script to Cancel OCN for Projected Excess Reserve Capacity |
| Projected Reserve Capacity Shortage with no market solution | T#67 - Typical Hotline Script for Watch for Projected Reserve Capacity Shortage with No Market Solution T#68 - Typical Hotline Script to Cancel Watch for Projected Reserve Capacity Shortage with No Market Solution |
| RMR Projected Reserve Capacity Shortage | T#69 - Typical Hotline Script for Watch for Projected Reserve Capacity Shortage with No Market Solution, RMR recommended T#70 - Typical Hotline Script to Cancel Watch for Projected Reserve Capacity Shortage with No Market Solution, RMR recommended |
| Execute a SASM | T#86 - Typical Hotline Script to Execute a SASM for Failure to Provide/Infeasibility |
| BAAL Firm Load Shed | T#87 BAAL Firm Load Shed: T#10 EEA3/BAAL Restore All Firm Load: |

## 7.4	Restore EEA Levels

Procedure Purpose:  To restore the ERCOT grid to normal state as system conditions warrant while recovering from an EEA event.

| Protocol Reference | 6.5.9.4.1(e) | 6.5.9.4(3)(g) | 6.5.9.4.3 |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.5.3.5 |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 18 | Effective Date: June 30, 2016 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Restore Firm Load |  |
| RESERVES | 1375 MW of PRC must be restored within 90 minutes. |
| 1 | IF: - Sufficient Regulation Service exist to control to 60 Hz, AND - PRC – Regulation Up Responsibility is ≥ 1375 MW for the last 15 minutes; THEN: - Using the Hotline, notify all TOs of firm load restoration. T#9 - Typical Hotline Script EEA3 Restore a Portion of the Firm Load OR T#10 - Typical Hotline Script EEA3/BAAL Restore All Firm Load |
| LOG | Log all actions. |
| ### Move from EEA Level 3 to EEA Level 2 |  |
| 1 | IF: - Sufficient Regulation Service exist to control to 60 Hz, AND - PRC is ≥ 1750 MW, AND - All firm load has been instructed to be restored; THEN: - Using the Hotline, notify all TOs of the reduction from EEA 3 to EEA 2: - Notify the TOs that Load Resources are being restored T#11 - Typical Hotline Script to move from EEA3 to EEA2 |
| LOG | Log all actions. |
| ### Move from EEA Level 2 to EEA Level 1 |  |
| 1 | IF: - The System can maintain PRC ≥ 2300 MW AND - All Load Resources have been instructed to be restored; THEN: - Using the Hotline, notify all TOs of the reduction from EEA 2 to EEA 1 and ERS Resources have been instructed to restore, - If distribution voltage reduction measures were used, restore - If BLTs were implemented, restore - *If Load Management Programs were deployed, restore T#12 - Typical Hotline Script to move from EEA2 to EEA1 |
| ### Move from EEA Level 1 to EEA 0 |  |
| 1 | IF: - The System can maintain PRC ≥ 2300 MW, AND - All uncommitted units secured in EEA 1 can be released, AND - Emergency energy from the DC Ties is no longer needed; THEN: - Using the hotline, notify all TOs of the termination of EEA. T#13 - Typical Hotline Script Terminate EEA1 |
| ### Cancel Watch |  |
| 1 | WHEN: - Requested by the Real-Time Operator; THEN: - Cancel Watch T#14 - Typical Hotline Script to cancel Watch for PRC <2500 MW |

## 7.5	Block Load Transfer

Procedure Purpose:  To transfer loads, located in ERCOT to a Non-ERCOT system or from a Non-ERCOT system to ERCOT during emergency conditions.

| Protocol Reference | 6.5.9.5 | 6.5.9.5.1 | 6.5.9.5.2 |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.4 |  |  |  |
| NERC Standard | TOP-001-1a R2, R6 |  |  |  |

| Version: 1 | Revision: 12 | Effective Date: June 30, 2016 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - Restoration of service to outage customers using BLT’s will be accomplished as quickly as possible if the transfers will not jeopardize the reliability of the ERCOT Interconnection. - BLTs that are comprised of looped systems may be tied to the non-ERCOT Control Area’s electrical system(s) through multiple interconnection points at the same time. Transfers of looped configurations are permitted only if all interconnection points are registered and netted under a single Electric Service Identifier (ESI ID) and represented by a single TSP or DSP or netted behind Non-Opt-in Entity (NOIE) metering points. |
| ### ERCOT picks up Load for Non-ERCOT System |  |
| 1 | IF: - ERCOT is requested to pick up load for CFE, MISO or SPP; THEN: - Consult with Operations Support Engineer to ensure the load pick up will not create a reliability concern, IF: - No reliability concern exists THEN: - Grant the approval |
| Electronic Dispatch Instruction Confirmation | IF: - The BLT is registered (refer to Desktop Guide Common to Multiple Desks Section 2.5): - Issue electronic Dispatch Instruction confirmation to the QSE listed - Determine the amount of load being transferred into ERCOT - Choose QSE level tab - Choose [Proper QSE from Desktop Guide] for Participant Name - Choose “OTHER For QSE” for Instruction Type - In text, state “BLT - ERCOT picks up load from [SPP, MISO or CFE]” When issuing a VDI or the confirmation, ensure the use of three-part communication: - Issue the Operating Instruction - Receive a correct repeat back - Give an acknowledgement |
| E-mail | SEND: - E-mail to the “BLT” distribution list INCLUDE: - The following information: - TO area - Was BLT registered or not - Was an electronic Dispatch Instruction confirmation sent - Was BLT modeled |
| 2 | For BLTs that are done in an emergency situation and are not modeled in the Network Operations Model, the responsible TO will notify ERCOT as soon as practicable after the event. |
| 3 | IF: - Congestion issues arise from switching variations due to the BLT; THEN: - Employ congestion management procedures, IF: - Congestion management cannot maintain the reliability of the system, THEN: - Terminate the BLT. |
| ### Non-ERCOT System picks up Load for ERCOT |  |
| 1 | IF: - CFE, MISO or SPP picks up load for ERCOT; THEN: - Ensure the RC in the other grid has given approval for the load to be transferred to them |
| Electronic Dispatch Instruction Confirmation | IF: - The BLT is registered (refer to Desktop Guide Common to Multiple Desks Section 2.5): - Issue electronic Dispatch Instruction confirmation to the QSE listed - Determine the amount of load being transferred out of ERCOT - Choose QSE level tab - Choose [Proper QSE from Desktop Guide] for Participant Name - Choose “OTHER For QSE” for Instruction Type - In text, state “BLT – [SPP, MISO or CFE] picks up load for ERCOT” When issuing a VDI or the confirmation, ensure the use of three-part communication: - Issue the Operating Instruction - Receive a correct repeat back - Give an acknowledgement |
| E-mail | SEND: - E-mail to the “BLT” distribution list INCLUDE: - The following information: - TO area - Was BLT registered or not - Was an electronic Dispatch Instruction confirmation sent - Was BLT modeled |
| 2 | For BLTs that are done in an emergency and are not modeled in the Network Operations Model, the responsible TO will notify ERCOT as soon as practicable after the event. |
| 3 | IF: - Congestion management issues that arise from switching variations due to the BLT; THEN: - Employ congestion management procedures, IF: - Congestion management cannot maintain the reliability of the System, THEN: - Terminate the BLT. |
| NOTE | If the Alamito Creek (ALMC) to Presidio (PRES) 69 kV transmission line trips, CFE will automatically pick up approximately 2 MW of load on the Presidio/Gonzales BLT. When AEP TO has informed you that this happened, follow step 1 above. |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Frosch, Hartmann, Stone, and Barcalow | Preparers | November 10, 2010 |
| Frosch and Hartmann | Procedure writers and editors | November 29, 2010 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2010 |
| Frosch and Hartmann | Procedure writers and editors | January 4, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 26, 2011 |
| Frosch and Hartmann | Procedure writers and editors | March 23, 2011 |
| Frosch and Hartmann | Procedure writers and editors | April 20, 2011 |
| Frosch and Hartmann | Procedure writers and editors | June 10, 2011 |
| Frosch and Hartmann | Procedure writers and editors | July 18, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 1, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 30, 2011 |
| Frosch and Hartmann | Procedure writers and editors | September 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | October 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 16, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | April 25, 2012 |
| Frosch and Hartmann | Procedure writers and editors | May 30, 2012 |
| Frosch and Hartmann | Procedure writers and editors | July 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | August 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | September 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | October 26, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 26, 2013 |
| Frosch and Hartmann | Procedure writers and editors | May 28, 2013 |
| Frosch, Hartmann & Weldon | Procedure writers and editors | July 8, 2013 |
| Frosch and Hartmann | Procedure writers and editors | August 7, 2013 |
| Frosch and Hartmann | Procedure writers and editors | August 28, 2013 |
| Frosch and Hartmann | Procedure writers and editors | September 25, 2013 |
| Frosch and Hartmann | Procedure writers and editors | December 11, 2013 |
| Frosch, Solis and Hartmann | Procedure writers and editors | December 20, 2013 |
| Frosch and Hartmann | Procedure writers and editors | February 18, 2014 |
| Frosch, Gaddy, and Hartmann | Procedure writers and editors | April 1, 2014 |
| Frosch, Gaddy, Hartmann and Solis | Procedure writers and editors | May 27, 2014 |
| Frosch and Hartmann | Procedure writers and editors | July 27, 2014 |
| Frosch and Hartmann | Procedure writers and editors | September 29, 2014 |
| Frosch, Hartmann, Lopez and Solis | Procedure writers and editors | December 10, 2014 |
| Frosch and Hartmann | Procedure writers and editors | February 25, 2015 |
| Frosch and Hartmann | Procedure writers and editors | March 25, 2015 |
| Frosch and Hartmann | Procedure writers and editors | April 29, 2015 |
| Frosch, Hartmann and Gaddy | Procedure writers and editors | July 13, 2015 |
| Hartmann and Gaddy | Procedure writers and editors | September 4, 2015 |
| Hartmann and Gaddy | Procedure writers and editors | September 25, 2015 |
| Hartmann and Gaddy | Procedure writers and editors | December 22, 2015 |
| Hartmann, Gaddy and Frosch | Procedure writers and editors | January 22, 2016 |
| Hartmann and Gaddy | Procedure writers and editors | February 23, 2016 |
| Hartmann, Gaddy and Frosch | Procedure writers and editors | April 22, 2016 |
| Hartmann, Gaddy and Frosch | Procedure writers and editors | June 24, 2016 |

Manual Change History

| Procedure | Ver/ Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All Sections | 1.0 / 0 | New procedures for all sections for Nodal implementation | November 28, 2010 |
| 3.2 4.1 4.2 4.3 4.4 4.5 4.6 6.1 7.4 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Updated Categories and Priorities In section “Post-Contingency Overloads”, updated step 5 and QSGR, “Managing Binding and Violated Constraints” step 1, “Reaching Shadow Price Cap” step 1, and ” Managing Congestion during SCED Failure” step 1 Updated steps 1 and 2 Updated steps 2 and 3 Updated step ≤200MW In section “Special Protection Systems (SPS) (Identified as RAS in EMS)” changed 3rd Note to “Monitor”, changed “Operation” to step 4, changed “Runback” to step 5 and updated In section “Manual Dispatch Instruction to take a Unit Off-Line” and “Taking One CT of a Combined Cycle Off-line”, Updated step 1 and deleted Manual Dispatch Instruction In section “Voltage Issues”, Updated 1st Note and Exceed URL, deleted 3rd Note and added QSE Performance In section “ERCOT picks up Load for Non-ERCOT System” and “Non-ERCOT System picks up Load for ERCOT”, updated step 1 | December 1, 2010 |
| 4.1 4.2 4.3 5.1 | 1.0 / 2 1.0 / 2 1.0 / 2 1.0 / 1 | Deleted 1st Note, updated step Critical Facilities & 2nd Note, step 1 in Evaluate Real-Time Contingency Analysis Results, steps 3-6, 8 & QSGR in Post-contingency Overload, step 2 in Transmission Issues in the Areas of the CFE Ties, changed title & updated all steps in Managing Binding and Violated Constraints, step 1 in Reaching Shadow Price Cap, all steps in QSE Requests to Decommit a Resource, deleted Deploy/Termination of Non-Spin for Congestion, updated step 1 in Managing Congestion during SCED failure Updated step 1 & 2 Updated step 3 Added Remedial Switching Action section | December 15, 2010 |
| 4.1 4.2 4.3 7.1 | 1.0 / 3 1.0 / 3 1.0 / 3 1.0 / 1 | Updated step 1 in Reaching Shadow Price Cap Updated step 1 & 2 Updated step 2 & 3 and added step 4 & 5 Updated step 1 in Watch and step Hotline in Scripts | January 5, 2011 |
| 2.3 2.4 3.3 4.1 4.3 4.4 4.5 4.6 4.7 6.1 7.1 7.2 7.3 7.5 8.1 8.2 8.3 9.3 | 1.0 / 0 1.0 / 0 1.0 / 1 1.0 / 4 1.0 / 4 1.0 / 2 1.0 / 2 1.0 / 2 1.0 / 1 1.0 / 2 1.0 / 2 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Added “Site failovers and Database Loads” as new procedure Added “Switching Control Center” as new procedure Updated step 5 Updated scripts, step 1 in “Managing Binding and Exceeding Constraints”, “Reaching Shadow Price Cap” and “Managing Congestion during SCED Failure” Updated step 2, 3 & 4 Updated scripts Updated scripts Added “Manual Commit of a Resource” as new procedure Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts Deleted procedure | January 31, 2011 |
| 2.3 4.1 4.6 7.1 7.2 | 1.0 / 1 1.0 / 5 1.0 / 3 1.0 / 3 1.0 / 2 | Updated Site Failovers & added W-N Active step Added Review Planned Outage Notes, Updated all steps in Transmission Issues in the Areas of the CFE DC-Ties and step 1 of SCED not able to Solve Congestion (Reached Max Shadow Price) Added Posting Manual Actions Updated Watch and Emergency Notice Updated step 2 in Implementation of EEA Level 2A | March 25, 2011 |
| 2.3 3.3 4.1 4.3 4.4 4.5 5.1 6.1 7.1 7.3 | 1.0 / 2 1.0 / 2 1.0 / 6 1.0 / 5 1.0 / 3 1.0 / 3 1.0 / 2 1.0 / 3 1.0 / 4 1.0 / 2 | Added steps and updated whole procedure Updated step 8 Updated Review Planned Outage Notes Added 1st Note Updated 1st Note and step VSAT Updated step Status Change in SPS Updated Definition in Remedial Switching Action Updated “PSS & AVR” 2nd note Updated step 1 in Watch and Emergency Notice and step Post Updated “Restore Firm Load” and “Move From EEA Level 3 to EEA Level 2B” step 1 | April 22, 2011 |
| 2.3 3.3 4.1 6.1 7.1 7.2 7.3 7.4 8.1 8.2 8.3 8.4 9.1 | 1.0 / 3 1.0 / 3 1.0 / 7 1.0 / 4 1.0 / 5 1.0 / 3 1.0 / 3 1.0 / 2 1.0 / 2 1.0 / 0 1.0 / 2 1.0 / 2 1.0 / 1 | Added step Site Failover Complete Updated step 2 Updated Critical Facilities and step 5 in Post-Contingency Overloads, changed Managing Binding and Exceeded Constraints procedure to Managing Constraints in SCED & updated procedure, deleted SCED not able to Solve Congestion procedure Updated 2nd Note and step 2 in Voltage Issues Updated all step 1’s Updated all step 1’s and deleted Note in Implement EEA Level 2A Updated all step 1’s Updated all steps Updated all steps Added new procedure Changed section number and updated all steps Changed section name and updated all steps Updated 1st Note and steps 2 & 3 | June 14, 2011 |
| 4.1 4.5 6.1 7.2 7.3 7.4 7.5 7.6 10.1 | 1.0 / 8 1.0 / 4 1.0 / 5 1.0 / 4 1.0 / 4 1.0 / 1 1.0 / 3 1.0 / 2 1.0 / 1 | Updated 2nd note & step Phase Shifters in Transmission Congestion Management, steps 3, 5 & 7 in Post-Contingency Overloads, Moved Transmission Issues in the Areas of the CFE DC Ties to 7.4 Updated 1st note, steps SPS Posting and Status Change in Special Protection Systems (SPS) (Identified as RAS in EMS) and Updated all steps in Mitigation Plan (MP) Updated 2nd note in Power System Stabilizers (PSS) & Automatic Voltage Regulators (AVR) Updated step 1 in Implement EEA Level 1 and 2A Updated step 1 in Move from EEA Level 1 to EEA 0 Moved procedure from section 4.1 Changed section number from 7.4 to 7.5 Changed section number from 7.5 to 7.6 Added Market Participant Backup Control Center Transfer procedure | July 20, 2011 |
| 4.1 4.4 4.6 6.1 8.4 8.5 | 1.0 / 9 1.0 / 4 1.0 / 4 1.0 / 6 1.0 / 0 1.0 / 3 | Updated step 5 in Post-Contingency Overloads and step Log in Managing Constraints in SCED Updated monitor section Updated step 1’s Updated step 2 and deleted For HHGT_G-O in Voltage Security Assessment Tool Added new procedure “Extreme Hot Weather” Changed section number | August 3, 2011 |
| 2.4 4.1 4.3 4.4 7.1 7.2 7.3 8.4 9.2 | 1.0 / 1 1.0 / 10 1.0 / 6 1.0 / 5 1.0 / 6 1.0 / 5 1.0 / 5 1.0 / 1 1.0 / 1 | Updated step Hotline Call Updated step 2 in Managing Constraints in SCED Updated step 2, 4 & 5, added step 3 Added 2nd note Updated step 1 in Watch Updated step 2 in Implement EEA Level 1, steps 1 & 2 in Implement EEA Level 2A Updated the step 1’s Updated temperature from 102 to 103 Updated 4th Note | September 1, 2011 |
| 3.3 4.2 7.2 7.3 7.4 7.5 9.1 | 1.0 / 4 1.0 / 4 1.0 / 6 1.0 / 6 1.0 / 2 1.0 / 4 1.0 / 2 | Updated Note to ensure compliance with IRO-008-1R2 Added 1st Note, added step 5, updated steps 4 & 6 Combined EEA 2 A and B per NPRR 379 Combined EEA 2 A and B per NPRR 379 Updated step 2 in Transmission Issues within CFE Updated step 1 in ERCOT picks up Load for Non-ERCOT System and step 1 in Non-ERCOT System picks up Load for ERCOT Updated step 2 | October 1, 2011 |
| 3.3 4.1 4.3 4.6 9.1 | 1.0 / 5 1.0 / 11 1.0 / 7 1.0 / 5 1.0 / 3 | Updated scripts Updated step 4 in Post Contingency Overloads & step 3 in Managing Constraints in SCED Updated step 3 Added Canceling RUC Commitments Added 3rd Note | November 1, 2011 |
| 2.3 3.1 4.1 4.4 4.5 4.6 6.1 7.1 8.1 8.3 | 1.0 / 4 1.0 / 1 1.0 / 12 1.0 / 6 1.0 / 5 1.0 / 6 1.0 / 7 1.0 / 7 1.0 / 3 1.0 / 3 | Updated step “Site Failover” Updated step “Review” Updated step 4 in Post-Contingency Overloads & added new procedure Post-Contingency Overloads on PUNs Updated 1st Note Updated step Status Change in SPS, step 1 in Remedial Action Plan (RAP) & Mitigation Plan (MP) Deleted 1st Note, changed titles to Manual Dispatch to take a Unit Off-line, Manual Dispatch to take a Unit of a CC Off-line, & updated procedure, changed title to Manual Dispatch to bring a Unit of a CC On-Line, & updated procedure Updated 2nd note and step 1 in Voltage Security Assessment Tool (VSAT)Updated Post in “Scripts” Added 2nd NOTE Updated OCN All procedures in this manual have been reviewed. | December 15, 2011 |
| 1.2 2.1 2.3 3.4 4.1 4.2 7.4 10.1 | 1.0 / 1 1.0 / 1 1.0 / 5 1.0 / 1 1.0 / 13 1.0 / 5 1.0 / 3 1.0 / 2 | Updated Scope Changed TSP to TO Updated database load script Changed insecure state to emergency condition Updated 1st Note, steps 6 & 8 in Post Contingency Overloads, steps 2 & 3 in Managing Constraints in SCED, added Model Inconsistencies/Updates procedure Updated Notes 1 & 2, Steps 1 & 2 Changed insecure state to emergency condition Updated Market Participant Backup Control Center Transfer | January 19, 2012 |
| 2.1 3.1 3.3 4.1 4.2 4.3 4.4 4.5 4.6 4.7 5.1 6.1 7.1 7.2 7.3 7.4 7.5 9.2 10.1 | 1.0 / 2 1.0 / 2 1.0 / 6 1.0 / 14 1.0 / 6 1.0 / 8 1.0 / 7 1.0 / 6 1.0 / 7 1.0 / 2 1.0 / 3 1.0 / 8 1.0 / 8 1.0 / 7 1.0 / 7 1.0 / 4 1.0 / 5 1.0 / 2 1.0 / 3 | Updated paragraph 4 Updated Operations Support Engineer Updated Operations Support Engineer & Desktop Guide reference Updated Operations Support Engineer, added 3rd Note, updated step 1 in Review Planned Outage Notes, steps 1, 2, 3, 4, 6, 7, 8, 9 & QSGR in Post Contingency Overloads, step 2, 4 & Log in Managing Constraints in SCED Updated Operations Support Engineer Updated Operations Support Engineer & step 1, 2 & 3 Updated Operations Support Engineer Updated Desktop Guide reference, 2nd Note, step 5 & SPS Posting & deleted step 4 in SPS, all steps in Mitigation Plan & Temporary Outage Action Plan Updated Desktop Guide reference Updated step 1 in Watch Updated TSP to TO, Operations Support Engineer & Desktop Guide reference Updated Operations Support Engineer, changed TSP to TO, Desktop Guide reference & step 1 of Power System Stabilizers (PSS) & Automatic Voltage Regulators (AVR) Updated step 1 in Watch Updated step 1 in Implement EEA Level 1 & step 1 in Implement EEA Level 3 Updated script in step 1 in Restore Firm Load Updated Operations Support Engineer & Desktop Guide reference Updated Operations Support Engineer & Desktop Guide reference Updated Desktop Guide reference Updated all steps in Telemetry Issues that could affect SCED and/or LMPs, step 1 in Backup/Alternate Control Center Transfer & Operations Support Engineer | March1, 2012 |
| 3.1 3.3 4.1 4.3 4.4 4.5 5.1 6.1 7.1 7.2 7.3 7.4 8.1 8.2 8.2 8.3 8.4 | 1.0 / 3 1.0 / 7 1.0 / 15 1.0 / 9 1.0 / 8 1.0 / 7 1.0 / 4 1.0 / 9 1.0 / 9 - / 8 1.0 / 8 1.0 / 5 1.0 / 4 1.0 / 0 1.0 / 4 1.0 / 2 1.0 / 4 | Updated step Gap Study Added TSAT Updated step 4 & deleted step 9 in Post-Contingency Overloads, clarified step 2 & 3 in Managing Constraints in SCED, Added Unsolved Contingencies Updated for TSAT tool, added Managing W-N during System Failures Updated step IROL and ‘instructing’ to ‘directing’ Updated step Status Change & ‘instructing’ to ‘directing’, updated step 3, 4 & log in RAP, added step 3 and log in PCAP, update Note, added TO Issue in MP Updated Opportunity Outage procedure Added Valley Import to VSAT procedure, deleted step 2 in PSS/AVR section Updated OCN, Advisory, Watch and Emergency Notice for Cold Weather and Extreme Cold Weather Added Load Management Programs in Implement EEA Added Load Management Programs in Restore EEA Updated for NPRR405 Changed ‘TDSP’ to ‘TO’ & T/S Operator to Real-Time Deleted Cold Weather Revised to 8.2 and changed Severe Cold Weather to Extreme Cold Weather Revised to 8.3, added OCN & Emergency Notice Revised to 8.4 and changed T/S Operator to Real-Time Operator | May 1, 2012 |
| 2.3 4.1 4.5 6.1 7.2 7.3 7.5 | 1.0 / 6 1.0 / 16 1.0 / 8 1.0 / 10 1.0 / 9 1.0 / 9 1.0 / 6 | Updated Database load with W-N active and Site Failover with W-N steps Added Constraint SF Cut Off step, updated step 2 & 3 in Managing Constraints in SCED Updated 2nd Note, added Basecase continuous SPS triggering step in SPS, updated step 1 in RAP, step Note, SCED unable to fully resolve constraint, & < 2% Absolute Shift Factors in MP, 1st Note in TOAP Updated step Valley Import Updated EILS to ERS per NPRR 451 Updated EILS to ERS per NPRR 451 Updated step 1 in ERCOT picks up Load for Non-ERCOT System and step 1 in Non-ERCOT System picks up Load for ERCOT | June 1, 2012 |
| 1.3 3.3 4.1 4.4 5.1 6.1 7.1 7.2 7.3 8.3 9.2 | 1.0 / 1 1.0 / 8 1.0 / 17 1.0 / 9 1.0 / 5 1.0 / 11 1.0 / 10 1.0 / 10 1.0 / 10 1.0 / 3 1.0 / 3 | Removed ERCOT Shift Supervisor paragraph Updated step 2 Updated step Constraint SF Cut Off, Managing Congestion during SCED Failure Updated step ≤300MW Updated Maintenance Level 2 and 3 outages Updated STP Voltage Tables Updated all step 1’s Updated Load Management Program Updated step 1 Updated scripts Updated 4th note | July 16, 2012 |
| 2.3 4.4 | 1.0 / 7 1.0 / 10 | Added Note to step Database Load Updated step IROL | August 29, 2012 |
| 2.3 2.4 3.3 4.1 4.3 4.4 4.5 4.7 6.1 7.1 7.2 7.3 7.4 7.6 8.1 8.2 8.3 8.4 | 1.0 / 8 1.0 / 2 1.0 / 9 1.0 / 18 1.0 / 10 1.0 / 11 1.0 / 9 1.0 / 3 1.0 / 12 1.0 / 11 1.0 / 11 1.0 / 11 1.0 / 6 1.0 / 3 1.0 / 5 1.0 / 6 1.0 / 4 1.0 / 5 | Added to make call to HHGT Added to make call to HHGT Added to make call to HHGT Updated PUN section and added to make call to HHGT Added Hotline script and to make call to HHGT Added Hotline script and to make call to HHGT Added to make call to HHGT Added to make call to HHGT Added to make call to HHGT Added to make call to HHGT Added to make call to HHGT Added to make call to HHGT Updated step 1 and added to make call to HHGT Added to make call to HHGT Added to make call to HHGT Added to make call to HHGT Added to make call to HHGT Added to make call to HHGT | September 12, 2012 |
| 2.2 3.1 3.2 3.3 3.4 4.1 4.3 4.4 4.5 5.1 5.2 6.1 7.4 8.3 9.1 | 1.0 / 1 1.0 / 4 1.0 / 2 1.0 / 10 1.0 / 2 1.0 / 19 1.0 / 11 1.0 / 12 1.0 / 10 1.0 / 6 1.0 / 1 1.0 / 13 1.0 / 7 1.0 / 5 1.0 / 4 | Added Hotline Call Communication Moved protective relay section to 5.2 Updated step 3 Split VSAT/TSAT and SE/RTCA out into separate procedures Updated steps Immediate Action Updated step Unknown Operating State, all steps in Evaluate Real-Time Contingency Analysis Results, steps 1, 4 & 6 in Post-Contingency Overloads Added 1st Note Added 1st Note, Updated 2nd NOTE & step 0 MW Updated 2nd Note Updated Returning from Planned Outage Early Added new procedure Updated Exceed URL, Reduce MW, added NOTE & moved step 1 to section 3.3 and renumbered Added Note Word smith OCN, Advisory, & Watch Updated step 1, 2 & 3. Added step 4 and Log All procedures in this manual have been reviewed. | November 1, 2012 |
| 3.2 3.5 4.1 4.4 4.5 6.1 7.2 7.5 | 1.0 / 3 1.0 / 0 1.0 / 20 1.0 / 13 1.0 / 11 1.0 / 14 1.0 / 12 1.0 / 7 | Updated step 3 Added procedure Updated Note, Constraint Shift Factor Cut Off, Post-Contingency Overloads steps 4-9 , QSGR & Managing Constraints in SCED step 2 & 4 Updated step VSAT Updated Special Protection Systems (SPS) (Identified as RAS in EMS) step 2, Remedial Action Plan (RAP) steps 1-5, & step 3 Pre-Contingency Action Plan (PCAP) Updated 2nd Note and steps 1-3 Voltage Issues Deleted step 2 per NPRR 480 Updated all step 1’s & added step 3 to clarify 6.5.9.5.2(1) | March1, 2013 |
| 2.3 2.4 3.1 3.3 3.5 4.1 4.2 4.3 4.4 4.5 4.6 4.7 5.1 6.1 7.1 7.2 7.3 7.4 7.6 8.1 8.2 8.3 8.4 | 1.0 / 9 1.0 / 3 1.0 / 5 1.0 / 11 1.0 / 1 1.0 / 21 1.0 / 7 1.0 / 12 1.0 / 14 1.0 / 12 1.0 / 8 1.0 / 4 1.0 / 7 1.0 / 15 1.0 / 12 1.0 / 13 1.0 / 12 1.0 / 8 1.0 / 4 1.0 / 6 1.0 / 6 1.0 / 6 1.0 / 6 | Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts and steps in Caution, Phase Shifters, Constraint Shift Factor Cut Off, Post Contingency Overloads, deleted Input Displays, added step In Series & Same Element in Managing Constraints in SCED & deleted Managing Congestion during SCED Failure Updated step 2 Deleted 2nd Note, added GTL and updated scripts Deleted 2nd Note, added GTL and updated scripts Deleted Directives, 1st Note in Mitigation Plan, 1st Note in Temporary Outage Action Plan and updated scripts Updated scripts Updated all steps and deleted Cancelation Updated script Updated script Added Generic script and Specific scripts Updated scripts Updated scripts Updated scripts Updated script Updated scripts Updated script Updated script Correct spelling and updated script | June 1, 2013 |
| 2.3 4.1 4.2 4.3 4.4 4.5 4.6 4.7 4.8 7.1 7.2 7.4 7.5 | 1.0 / 10 1.0 / 22 1.0 / 9 1.0 / 8 1.0 / 13 1.0 / 15 1.0 / 13 1.0 / 9 1.0 / 5 1.0 / 13 1.0 / 14 1.0 / 8 1.0 / 5 | Updated step EMS Changes and added MMS Changes Updated step Caution Updated and moved section 7.4 and renamed to 4.2 Changed section # Updated and changed section # Changed section #, IROL & updated step 0MW Changed section # & updated step 4 in RAPs Changed section # Changed section # Updated step 1 in Watch, Emergency Notice & DRUC Timeline not Met Updated 2nd Note Changed section # & step 2 Changed section # | July 15, 2013 |
| 2.3 4.1 4.2 4.5 6.1 7.1 | 1.0 / 11 1.0 / 23 1.0 / 10 1.0 / 16 1.0 / 16 - / 14 | Spelling correction to step MMS Changes Updated Caution, Constraint Shift Factor Cut Off, step 8 of Post-Contingency Overloads & PUN procedure Removed the word “load” Updated step VSAT Updated 2nd note & step 1 on Voltage Security Assessment Tool (VSAT) Updated Specific Scripts EMMS (LFC and RLC/SCED) Failure | August 9, 2013 |
| 2.3 2.4 3.3 3.5 4.1 4.2 4.4 4.5 4.6 4.8 7.1 7.2 7.3 7.5 8.1 8.2 8.3 8.4 | - / 12 - / 4 - / 12 - / 2 - / 24 1.0 / 11 1.0 / 14 1.0 / 17 1.0 / 14 1.0 / 6 1.0 / 15 1.0 / 15 1.0 / 13 1.0 / 6 1.0 / 7 1.0 / 7 1.0 / 7 1.0 / 7 | Removed HHGT TO reference Removed HHGT TO reference Removed HHGT TO reference Removed HHGT TO reference Removed HHGT TO reference Removed HHGT TO reference Removed HHGT TO reference Removed HHGT TO reference Removed HHGT TO reference Removed HHGT TO reference Removed HHGT TO reference Removed HHGT TO reference Removed HHGT TO reference Removed HHGT TO reference Removed HHGT TO reference Removed HHGT TO reference Removed HHGT TO reference Removed HHGT TO reference | August 30, 2013 |
| 4.1 5.1 6.1 | 1.0 / 25 1.0 / 8 1.0 / 17 | Updated step 5 in Post-Contingency Overloads Updated to reflect SCR770 changes Updated script and added new script for Power System Stabilizers (PSS) & Automatic Voltage Regulators (AVR) | September 27, 2013 |
| 3.3 3.4 3.5 4.1 4.2 4.4 4.5 4.6 4.7 4.8 4.9 5.1 5.2 6.1 7.1 7.2 7.3 7.5 8.1 8.2 8.3 8.4 9.2 10.1 | 1.0 / 13 1.0 / 3 1.0/ 3 1.0 / 26 1.0 / 12 1.0 / 15 1.0 / 18 1.0 / 15 1.0 / 10 1.0 / 7 1.0 / 0 1.0 / 9 1.0 / 1 1.0 / 18 1.0 / 16 1.0 / 16 1.0 / 14 1.0 / 7 1.0 / 8 1.0 / 8 1.0 / 8 1.0 / 8 1.0 / 4 1.0 / 4 | Updated Log steps Updated Log steps Updated Log step Updated step 1 on Review Planned Outage Notes, step 1 for PUNs, Managing Constraints in SCED and Logs Updated Title, added step 2 and Log steps Deleted step GTL, updated step 1 and Log Updated step VSAT, Log and deleted GTL Updated Log steps Updated Log steps Updated Log steps Added new procedure Updated steps Definition, Approve Maintenance Outage, Coordinate Maintenance, Coordinate Maintenance Level 2 and 3, Log and step 1 in Simple Transmission Outage Updated Log steps Updated VSAT section Updated Log steps Updated Log steps Added step Reserves and Log steps Updated Log steps Updated note, OCN, Advisory and Log step Added note, updated OCN, Advisory, Watch and Log step Added note, updated OCN, Advisory, Watch and Log step Updated note and Log step Updated Log steps Updated Log steps All procedures in this manual have been reviewed | December 13, 2013 |
| 4.2 4.4 4.5 4.6 4.7 4.8 4.9 4.10 7.1 | 1.0 / 13 1.0 / 16 1.0 / 19 1.0 / 0 1.0 / 16 1.0 / 11 1.0 / 8 1.0 / 1 1.0 / 17 | Updated 1st Note, step 3, added step 4 & deleted step 5 in Transmission Issues within ERCOT. Added Note to Transmission/Capacity Issues within the CFE Area Removed posting requirement Removed posting requirement New procedure for new GTL Updated section number Updated section number Updated section number Updated section number & changed Watch to OCN Updated to incorporate NPRR542 and update scripts | January 1, 2014 |
| 4.1 4.2 4.6 7.3 8.4 | 1.0 / 27 1.0 / 14 1.0 / 1 1.0 / 15 1.0 / 9 | Updated step 3 in Post-Contingency Overloads Updated step 3, 4 in Transmission Issues within ERCOT and step 1, 2 & 3 in Transmission/Capacity Issues within the CFE Area Updated step 1 & 2 Updated steps Reserves and 1 in Restore Firm Load Updated 1st Note | February 25, 2014 |
| 4.1 4.2 4.4 4.5 4.8 6.1 7.2 7.4 9.1 | 1.0 / 28 1.0 / 15 1.0 / 17 1.0 / 20 1.0 / 12 1.0 / 19 1.0 / 17 1.0 / 9 1.0 / 5 | Updated VDI information Updated steps in Transmission Issues within ERCOT Updated VDI information Updated VDI information Updated Manual commitment process Updated VDI information Updated media appeal language & LM Program Updated VDI information Updated step 1 & 3, added step 5 | April 4, 2014 |
| 2.2 4.1 4.2 4.4 4.6 4.7 4.9 6.1 7.1 8.1 | 1.0 / 2 1.0 / 29 1.0 / 16 1.0 / 18 1.0 / 2 1.0 / 17 1.0 / 9 1.0 / 20 1.0 / 18 1.0 / 9 | Added VDI to Master QSEs Updated step 1 in Review Planned Outage Notes, QSGR & Log in Post-Contingency Overloads & PUN steps Updated section title & step 5, deleted step 3 Updated step 2 Updated step 1 & 2 Updated step 1 in RAP Deleted Note Updated Note & Step 1 in Voltage Issues Added Note, updated Market Notices Advisory & Watch Updated scripts | June 1, 2014 |
| 4.1 4.2 4.7 7.2 | 1.0 / 30 1.0 / 17 1.0 / 18 1.0 / 18 | Changed WGR to IRR & updated desktop reference Updated step 4 & 6 Updated 1st Note Added Media Appeal & updated step 1 script | August 1, 2014 |
| 4.1 5.1 6.1 7.1 | 1.0 / 31 1.0 / 10 1.0 / 21 1.0 / 19 | Updated desktop reference number & step 3 in Post-Contingency Overloads, added step 4 to PUN section Updated desktop reference number Updated step 1, 2 & 3 in Real-Time Voltage Issues, added Future Voltage Issues Updated Generic Script | October 1, 2014 |
| 2.3 2.4 3.3 3.5 4.1 4.2 4.4 4.5 4.6 4.7 4.8 4.9 5.1 6.1 7.1 7.2 10.1 | 1.0 / 13 1.0 / 5 1.0 / 14 1.0 / 4 1.0 / 32 1.0 / 18 1.0 / 21 1.0 / 3 1.0 / 19 1.0 / 13 1.0 / 10 1.0 / 2 1.0 / 11 1.0 / 22 1.0 / 20 1.0 / 19 1.0 / 5 | Removed references to W-N Updated scripts Removed references to W-N/TSAT, combined SE/RTCA Updated for Operating Guide 4.7 Updated Phase Shifters & removed references to TSAT Removed references to TSAT & added Future Studies Deleted West to North procedure and re-numbered Re-numbered Re-numbered Re-numbered Re-numbered Re-numbered Updated step 1 Updated step 2 & 3 in Real-Time Voltage Issues, Future Voltage Issues & Requesting Resource to operate beyond URL Updated Specific Scripts Updated EEA2 script Deleted Requests to decommit in Operating Period All procedures in this manual have been reviewed | December 15, 2014 |
| 2.2 4.1 4.2 4.3 4.4 4.7 4.8 6.1 7.4 8.2 | 1.0 / 3 1.0 / 33 1.0 / 19 1.0 / 9 1.0 / 22 1.0 / 14 1.0 / 11 1.0 / 23 1.0 / 10 1.0 / 9 | Added definitions for Dispatch and VDIs Updated “Review Planned Outage Notes” and provided a better flow, deleted redundant steps & added Basecase Overloads, Added step Topology Change Updated to reflect SOL Methodology and provide a better flow Updated step <200MW Updated step 1 Updated script Updated step Exceeding URL or Reducing Output Updated all steps for better flow Updated scripts | March 1, 2015 |
| 3.5 4.2 4.5 4.9 9.1 | 1.0 / 5 1.0 / 20 1.0 / 4 1.0 / 3 1.0 / 6 | Updated GMD process Updated step 2 of Rio Grande Valley Renamed to GTC Stability and added Ajo – Zorrillo Updated to new name Generic Transmission Constraint Updated scripts | March 30, 2015 |
| 2.3 2.4 3.3 3.5 4.1 4.2 4.3 4.4 4.5 4.6 4.8 4.9 7.1 7.2 7.3 7.4 7.5 7.6 8.1 8.2 8.3 8.4 9.1 | 1.0 / 14 1.0 / 6 1.0 / 15 1.0 / 6 1.0 / 34 1.0 / 21 1.0 / 10 1.0 / 23 1.0 / 5 1.0 / 20 1.0 / 12 1.0 / 4 1.0 / 21 1.0 / 0 - / 20 - / 16 1.0 / 11 1.0 / 8 - / 10 - / 10 - / 9 - / 10 1.0 / 7 | Moved scripts to script procedure Moved scripts to script procedure Moved scripts to script procedure & updated GTL to GTC Moved scripts to script procedure Updated step 1 QSE Requests to Decommit a Resource, updated GTL to GTC, and moved scripts to script procedure Moved scripts to script procedure Moved scripts to script procedure Moved scripts to script procedure & updated GTL to GTC Renamed and updated Zorrillo – Ajo table Moved scripts to script procedure Updated for implementation of NOGRR135/NPRR642 and moved scripts to script procedure Moved scripts to script procedure & updated GTL to GTC Updated 50% Probability Of Down Ramp to 30%, removed 70% Probability Of Up Ramp, added note and moved scripts to script procedure New process for implementation of NOGRR135/NPRR642 Updated section number and moved scripts to script procedure Updated section number and moved scripts to script procedure Updated section number Updated section number and moved scripts to script procedure Moved scripts to script procedure Moved scripts to script procedure Moved scripts to script procedure Moved scripts to script procedure Moved scripts to script procedure | May 1, 2015 |
| All Sections 2.3 3.1 3.5 4.4 | 1.0 / 1 1.0 / 15 1.0 / 6 1.0 / 7 1.0 / 24 | Added a “T” for TO scripts Renamed section to Site Failovers and Database Loads Updated Gap Study Updated Procedure Purpose. Updated GMD MIS Posting Scripts to include “until time” Updated procedure purpose and step ≤500MW | July 15, 2015 |
| 4.1 4.5 | 1.0 / 35 1.0 / 6 | Updated step 1 Post-Contingency Overloads Replaced East Texas Stability with Panhandle Stability Added Laredo Import Stability Removed Zorillo – Ajo Table | September 9, 2015 |
| 4.5 7.2 | 1.0 / 7 1.0 / 1 | Removed Panhandle Stability Step 1, updated Step 2 and Laredo Area Stability Updated Double-Circuit Contingency actions | October 1, 2015 |
| 2.3 3.3 3.5 4.1 4.2 4.3 4.4 4.5 4.6 4.8 4.9 7.1 7.3 7.4 7.6 8.1 8.2 8.3 8.4 9.1 | 1.0 / 16 1.0 / 16 1.0 / 8 1.0 / 36 1.0 / 22 1.0 / 11 1.0 / 25 - / 8 1.0 / 21 1.0 / 13 1.0 / 5 1.0 / 22 1.0 / 21 1.0 / 17 1.0 / 9 1.0 / 11 1.0 / 11 1.0 / 10 1.0 / 11 1.0 / 8 | Updated step Site Failover T#17 Updated step Site Failover Complete T#18 Updated State Estimator/RTCA step 3 T#21 & step 7 T#22 Updated Voltage Security Assessment Tool (VSAT) step 2 T#23 & step 6 T#24 Updated step 1 T#25 Updated step K Level Increases/Decreases T#26 Updated step Cancel T#27 Updated Review Planned Outage notes step Cascading Condition Updated Basecase Overloads step Qualifying Facilities T#28 Updated Rio Grande Valley step 2 Added Rio Grande Valley step Reliability Margin <100 MW Updated Rio Grande Valley step 3 T#29 Updated step Cascading Condition Updated Pre-Contingency Load Shedding to avoid Post-Contingency cascading step 3 T#30 Updated step ≤300 T#31 Updated step ≤100 T#32 Updated step 0MW T#33 Updated Laredo Area Stability step 4 T#29 Updated Zorrillo – Ajo 345kV Stability step 1 & step 2 Added Liston Stability Added Molina Stability Updated Special Protective Systems (SPS) step SPS Posting Updated Mitigation Plan (MP) step Issue Watch T#34 Updated Mitigation Plan (MP) step Cancel Watch T#35 Updated Advisory step Cancel Advisory T#2 Updated Watch step Issue Watch T#3 Updated Watch step Cancel Watch T#4 Updated step GTC T#36 Updated Title Operating Condition Scripts Updated Operating Condition Scripts step Hotline T#37 Updated Operating Condition Scripts step Hotline Cancellation T#38 Updated Title Specific Scripts for QSE’s Updated Specific Scripts for QSE’s step 30% Probability Of Down Ramp T#39 & T#40 Updated Specific Scripts for QSE’s step Failure T#41 & T#42 Updated Specific Scripts for QSE’s step EMMS (LFC and RLC/SCED) Failure T#43 & T#44 Updated Specific Scripts for QSE’s step Increasing Amount of Ancillary Services T#45 & T#46 Updated Specific Scripts for QSE’s step A/S Insufficiency Offers in DAM T#47 & T#48 Updated Specific Scripts for QSE’s step REG/RRS – RUC Committed Shortages T#51 & T#52 Updated Specific Scripts for QSE’s step DAM Timeline Deviation T#53 & T#54 Updated Specific Scripts for QSE’s step DAM Failure T#55 & T#56 Updated Specific Scripts for QSE’s step DRUC Delay or Timeline Deviation T#57 & T#58 Updated Specific Scripts for QSE’s step DRUC Timeline not Met T#59 & T#60 Updated Specific Scripts for QSE’s step HRUC Failure or Timeline Deviation T#61 & T#62 Updated Specific Scripts for QSE’s step DRUC Committed for Capacity Shortage T#63 & T#64 Updated Specific Scripts for QSE’s step Excess Generation T#65 & T#66 Updated Specific Scripts for QSE’s step Projected Reserve Capacity Shortage with no market solution T#67 & T#68 Updated Specific Scripts for QSE’s step RMR Projected Reserve Capacity Shortage T#69 & T#70 Update first note, Updated Implement EEA Level 1 step Load Management title T#6 Updated Implement EEA Level 2 step 1 T#7 Updated Implement EEA Level 3 step 1 T#8, and Implement NPRR708 for EEA Updated Restore Firm Load step 1 T#9 & T#10 Updated Move from EEA Level 1 to EEA 0 step 1 T#13 Updated step Return to Normal TO Notification T#71 Updated step OCN T#72 Updated step Advisory T#73 Updated step Watch T#74 Updated step Emergency T#75 Updated step OCN T#76 Updated step Advisory T#77 Updated step Watch T#78 Updated step Emergency Notice T#79 Updated step OCN T#80 Updated step Advisory T#81 Updated step Watch T#82 Updated step Emergency Notice T#83 Updated step OCN/Advisory/Watch T#84 Updated step 2 T#85 All procedures in this manual have been reviewed | December 31, 2015 |
| 2.1 4.1 4.3 4.5 4.6 5.1 6.1 7.1 9.1 | 1.0 / 3 1.0 / 37 1.0 / 12 1.0 / 9 1.0 / 22 1.0 / 12 1.0 / 24 1.0 / 23 1.0 / 9 | Updated System Operator Responsibilities and Authority Updated NERC Standard Reference Updated NERC Standard Reference Updated Molina Stability Updated NERC Standard Reference Updated NERC Standard Reference Updated NERC standard Reference Updated Voltage Security Assessment Tool step 1 table Updated PSS & AVR step Note Added Specific Scripts for QSE’s T#86 Updated Specific Scripts for QSE’s T#51 Updated Alert Levels | February 1, 2016 February 10, 2016 |
| 1.3 6.1 7.1 | 1.0 / 2 1.0 / 25 1.0 / 24 | Removed Interchange Coordinator Updated STP Voltage Table Updated Execute a SASM script title T#86 |  |
| 3.1 4.1 4.2 4.4 4.5 6.1 | 1.0 / 11 1.0 / 38 1.0 / 23 1.0 / 26 1.0 / 10 1.0 / 26 | Updated step STP Lines Updated Review Planned Outages Cascading Condition Updated Reliability Margin Updated ≤300MW Updated Zorrillo – Ajo 345kV Stability step 1 Updated step STP Voltage Table, 1 and 2 | April 29, 2016 |
| 2.1 2.2 4.1 4.2 4.3 4.4 4.5 4.6 6.1 7.1 7.4 7.5 | 1.0 / 4 1.0 / 4 1.0 / 39 1.0 / 24 1.0 / 13 1.0 / 27 1.0 / 11 1.0 / 23 1.0 / 27 1.0 / 25 1.0 / 18 1.0 / 12 | Updated steps for COM-002-4 Updated steps for NPRR748, NOSCED and COM-002-4 Updated Reliability Margin Updated steps for COM-002-4 Updated steps for COM-002-4 Updated step for COM-002-4 Updated steps for COM-002-4 Updated steps for COM-002-4 Updated steps for COM-002-4 & added Typical Script T#87 BAAL Firm Load Shed Updated Restore Firm Load step 1 Updated steps for COM-002-4 | June 30, 2016 |