- Power Operations Bulletin # 771

ERCOT has posted/revised the DC Tie manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

- http://www.ercot.com/mktrules/guides/procedures/index.html

## 2.1	System Operator Responsibility and Authority

Procedure Purpose: To ensure the System Operators know their roles, responsibility and authority.

| Protocol Reference | 6.5.1.1 | 6.5.1.2(3) | 6.5.2 |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.5.2(1) |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 4 | Effective Date: March 31, 2017 |
| --- | --- | --- |

ERCOT ISO as a Transmission Operator (TOP), the single Balancing Authority (BA), and only Reliability Coordinator (RC) registered within the ERCOT Interconnection shares all information between these roles simultaneously and acts concurrently as a single entity, satisfying coordination between the TOP, BA and RC.

The System Operator (SO) shall, in accordance with NERC Reliability Standards and ERCOT Protocols, have clear decision-making authority to act to address the reliability of its Reliability Coordinator Area by direct actions or by issuing Operating Instructions during both normal and emergency conditions.  These actions shall be taken without delay and  may include shedding of firm load without obtaining approval from higher-level personnel.

- The SO on duty is, in accordance with the ERCOT Protocols, Operating Guides, and NERC Reliability Standards, and acting as the Balancing Authority, Transmission Operator, and Reliability Coordinator shall request and receive information required to continually monitor the operating conditions which will assure security and reliability of the ERCOT system.

- The SO issues Dispatch Instructions / Operating Instructions for the Real-Time operation of Transmission Facilities to a TO and to a QSE for the Real -Time operation of a Resource.

- The SO shall, on an ERCOT-wide basis, coordinate the ERCOT System Restoration (Black Start) Plan.  The SO shall implement the Black Start Plan and shall direct the reconnection efforts of the islands, established by restoration activities.

- The SO shall ensure compliance with the ERCOT Protocols and Operating Guides on identified transfer limits.  The SO receives all specified notifications for the MPs with regard to energy transactions (Balanced Schedules), AGC control modes, routine adjustments, and equipment limitations and outages.

- The SO performs security analyses on a Day Ahead and real-time basis and ensures all Forced Outages are entered into the Outage Scheduler. The SO shall obtain or arrange to provide emergency energy over the DC Tie(s) on behalf of ERCOT.

- The SO shall issue appropriate OCN’s, Advisories, Watches, and Emergency Notices, and coordinate the reduction or cancellation of clearances, re-dispatch of generation, and request, order, or take other action(s) that the SO determines is necessary to maintain safe and reliable operating conditions on the ERCOT system in accordance with ERCOT Protocols, Operating Guides, and NERC Reliability Standards.  The SO will implement and terminate ERCOT Time Corrections, and will determine the need for and implement the operation of a QSE on Constant Frequency Control for loss of ERCOT’s load frequency control system.

The SPP DC-Tie processes, procedures, or plans that support or affect SPP shall be reviewed at least once every 3 years and updated if needed.  These would include any DC-Tie procedures, inadvertent energy procedures, and emergency procedures.

## 2.3	NXT Notification Requirements

Procedure Purpose:  To ensure the operator stays current using the system and to ensure system is tested.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 5 | Effective Date: March 31, 2017 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Beginning of each Shift | - Log into the Taylor NXT Communicator Emergency Notification System (ENS) at the beginning of each shift, UNLESS: - TaylorENS is unavailable - Notified by Telecommunications/Help Desk/Shift Supervisor of maintenance, etc. - Testing Non-Routinely used Telecommunications - Refer to Desktop Guide Common to Multiple Desks Section 2.8, - Notify Help Desk immediately if unable to log into the NXT Communicator and request immediate assistance. |
| NXT Test | On the first weekend of each month, between the hours of 0800-2200: - Coordinate the actual test time with the Shift Supervisor if he instructs you to proceed, - Test NXT Communicator by activating the “SO ENS Test” scenario, - If any issues are found, open help ticket and cc: “shiftsupv”, - Make log entry. |

## 3.2	Import and Export Limits for the CENACE DC Ties

Procedure Purpose: To confirm the import and export limits of the CENACE DC Ties to ensure Reliability of the ERCOT Interconnection.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | INT-006-4 R1.1 |  |  |  |

| Version: 1 | Revision: 13 | Effective Date: March 31, 2017 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | Studies are required to set import/export limits between CENACE and ERCOT based on system conditions for commercial and emergency operations. ERCOT will conduct studies in different time horizons including but not limited to seasonal (winter and summer peaks), Day-Ahead and real-time as needed. Operations Support group will calculate daily import/export transfer limits for the Railroad and Eagle Pass DC Ties, and Laredo VFT. Daily import and export limits for the Railroad and Eagle Pass DC Ties, and Laredo VFT will be posted on the “Transmission Limits to Be Monitored” on the MIS Secure at approximately 1700 in the Day-Ahead. MIS Secure>GRID>Transmission>Generic Transmission Limits If the limits are not posted, notify the Operations Support Engineer. |
| Adjustment Period | Except in the case of an actual or anticipated transmission emergency, any curtailments or adjustments of schedules over the posted limit must be completed prior to the beginning of the Adjustment Period. The Adjustment Period is for each Operating Hour, the time between 1800 in the Day-Ahead up to the start of the hour before that Operating Hour. |
| 1 | Once the DC-Tie limits for next day are received and prior to the start of the 1800 Day-Ahead Adjustment Period, check the sum of the E-Tags to ensure the export limits are not exceeded on any of the CENACEE DC-Tie. IF: - The sum of the E Tags exceed the import or export limit on any CENACE DC Tie, THEN: - ERCOT will curtail the E-Tag to posted limit based on the criteria of “Last in – First out” until the over schedule is alleviated. |
| 2 | IF: - A new E-Tag is received in the Adjustment Period or Operating Hour which creates an exceedance of the posted export limits on any CENACEE DC-Tie, THEN: - Deny the E-Tag. |

## 3.3	Approve E-Tags for the CENACE DC Ties

Procedure Purpose: An E-Tag received in the OATI WebTrans regarding DC Tie flows into or out of ERCOT will be validated for accuracy.

| Protocol Reference | 4.4.4(5) | 4.4.4.1 | 4.4.4.2(1) |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 2.1 (3)(e) |  |  |  |
| NERC Standard | INT-006-4 R1, R1.2, R2, R2.1, R4 | TOP-002-4 R4, R4.2, R5 |  |  |

| Version: 1 | Revision: 22 | Effective Date: March 31, 2017 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - AEP TO in Corpus Christi is the DC Tie Operator (AEP TO) for the DC_S (Eagle Pass DC Tie) and the DC_L (Laredo VFT) - Sharyland TO in Amarillo is the DC Tie Operator (SHARYLAND TO) for the DC_R (Railroad DC Tie) - All communications will be with the DC-Tie Operator and they will communicate with CENACE |
| NOTE | ERCOT will not allow an E-Tag to flow from CENACE to SPP or from SPP to CENACE. This will require two separate E-Tags. E-Tags are not calculated in our ACE equation, DC Tie schedules are seen by our EMMS as a generator (import) or load (export). |
| NOTE | - ERCOT has analyzed the ramping capability of its Interconnection and is capable of ramping at a greater rate than the maximum ramp rate schedule on any of the DC Ties - The Railroad DC Tie has a 15 MW minimum flow requirement when E-Tags are scheduled - Approximately one hour before start of schedule, notify the ERCOT Transmission & Security Operator with scheduled MW, Tie and direction of flow and duration. |
| NOTE | Timing requirements can be found in NERC Standard INT-006-4 Attachement 1, the OATI software incorporates these timing requirements into the tool and actions can not be taken outside the timing requirements. |
| 1 | Automatic validation in WebTrans for each new or updated E-Tag will display ‘pass’ or ‘fail’. The criteria ERCOT uses to validate E-Tags is: - ERCOT Market Information fields must have QSE information - TP (Transmission Provider) must have ERCO specified in the Physical Path If either of the above validations fail, the E-Tag will be automatically denied. If you believe an E-Tag failed validation erroneously, the list of approved ERCOT Registered QSE’s can be found at the following website: http://www.ercot.com/mktparticipants/ Select the “List of Market Participants in ERCOT Region”, and then select the DC Tie Scheduling List tab to view the ERCOT Registered QSE’s. If the QSE name is on the list but was denied by WebTrans, approve the E-Tag and inform the ERCOT help desk and OATI help desk if needed. Another point of reference is to view the “QSE Contracts” in WebTrans. Each QSE is associated with each DC-Tie individually. WebTrans Reference Display: Tag Validation Summary Data>QSE Contracts |
| 2 | When a New or Updated E-Tag is received in the WebTrans system: Manually validate the following: - PSE Contact Information must be the QSE information and not ERCOT - “ERCO” must not be listed as a PSE in the Tag Information - “ERCO” must not be listed as a PSE in the Physical Path - Time Zone should be CS (central standard), CD (central daylight) or CP (central prevailing) during time change - “Transaction type” must be “Energy or Normal” - AEPT must be included as the TP (Transmission Provider) in the Physical Path and ERCO as a Scheduling Entity on the AEPT TP row in the Physical Path for DC_S or DC_L - SULP must be included as the TP in the Physical Path and ERCO as a Scheduling Entity on the SULP TP row in the Physical Path for the DC_R - There are no losses (MW) in the ERCOT Control Area. This should be to or from AEPT or SULP as shown on the “Energy and Transmission Profiles” section, loss accounting may be blank, financial or in-kind for ERCOT - Tags are permitted to be submitted within the COP time frame (up to seven days in advance), but a separate tag for each day must be submitted and the Start Time and Stop Time MUST NOT cross the midnight hour. - If Tag comes in with a Late status, deny the Tag (unless it is a curtailment). - The sum of E-Tags are submitted that will cause the DC Tie to exceed the import/export limits for the tie; IF: - Any of the above information is incorrect on the E-Tag; THEN: - Deny the E-Tag, otherwise proceed below. WebTrans Reference Displays: Scheduling>Interchange>BTF Checkout |
| 3 | The ramp rate for DC_R will be 50 MW per minute due to reactive issues on the CENACE side. DC_L and DC_S have no ramp limitations. - Ramp Duration should be filled out on DC_R E-Tags only - Deny any Railroad DC-Tie E-Tag that does not have a ramp duration entered. - DC_L and DC_S ramp duration can remain blank which is the default for a 10 minute ramp. |
| 4 | The Railroad DC Tie has a 15 MW minimum flow requirement. Ensure the net of the E-Tags are not less than 15 MW. |
| NOTE | Webtrans and MMS (ABB) utilize a different sign convention (positive and negative numbers) between the two systems. WebTrans: - (-) Imports - (+) Exports MMS: - (+) Imports - (-) Exports |
| COP E-Tags | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment> HRUC Displays> DSI Displays> DSI Data Processes> DSI DC Tie Schedule Market Operation>Reliability Unit Commitment> HRUC Displays> DSI Displays> External Input Data> MI COP - Verify that E-tags are being imported into the MMS by going to the MI COP display and filter ‘ERCOT’ as the QSE name |

## 3.6	Adjustment of CENACE DC Ties

Procedure Purpose: The process to approve or deny adjustments to E-Tags.

| Protocol Reference | 4.4.4(1) | 4.4.4(10) |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 2.8 |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 9 | Effective Date: March 31, 2017 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Imports |  |
| NOTE | E-Tag adjustments must be in an “Approved” or “Implemented” status to be calculated into the net scheduled interchange. |
| 1 | IF requested by either DC Tie Operator, AEP TO or SHARYLAND TO, checkout the net scheduled interchange value for each CENACE DC Tie affected by E-Tag adjustments. WebTrans Reference Display: Realtime Summary |
| ### Exports |  |
| 1 | IF: - The adjustment causes the sum of the E-Tags to exceed the posted export limit on any CENACE DC-Tie, THEN: - Deny the E-Tag adjustment. |
| 2 | Notify the ERCOT Transmission & Security Operator when E-Tag Net Export adjustments are greater than 100 MW during the Adjustment Period. |
| NOTE | E-Tag adjustments must be in an “Approved” or “Implemented” status to be calculated into the net scheduled interchange. |
| 3 | IF requested by either DC Tie Operator, AEP TO or SHARYLAND TO, checkout the net scheduled interchange value for each CENACE DC Tie affected by E-Tag adjustments. WebTrans Reference Display: Realtime Summary |

## 3.7	DC Tie Trips or Derates

Procedure Purpose: The process when a DC Ties trip or is de-rated.

| Protocol Reference | 4.4.4(1) |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 10.1(2) |  |  |  |
| NERC Standard | INT-006-4 R1.1 |  |  |  |

| Version: 1 | Revision: 13 | Effective Date: March 31, 2017 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### CENACE DC Ties |  |
| 1 | IF: - Any of the CENACE DC Ties trip, THEN: - ERCOT will have the responsibility to curtail the E-Tags. - Curtail the E-Tags for the Tie that tripped (see Desktop Guide DC Tie Desk Section 2.3 or 2.4). |
| 2 | Once the DC Tie that tripped is operational, re-load the curtailed E-Tag(s), if applicable: - Re-load curtailed E-Tag(s) (see Desktop Guide DC Tie Desk Section 2.5), - Notify the appropriate DC Tie Operator. |
| 3 | IF: - The re-loaded E-Tag(s) go passive deny because CENACE or DC Tie Operator did not approve the E-Tag(s) in the allotted time; THEN: - Re-load the E-Tag(s) again, AND - Notify the appropriate DC Tie Operator. If reload fails the second time stop trying and keep tag curtailed. |
| Post Message | WHEN: - The Eagle Pass, Railroad, or Laredo DC Tie trips; THEN: - Post message on MIS Public, - Use the canned message, - End time will be unknown, put through the end of the day |
| Cancel Message | WHEN: - The DC Tie returns to service; THEN: - Cancel message |
| ### CENACE DC Tie Derates |  |
| Post Message | IF: - Notified that any of the CENACE DC Ties are temporally derated; THEN: - Post message on MIS Public; - Select Create Freeform Notice, - Operational Information, - Low priority, - Public. Typical MIS Posting: “ERCOT has been notified that the [TIE] DC Tie has been derated to [AMOUNT] MW Import/Export due to [REASON] until further notice.” |
| Cancel Message | WHEN: - Tie returned to normal service; THEN: - Cancel message |
| ### SPP DC TIES |  |
| 1 | IF: - Any of the SPP DC Ties trip, THEN: - SPP has the responsibility to curtail the E-Tags. |
| Post Message | WHEN: - The East or North DC Tie trips; THEN: - Post message on MIS Public, - Use the canned message, - End time will be unknown, put through the end of the day |
| Cancel Message | WHEN: - Tie returned to service; THEN: - Cancel message |
| ### SPP DC Tie Derates |  |
| Post Message | IF: - Notified that any of the SPP DC Ties are temporally derated; THEN: - Post message on MIS Public; - Select Create Freeform Notice, - Operational Information, - Low priority, - Public. Typical MIS Posting: “ERCOT has been notified that the [TIE] DC Tie has been derated to [AMOUNT] MW Import/Export due to [REASON] until further notice.” |
| Cancel Message | WHEN: - Tie returned to normal service; THEN: - Cancel message |

## 3.9	Managing Daily Inadvertent Energy for the Laredo VFT and Eagle Pass DC Ties

Procedure Purpose: To track any difference between the schedule net interchange and the actual net interchange.

| Protocol Reference | 6.5.4 |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 2.2.1(3)(c)(i) | 2.8(1) & (3) |  |  |
| NERC Standard | INT-009-2.1 R3 |  |  |  |

| Version: 1 | Revision: 12 | Effective Date: March 31, 2017 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Monitor | Monitor the flows on the DC-Ties to ensure the Ties are ramping appropriately and match the net schedules. |
| NOTE | If the proper information is not listed when an E-Tag is created and submitted, the E-Tag may not be displayed correctly in all WebTrans displays. Examples include, but are not limited to a PSE not using the proper POR/POD in the Physical Path (EGPS_DC or LAR_VFT). |
| 1 | Before the start of the hour, confirm the net-scheduled value for each DC Tie with the DC Tie Operator (AEP TO). If there is a discrepancy, go over each E-Tag ID and MW amount for the affected DC Tie(s). - If an E-Tag can not be seen in WebTrans OR by the DC Tie Operator, work to resolve the problem OR ensure the E-Tag is curtailed to zero (0). WebTrans Reference Displays: Scheduling>QSE Summary Scheduling>BTF Display |
| 2 | Check out the Actual SCADA data values for the previous hour with the DC Tie Operator (AEP TO) for each DC Tie. - If ERCOT’s actual values are different from the DC Tie Operator’s actual values by less than 10 MWH, overwrite the actual value in the WebTrans system with a whole number. - If ERCOT’s actual values are different from the DC Tie Operator’s actual values by 10 MWH or more and the reason is known (database load, loss of ICCP, etc.), overwrite the actual value in the WebTrans system. Log the appropriate information. - If ERCOT’s actual values are different from the DC Tie Operator’s actual values by 10 MWH or more and the reason is unknown; ERCOT and the DC Tie Operator will initiate an investigation. Log the appropriate information (time, date, total MW difference, DC Tie, name of the DC Tie Operator and any other relevant information). Open an ERCOT Help Desk ticket for EMMS Production to investigate problems with the meter information and notify Shift Supervisor. WebTrans Reference Displays: Scheduling>Inadvertent>Tie Data Scheduling>Interchange>ATF Checkout |
| 3 | After midnight, each day, check out the total scheduled and actual values for each DC Tie with the DC Tie Operator, AEP TO: IF: - Both parties agree on the Scheduled In and Out values and on the Actual In and Out values; THEN: - Prepare report for the DC_L and DC_S - Select “[Tie name]” on the CA/Interface - Select “Schedule” on the “Checkout” dropdown - Check the bottom box on the totals row in Column C - Click the “Apply Checkout” button - Proceed to Step 5. WebTrans Reference Display: Scheduling>Interchange>ATF Checkout |
| 4 | If there is a disagreement on the total scheduled and/or actual values with the DC Tie Operator, verify the values for each hour as necessary to find the discrepancy. An effort should be made to work out all discrepancies. If the discrepancy is with the scheduled values: - Check the box in Column C for each hour that ERCOT is in agreement with the DC Tie Operator for the scheduled value. - Leave the box unchecked in Column C for each hour where there is a discrepancy with a scheduled value and it can not be worked out with the DC Tie Operator. - Click the “Apply Checkout” button. - Log the appropriate information and send email to shiftsupv@ercot.com. If the discrepancy is with an actual value, change the ERCOT value to match the DC Tie Operator’s value. WebTrans Reference Displays: Scheduling>Interchange>ATF Checkout Scheduling>Inadvertent>Tie Data |
| 5 | Create an Excel file for each the DC_S and DC_L DC Ties and email to the following (see Desktop Guide DC Tie Desk Section 2.9): - CFE DC-Tie Inadvertent |

## 3.10	Managing Daily Inadvertent Energy for the Railroad Tie

Procedure Purpose: To track any difference between the schedule net interchange and the actual net interchange.

| Protocol Reference | 6.5.4 |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 2.2.1(3)(c)(i) | 2.8(1) & (3) |  |  |
| NERC Standard | INT-009-2.1 R3 |  |  |  |

| Version: 1 | Revision: 4 | Effective Date: March 31, 2017 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Monitor | Monitor the flows on the DC-Ties to ensure the Ties are ramping appropriately and match the net schedules. |
| NOTE | If the proper information is not listed when an E-Tag is created and submitted, the E-Tag may not be displayed correctly in all WebTrans displays. Examples include, but are not limited to a PSE not using the proper POR/POD in the Physical Path (ROAD_DC). |
| 1 | Before the start of the hour, confirm the net-scheduled value for the DC Tie with the DC Tie Operator, SHARYLAND TO. If there is a discrepancy, go over each E-Tag ID and MW amount. - If an E-Tag can not be seen in WebTrans OR by the DC Tie Operator, work to resolve the problem OR ensure the E-Tag is curtailed to zero (0). WebTrans Reference Displays: Scheduling>QSE Summary Scheduling>BTF Display |
| 2 | Check out the Actual SCADA data values for the previous hour with the DC Tie Operator, SHARYLAND TO for the Railroad DC Tie. - If ERCOT’s actual values are different from the DC Tie Operator’s actual values by less than 10 MWH, overwrite the actual value in the WebTrans system with a whole number. - If ERCOT’s actual values are different from the DC Tie Operator’s actual values by 10 MWH or more and the reason is known (database load, loss of ICCP, etc.), overwrite the actual value in the WebTrans system. Log the appropriate information. - If ERCOT’s actual values are different from the DC Tie Operator’s actual values by 10 MWH or more and the reason is unknown; ERCOT and the DC Tie Operator will initiate an investigation. Log the appropriate information (time, date, total MW difference, DC Tie, name of the DC Tie Operator and any other relevant information). Open an ERCOT Help Desk ticket for EMMS Production to investigate problems with the meter information and notify Shift Supervisor. WebTrans Reference Displays: Scheduling>Inadvertent>Tie Data Scheduling>Interchange>ATF Checkout |
| 3 | After midnight, each day, check out the total scheduled and actual values for the Railroad DC Tie with the DC Tie Operator, SHARYLAND TO: IF: - Both parties agree on the Scheduled In and Out values and on the Actual In and Out values; THEN: - Prepare report for the DC_R - Select “[Tie name]” on the CA/Interface - Select “Schedule” on the “Checkout” dropdown - Check the bottom box on the totals row in Column C - Click the “Apply Checkout” button - Proceed to Step 5. WebTrans Reference Display: Scheduling>Interchange>ATF Checkout |
| 4 | If there is a disagreement on the total scheduled and/or actual values with the DC Tie Operator, verify the values for each hour as necessary to find the discrepancy. An effort should be made to work out all discrepancies. If the discrepancy is with the scheduled values: - Check the box in Column C for each hour that ERCOT is in agreement with the DC Tie Operator for the scheduled value. - Leave the box unchecked in Column C for each hour where there is a discrepancy with a scheduled value and it can not be worked out with the DC Tie Operator. - Click the “Apply Checkout” button. - Log the appropriate information and send email to shiftsupv@ercot.com. If the discrepancy is with an actual value, change the ERCOT value to match the DC Tie Operator’s value. WebTrans Reference Displays: Scheduling>Interchange>ATF Checkout Scheduling>Inadvertent>Tie Data |
| 5 | Create an Excel file for the DC-R Tie and email to the following (see Desktop Guide DC Tie Desk Section 2.9): - CENACE DC-Tie Inadvertent |

## 3.11	Managing Inadvertent Energy Payback

Procedure Purpose: To provide communication contacts and information prior to starting and ending inadvertent payback.

| Protocol Reference | 6.5.4 |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 2.8 (3) |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 6 | Effective Date: March 31, 2017 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | Payback will only be planned when there is room on the DC Tie(s). Energy schedules of market participants will supersede any inadvertent payback. |
| NOTE | When inadvertent needs to be paid back in either direction, the ERCOT Operator will receive the payback plan information from the Manager of System Operations and/or Control Room Operations Manager. |
| CENACE DC-Ties | - Prior to the start of the payback plan, call the appropriate DC Tie Operator and confirm the start time, hourly MW amount, and direction of the payback. - If payback is planned across the DC_L, verify the transmission path (230kV or 138kV) - Prior to the Payback plan stopping, call the appropriate entity and confirm the agreed upon stop time. |
| SPP DC-Ties | - Prior to the start of the payback plan, call the SPP Operator (SPP Tariff) and confirm the start time, hourly MW amount and direction of the payback |

## 4.1	Implement EEA Levels

Procedure Purpose: Steps to perform when ERCOT declares Energy Emergency Alert (EEA).

| Protocol Reference | 6.5.9.4.2 | 6.5.9.4.3 |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 2.1(3)(f) | 4.5.3(2) | 4.5.3.3 |  |
| NERC Standard | EOP-011-1 R2.1, R2.2.2, R2.2.3, R2.2.3.1, R2.2.7 | INT-006-4 R1.1 | INT-010-2.1 R2, R3 | IRO-001-4 R1 |
|  | TOP-001-3 R2 |  |  |  |

| Version: 1 | Revision: 21 | Effective Date: March 31, 2017 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Turret Phone | - The DC Tie Operator for the Laredo and Eagle Pass DC Ties can be reached using the Turret phone button labeled (AEP TO), page 4 - The DC Tie Operator for the Railroad DC Tie can be reached using the Turret phone button labeled (SHARYLAND TO), page 14 - AEP un-regulated QSE is responsible for assets associated with unregulated retail operations (SQ2, SQ3, and SQ4 sub-QSEs). The electronic Dispatch Instruction for emergency energy to and from CENACE will be given to this QSE. They can be reached using the Turret phone button labeled (AEP UNREG QSE), page 4 |
| EEA | When notified by Hotline that ERCOT has implemented EEA 1, proceed with this procedure. See Desktop Guide DC Tie Desk Section 2.8 for flow diagram. |
| ### DC-Ties with Centro Nacional de Control de Energia (CENACE) |  |
| 1 | This applies to the Laredo and Eagle Pass DC Ties: IF: - There are export schedules, OR - Export inadvertent payback flowing; THEN: - Curtail the export schedules (see Desktop Guide DC Tie Desk Section 2.3 or 2.4) CONTACT: - The DC-Tie Operator (AEP TO) Typical script (use what is applicable): This is ERCOT operator [first and last name]. Due to ERCOTs EEA status: - We have curtailed E-Tag(s) [tag number(s)] on the [DC Tie name] and request ramping the Tie(s) accordingly - We request the inadvertent payback on [DC-Tie] be ramped to zero - We request you inquire about the availability of emergency energy from CENACE. Please repeat this back to me. That is correct. Thank you.” |
| 2 | This applies to the Railroad DC-Tie: IF: - There are export schedules, OR - Export inadvertent payback flowing; THEN: - Curtail the export schedules (see Desktop Guide DC Tie Desk Section 2.3 or 2.4) CONTACT: - The DC-Tie Operator (SHARYLAND TO) Typical script (use what is applicable): This is ERCOT Operator [first and last name]. Due to ERCOTs EEA status: - We have curtailed E-Tag(s) [tag number(s)] and request ramping the Tie accordingly - We request the inadvertent payback be ramped to zero - We request you inquire about the availability of emergency energy from CENACE. Please repeat this back to me. That is correct. Thank you.” |
| Electronic Dispatch Instruction | IF: - AEP TO and/or Sharyland notifies ERCOT of available emergency energy; THEN: - Accept all available emergency energy - Notify the Shift Supervisor - Issue the electronic Dispatch Instruction as time permits AEP un-regulated QSE (AEP UNREG QSE): - Choose QSE level tab - Choose QAEPS2 for Participant Name - Choose PROVIDE EMERGENCY POWER FROM DC TIE for Instruction Type - State “Emergency Energy to ERCOT on [DC Tie(s)] in Other Information - Completion time will be the same as initiation time (back office will take care of the rest) Notify AEP un-regulated QSE (AEP UNREG QSE) that the electronic Dispatch Instruction has been issued. When issuing a VDI or confirmation, ensure the use of three-part communication. |
| 3 | This applies to the Laredo and Eagle Pass DC Ties: WHEN: - EEA has ended; THEN: - Notify the DC-Tie Operator (AEP TO) Typical script (use what is applicable): “This is ERCOT Operator [first and last name]. At [time], ERCOT has ended EEA 1. Thank you.” CONTACT: - The DC-Tie Operator (AEP TO) for the following as appropriate: - End emergency energy - Reload any E-Tag (see Desktop Guide DC Tie Section 2.5) - Re-start inadvertent payback |
| 4 | This applies to the Railroad DC-Tie: WHEN: - EEA has ended; THEN: - Notify the DC-Tie Operator (SHARYLAND TO) Typical script (use what is applicable): “This is ERCOT Operator [first and last name]. At [time], ERCOT has ended EEA 1. Thank you.” CONTACT: - The DC-Tie Operator (SHARYLAND TO) for the following as appropriate: - End emergency energy - Reload any E-Tag (see Desktop Guide DC Tie Section 2.5) - Re-start inadvertent payback |
| LOG | Log all actions taken. |
| ### DC-Ties with Southwest Power Pool (SPP) |  |
| Turret Phone | - SPP Reliability Coordinator can be reached using the Turret phone button labeled (SPP RC), page 2 - AEP regulated QSE is responsible for assets associated with regulated retail operations (Main and SQ1sub-QSE). The electronic Dispatch Instruction for emergency energy from SPP will be given to this QSE. They can be reached using the Turret phone button labeled (AEP REG QSE), page 4 |
| NOTE | For any EEA level, only hourly non-firm transmission service is available for the North and East DC Ties. Keep AEP informed so they can make the proper submittals hour to hour. |
| 1 | NOTIFY: - SPP Reliability Coordinator (SPP RC) of ERCOT’s EEA 1 status: Typical Script to SPP Reliability Coordinator (SPP RC): “This is ERCOT Operator [first and last name]. At [time], ERCOT declared EEA 1”. WHEN: - EEA status changes; THEN: - Notify SPP Reliability Coordinator (SPP RC) Typical Script to SPP Reliability Coordinator (SPP RC): “This is ERCOT Operator [first and last name]. At [time], ERCOT moved from EEA 1 to EEA 2. Thank you”. If moved to EEA 2 or 3 continue process above but with new levels. |
| 2 | IF: - There are export E-tags across the DC Ties (does not apply to DC_N schedules which are identified by “OKLA” in the Physical Path on the tag), OR - Export inadvertent payback flowing, OR - DC_N deadband is active and exporting; CONTACT: - The SPP Tariff Operator (SPP Tariff) Typical script (use what is applicable): This is ERCOT Operator [first and last name]. ERCOT is in EEA [level]: - We are curtailing E-Tag(s) [tag number(s)] and request that you ramp the Tie accordingly - We request the inadvertent payback be ramped to zero - If applicable, request the deadband on the North Tie be turned into ERCOT. Please repeat this back to me. That is correct. Thank you.” IF: - SPP provides a reliability reason for NOT approving the curtailing of the E-Tag(s); THEN: - Do not proceed with curtailments - Notify the Shift Supervisor - Make a log entry IF: - SPP approves; THEN: - Curtail the export schedules (usually done one hour at a time) (see Desktop Guide DC Tie Desk Section 2.3 or 2.4) |
| 3 | IF: - The SPP DC Ties are not at maximum import into ERCOT; THEN: - Notify the AEP regulated QSE (AEP REG QSE) to request emergency energy. Typical Script to AEP (AEP REG QSE): “This is ERCOT Operator [first and last name]. At [time], ERCOT declared EEA [state level]. Can AEP assist ERCOT with transmission service and energy on either available DC Tie?” NOTE: AEP will have to request the transmission service and energy first before they will know if it is available. SPP will approve if both services are available. IF: - Not approved; THEN: - Do NOT proceed and make log entry - Notify Shift Supervisor |
| Electronic Dispatch Instruction | IF: - AEP notifies ERCOT of available emergency energy THEN: - Accept all available emergency energy - Notify the Shift Supervisor - Approve the E-Tag - Issue electronic Dispatch Instruction as time permits AEP REG QSE: - Choose QSE level tab - Choose QAEPSC for Participant Name - Choose PROVIDE EMERGENCY POWER FROM DC TIE for Instruction Type - State “Emergency into ERCOT” and which DC Tie(s) in Other Information - Completion time will be the same as initiation time (back office will take care of the rest) Notify AEP regulated QSE (AEP REG QSE) that the electronic Dispatch Instruction has been issued. When issuing a VDI or confirmation, ensure the use of three-part communication. |
| 4 | WHEN: - EEA has ended; THEN: - Notify SPP Reliability Coordinator (SPP RC) Typical Script to SPP Reliability Coordinator (SPP RC): “This is ERCOT Operator [first and last name]. At [time], ERCOT has ended EEA 1. Thank you.” CONTACT: - The SPP Tariff Operator (SPP Tariff) for the following as appropriate: - End emergency energy - Reload any E-Tag (see Desktop Guide DC Tie Section 2.5) - Re-start inadvertent payback - If applicable, have deadband turned back into SPP |
| LOG | Log all actions taken. |

## 4.2	Emergency Energy to CENACE

Procedure Purpose: Provide Emergency Energy to CENACE across the DC Ties.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | INT-006-4 R3 |  |  |  |

| Version: 1 | Revision: 18 | Effective Date: March 31, 2017 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | If CENACE requests emergency energy, no emergency notification needs to be declared by ERCOT. See Desktop Guide DC Tie Desk Section 2.8 for flow diagram. |
| 1 | If notified by the ERCOT Transmission & Security Operator or a DC Tie Operator(AEP TO or SHARYLAND) of a request from CENACE for emergency energy across a specific DC-Tie: IF: - There are import schedules, OR - Import inadvertent payback flowing; THEN: - Curtail the import schedules (see Desktop Guide DC Tie Section 2.3 or 2.4) CONTACT: - The DC-Tie Operator (AEP TO or SHARYLAND) Typical script to appropriate DC Tie Operator (use what is applicable): This is ERCOT Operator [first and last name]. Due to CENACEs emergency status: - We have curtailed E-Tag(s) [tag number(s)] on the [DC tie name] - We request the inadvertent payback on [DC Tie] be ramped to zero - We [are able/not able] to send emergency energy on [DC Tie - If sending emergency energy, request the DC Tie be ramped to the agreed amount Please repeat this back to me. That is correct. Thank you.” |
| Electronic Dispatch Instruction | Issue to AEP un-regulated QSE (AEP UNREG QSE): - Choose QSE level tab - Choose QAEPS2 for Participant Name - Choose PROVIDE EMERGENCY POWER FROM DC TIE for Instruction Type - State “Emergency Energy to CENACE” and which DC Ties in “Other Information” - Completion time will be the same as initiation time. Notify AEP un-regulated QSE (AEP UNREG QSE) that electronic Dispatch Instruction has been issued. When issuing a VDI or confirmation, ensure the use of three-part communication. |
| 2 | WHEN: - Notified that CNACEs emergency has ended; THEN: - Perform/verify the following, if appropriate: - End emergency energy - Re-load E-Tag(s) (see Desktop Guide DC Tie Section 2.5) - Restart import inadvertent payback |
| Log | Log all actions taken. |

## 4.3	Emergency Condition in the Areas of the CENACE DC Ties

Procedure Purpose: The process to curtail E-Tags for the CENACE Ties and request emergency energy, if needed.

| Protocol Reference | 4.4.4(9) | 6.5.9.3.4(5) |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 2.8(2) |  |  |  |
| NERC Standard | EOP-011-1 R1.1, R1.2.4, R2.1, R.2.2.3.1 | IRO-001-4 R1 | TOP-001-3 R2 |  |

| Version: 1 | Revision: 22 | Effective Date: March 31, 2017 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Turret Phone | - The DC Tie Operator for the Laredo or Eagle Pass DC Ties can be reached using the Turret phone button labeled (AEP TO), page 4 - The DC Tie Operator for the Railroad DC Tie can be reached using the Turret Phone button labeled (SHARYLAND TO), page 14 - AEP un-regulated is the QSE receiving the VDI for emergency energy is issued to and from CENACE. They can be reached using the Turret phone button labeled (AEP UNREG QSE), page 4 |
| NOTE | DC Tie Load shall neither be curtailed during the Adjustment Period, nor for more than one hour at a time, except for the purpose of maintaining reliability. |
| NOTE | When ERCOT curtails an E-Tag whether to zero (0) or a specific MW amount, only CENACE needs to approve the change. Curtailments will be automatically approved by them. See Desktop Guide DC Tie Desk Section 2.8 for flow diagram. |
| ### Emergency Condition within ERCOT |  |
| 1 | When ERCOT is in an emergency, it may be necessary to curtail export E-Tags using the Last-in-First-Out (LIFO). IF: - Notified by the ERCOT Transmission & Security Operator of the need to curtail (which includes reductions) exports on a specific DC Tie; THEN: - Verify the MW amount the E-tag needs to be curtailed, - Curtail the appropriate E-Tag to the MW amount needed (see Desktop Guide DC Tie Section 2.3 or 2.4) - Notify the appropriate DC Tie Operator with curtailment information and instruct them to ramp the DC Tie and to notify CNACE - Notify PSE with curtailment information and reason. Typical script to appropriate DC Tie Operator: This is ERCOT Operator [first and last name]. ERCOT has curtailed E-Tag(s) [tag number(s)] on the [DC Tie name] to [state MW amount] starting at [xx:xx] due to an Emergency condition within ERCOT. Please ramp the Tie accordingly and notify CENACE. Please repeat this back to me. That is correct. Thank you.” |
| 2 | Once notified by the ERCOT Transmission & Security Operator that the E-Tags can be re-loaded: - Notify PSE with reload information - Re-load curtailed E-Tag(s) (see Desktop Guide DC Tie Section 2.5) - Notify the appropriate DC Tie Operator to approve the re-loaded E-Tag and instruct them to notify CENACE. Typical script to appropriate DC Tie Operator: This is ERCOT Operator [first and last name]. At [xx:xx], the Emergency conditions within ERCOT has ended and the E-Tag(s) [tag number(s)] have been re-loaded for [xx:xx]. Please notify CENACE to approve re-load. Please repeat this back to me. That is correct. Thank you.” |
| 3 | IF: - The re-loaded E-Tag(s) go passive deny because DC Tie Operator or CENACE did not approve the E-Tag(s) in the allotted time; THEN: - Re-load the E-Tag(s) again, AND - Notify appropriate DC Tie Operator. If reload fails the second time stop trying and keep tag curtailed. |
| 4 | IF: - Notified by the ERCOT Transmission & Security Operator there is need for emergency energy across a specific DC Tie; THEN: - Request the appropriate DC-Tie Operator to inquire about the availability of emergency energy on [name DC Tie(s)] Typical Script to appropriate DC Tie Operator: “This is ERCOT Operator [first and last name] At [xx:xx] ERCOT declared an Emergency, we are requesting you to contact CENACE to inquire about the availability of emergency energy into ERCOT on [name DC Tie(s)] IF: - Emergency energy is available; THEN: - Request the appropriate DC Tie Operator to ramp the appropriate DC Tie(s) with the amount of emergency energy that CENACE is able to send, - Issue electronic Dispatch Instruction IF: - Emergency energy is not available; THEN: - Notify ERCOT Transmission & Security Operator |
| 5 | Issue VDI to AEP un-regulated QSE (AEP UNREG QSE) for the emergency energy: - Choose QSE level tab - Choose QAEPS2 for Participant Name - Choose PROVIDE EMERGENCY POWER FROM DC TIE for Instruction Type - State “Emergency Energy to ERCOT on [DC Tie(s)] in Other Information - Completion time will be the same as initiation time (back office will take care of rest) Notify AEP un-regulated QSE (AEP UNREG QSE) that the electronic Dispatch Instruction has been issued. When issuing a VDI or confirmation, ensure the use of three-part communication. |
| LOG | Log all actions taken. |
| ### Emergency Condition within CENACE |  |
| NOTE | On the CENACE side of the Railroad DC Tie, there is an automatic runback scheme that runs back the DC Tie under CENACE contingency conditions. When this occurs, and notification is made by the DC Tie Operator; follow the procedure below. |
| 1 | Due to reliability issues within CENACE it may be necessary to curtail import E-Tag(s) for them. IF: - Notified by the ERCOT Transmission & Security Operator or one of the DC Tie Operators of the need to curtail imports on specific CENACE DC Ties; THEN: - Verify the MW amount and time of the curtailment, - Curtail the appropriate E-Tag to the MW amount needed (see Desktop Guide DC Tie Section 2.3 or 2.4), - Contact the appropriate DC Tie Operator when curtailment is complete and instruct them to ramp the DC Tie and make notification to CENACE - Notify PSE with curtailment information and reason. Typical script to appropriate DC Tie Operator: This is ERCOT Operator [first and last name]. At [xx:xx] ERCOT has curtailed E-Tag [tag number] on the [DC Tie name] to [state MW amount] due to reliability issues within CENACE. Please ramp the Tie accordingly and notify CENACE. Please repeat this back to me. That is correct. Thank you.” |
| 2 | Once notified that CENACEs reliability issue has been resolved and E-Tags can be re-loaded: - Notify PSE with reload information - Re-load curtailed E-Tag(s) (see Desktop Guide DC Tie Desk Section 2.5), - Notify the appropriate DC Tie Operator to approve the re-loaded E-Tag and to notify CENACE. |
| 3 | IF: - The re-loaded E-Tag goes passive deny because a DC Tie Operator or CENACE did not approve the E-Tag in the allotted time; THEN: - Re-load the E-Tag again, AND - Notify the appropriate DC Tie Operator. If reload fails the second time stop trying and keep tag curtailed. |
| 4 | IF: - Notified by the ERCOT Transmission & Security Operator of the need for emergency energy; THEN: - Proceed and follow step 3 in section 4.2, Emergency Energy to CENACE. |
| LOG | Log all actions taken. |

## 4.6	Market Notifications

Procedure Purpose: Guidelines for issuing Emergency Conditions and the four possible levels: Operating Condition Notices (OCN), Advisories, Watches, and Emergency Notices.

| Protocol Reference | 6.3.3 | 6.3.3 | 6.5.9.3.1 | 6.5.9.3.2 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.3.3 | 6.5.9.3.4 |  |  |
| Guide Reference | 4.2.1 | 4.2.2 | 4.2.3 | 4.2.4 |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 18 | Effective Date: March 31, 2017 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### OCN |  |
| NOTE | Consider the severity of the potential Emergency Condition. The severity of the Emergency Condition could be limited to an isolated local area, or the condition might cover large areas affecting several entities, or the condition might be an ERCOT-wide condition potentially affecting the entire ERCOT System. |
| 1 | As directed by the Shift Supervisor or when appropriate, issue an Operating Condition Notice (OCN). The OCN can be issued for any of the following reasons or to obtain additional information from TOs and/or QSEs. - There is a projected reserve capacity shortage that could affect reliability and may require more Resources - When extreme cold weather is forecasted approximately 5 days away - When extreme hot weather is forecasted approximately 5 days away - When an approaching Hurricane / Tropical Storm is approximately 5 days away - Unplanned transmission Outages that may impact System reliability - When adverse weather conditions are expected, ERCOT may confer with TOs and QSEs regarding the potential for adverse reliability impacts and contingency preparedness. |
| ### ADVISORY |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue an Advisory. The Advisory can be issued for any of the following reasons or to obtain additional information from Market Participants. - When an approaching Hurricane / Tropical Storm is approximately 3 days away - When extreme cold weather is forecasted approximately 3 days away - When extreme hot weather is forecasted approximately 1 to 3 days away - When conditions are developing or have changed and more Ancillary Services will be needed to maintain current or near-term reliability - ERCOT may exercise its authority to increase Ancillary Service requirements above the quantities originally specified in the Day-Ahead Market in accordance with ERCOT procedures. - When extreme weather or conditions require more lead-time than the normal Day-Ahead Market allows. - Transmission system conditions are such that operations within security criteria are not likely or possible because of Forced Outages or other conditions unless a CMP exists - Loss of communications or control condition is anticipated or significantly limited - ERCOT may require information from QSEs representing Resources regarding the Resources’ fuel capabilities. Requests for this type of information shall be for a time period of no more than seven days from the date of the request |
| ### WATCH |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue a Watch. The Watch can be issued for any of the following reasons or to obtain additional information from Market Participants. - A projected reserve capacity shortage is projected with no market solution available that could affect reliability - When an approaching Hurricane / Tropical Storm is approximately 1 day away - When extreme cold weather is projected for next day or current day - When extreme hot weather is projected for next day or current day - Conditions have developed such that additional Ancillary Services are needed in the Operating Period - Insufficient Ancillary Services or Energy Offers in the DAM - Market-based congestion management techniques embedded in SCED will not be adequate to resolve transmission security violations - Forced Outages or other abnormal operating conditions have occurred, or may occur that would require ERCOT to operate with active violations of security criteria as defined in the Operating Guides unless a CMP exists - The SCED process fails to reach a solution, whether or not ERCOT is using one of the measures in Failure of the SCED Process. - The need to immediately procure Ancillary Services from existing offers - ERCOT may instruct TOs to reconfigure transmission elements as necessary to improve the reliability of the system - ERCOT may require information from QSEs representing Resources regarding the Resources’ fuel capabilities. Requests for this type of information shall be for a time period of no more than seven days from the date of the request |
| ### EMERGENCY NOTICE |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue an Emergency Notice. The Emergency Notice can be issued for any of the following reasons or to obtain additional information from Market Participants. - Loss of Primary Control Center functionality - Load Resource deployment for North-Houston voltage stability - ERCOT cannot maintain minimum reliability standards (for reasons including fuel shortages) during the Operating Period using every Resource practically obtainable from the market - Immediate action cannot be taken to avoid or relieve a Transmission Element operating above its Emergency Rating - ERCOT forecasts an inability to meet applicable Reliability Standards and it has exercised all other reasonable options - A transmission condition has been identified that requires emergency energy from any of the DC Ties or curtailment of schedules - The Transmission Grid is such that a violation of security criteria as defined in the Operating Guides presents the threat of uncontrolled separation or cascading outages, large-scale service disruption to load (other than Load being served from a radial transmission line) and/or overload of Transmission Elements and no timely solution is obtainable through SCED or CMPs - When extreme cold weather is beginning to have an adverse impact on the System - When extreme hot weather is beginning to have an adverse impact on the System - When Hurricane / Tropical Storm is in the ERCOT Region and is beginning to have an adverse impact on the System |
| ### Notifications |  |
| HOTLINE | Notify QSEs of Notice Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing a [state Notice type] for [state reason]. [QSE] please repeat this back to me. That is correct, thank you.” Notify TOs of Notice Typical script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing a [state Notice type] for [state reason]. [TO] please repeat this back to me. That is correct, thank you.” All Operating Instructions shall be in a clear, concise, and definitive manner. Ensure the recipient of the instruction repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| POST | - All notices must be posted on MIS Public using Notice Builder. - For “free form” messages, the only option is “public” - For “free form” messages, the “Notice priority” will be specified as follows: - Operational Information/OCN type messages – low priority - Advisory/Watch type messages – medium priority - Emergency type messages – high priority |
| Hotline Cancellation | Typical Hotline Script cancellation: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is cancelling the [state Notice type] for [state reason]. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| LOG | Make log entry. |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Frosch, Hartmann, Stone, and Barcalow | Preparers | November 10, 2010 |
| Frosch and Hartmann | Procedure writers and editors | November 27, 2010 |
| Frosch and Hartmann | Procedure writers and editors | January 26, 2011 |
| Frosch and Hartmann | Procedure writers and editors | March 23, 2011 |
| Frosch and Hartmann | Procedure writers and editors | April 20, 2011 |
| Frosch and Hartmann | Procedure writers and editors | June 6, 2011 |
| Frosch and Hartmann | Procedure writers and editors | June 16, 2011 |
| Frosch and Hartmann | Procedure writers and editors | July 18, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 30, 2011 |
| Frosch and Hartmann | Procedure writers and editors | September 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | October 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 16, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | April 25, 2012 |
| Frosch and Hartmann | Procedure writers and editors | July 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | August 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | October 26, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 26, 2013 |
| Frosch and Hartmann | Procedure writers and editors | May 28, 2013 |
| Frosch and Hartmann | Procedure writers and editors | June 27, 2013 |
| Frosch and Hartmann | Procedure writers and editors | July 9, 2013 |
| Frosch and Hartmann | Procedure writers and editors | August 28, 2013 |
| Frosch and Hartmann | Procedure writers and editors | December 11, 2013 |
| Frosch and Hartmann | Procedure writers and editors | January 27, 2014 |
| Frosch and Hartmann | Procedure writers and editors | February 18, 2014 |
| Frosch and Hartmann | Procedure writers and editors | February 26, 2014 |
| Frosch, Gaddy and Hartmann | Procedure writers and editors | April 1, 2014 |
| Frosch, Gaddy and Hartmann | Procedure writers and editors | May 27, 2014 |
| Frosch, Gaddy and Hartmann | Procedure writers and editors | July 27, 2014 |
| Frosch and Hartmann | Procedure writers and editors | September 29, 2014 |
| Frosch Hartmann and Lopez | Procedure writers and editors | December 10, 2014 |
| Frosch and Hartmann | Procedure writers and editors | February 25, 2015 |
| Frosch and Hartmann | Procedure writers and editors | April 29, 2015 |
| Frosch, Hartmann and Gaddy | Procedure writers and editors | July 13, 2015 |
| Hartmann and Gaddy | Procedure writers and editors | December 22, 2015 |
| Hartmann, Gaddy and Frosch | Procedure writers and editors | February 23, 2016 |
| Hartmann, Gaddy and Frosch | Procedure writers and editors | April 22, 2016 |
| Hartmann, Gaddy and Frosch | Procedure writers and editors | June 24, 2016 |
| Hartmann and Gaddy | Procedure writers and editors | September 26, 2016 |
| Hartmann and Gaddy | Procedure writers and editors | October 31, 2016 |
| Hartmann and Gaddy | Procedure writers and editors | December 23, 2016 |
| Hartmann, Gaddy and Frosch | Procedure writers and editors | March 27, 2017 |

Manual Change History

| Procedure | Ver/Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All Sections | 1.0 / 0 | New procedures for all sections for Nodal implementation | November 30, 2010 |
| 3.1 3.3 3.12 3.13 3.14 3.16 3.17 4.1 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Updated step 1 Updated step 1 Updated step 1 and added Log Updated step 4 Updated step 3 Updated step 1 and added Log Updated step 3 Updated Constant Frequency, Respond to QSE’s, Stability Limits Reached and Thermal Limits Reached | December 1, 2010 |
| 2.3 3.4 4.1 4.2 4.3 | 1.0 / 0 1.0 / 1 1.0 / 2 1.0 / 1 1.0 / 1 | Added new procedure Updated step 1 Updated steps “Constant Frequency”, “QSE Hotline Call”, “TO Hotline Call”, “Respond to QSEs” “Respond to TOs”, “Stability Limits” and added “Nuclear Plants” Updated Note and “Additional Operators” Updated Hotline in “Notifications” | January 31, 2011 |
| 2.3 3.1 3.2 3.3 3.7 4.1 4.2 4.3 4.4 4.5 4.6 4.7 4.8 4.9 | 1.0 / 1 1.0 / 2 1.0 / 1 1.0 / 2 1.0 / 1 - / 2 1.0 / 2 - / 2 1.0 / 1 1.0 / 2 1.0 / 2 1.0 / 3 - / 2 1.0 / 2 | Updated NXT Test Updated 4th Note and step 1 Updated step 2 Updated 5th note, step 1, deleted step 4 and 6th Note Updated all sections Section number changed from 3.12 and updated all steps Section number changed from 3.13 and updated all steps Section number changed from 3.14 and updated all steps Section number changed from 3.15 and updated all steps Section number changed from 3.16 and updated step 1 Section number changed from 3.17 and updated step 1 Section number changed from 4.1 & updated multiple steps Section number changed from 4.2 & Note Section number changed from 4.3 | March 25, 2011 |
| 1.1 2.3 3.1 3.2 3.3 3.4 3.5 3.6 3.7 3.8 3.9 3.10 4.1 4.2 4.3 4.4 4.5 4.6 4.7 4.9 | 1.0 / 1 1.0 / 2 1.0 / 3 1.0 / 2 1.0 / 3 1.0 / 2 1.0 / 1 1.0 / 1 - / 2 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 3 1.0 / 3 1.0 / 3 1.0 / 2 1.0 / 3 1.0 / 3 1.0 / 4 1.0 / 3 | Updated text Updated step “Beginning of each Shift” Updated 1st & 3rd note and step 1, deleted 2nd note and added 5th note Updated 1st note and step 2 Updated 1st & 4th note, step 1 & 2, deleted 2nd and added 5th note Updated 1st & step 1 Updated steps 1, 2 and 3 Updated “Import” step 1 and “Export” steps 1 & 2 Updated all sections Updated all sections Updated all sections Updated 1st & 2nd note and step 1 and 2 Updated 1st note and step 1 Updated 1st note Updated 1st note Updated step 3 Updated step 1 Updated step 2 Updated step QSE Hotline Call Updated step 1 in Watch and Emergency Notice | April 22, 2011 |
| 3.1 3.2 3.3 3.4 3.5 3.6 3.73.8 3.9 3.10 3.11 4.1 4.2 4.3 4.4 4.5 4.6 4.7 4.9 | 1.0 / 4 1.0 / 3 1.0 / 4 1.0 / 3 1.0 / 2 1.0 / 2 1.0 / 31.0 / 2 1.0 / 1 1.0 / 2 1.0 / 1 1.0 / 4 1.0 / 4 1.0 / 3 1.0 / 3 1.0 / 4 1.0 / 4 - / 5 1.0 / 4 | Updated all steps Updated all steps Updated all steps Updated step 1 Updated step 1, 2, 3 & added 2nd note Updated step 1 and 2 Updated all steps Updated all steps Updated all steps Updated 3rd note and step 1 Updated all steps Updated all steps Updated all steps Updated all steps Updated all steps Updated step 1 Updated steps 2 & 3 Updated steps Call in Additional Operators and Respond to QSEs Updated all steps | June 8, 2011 |
| 3.1 3.3 3.7 3.9 4.2 | 1.0 / 5 1.0 / 5 1.0 / 4 1.0 / 2 1.0 / 5 | Changed 3rd Note to step 1, updated step 1 & 2 Updated step 1 Updated all steps in DC Tie Trips, step 1 in Transmission Issues within ERCOT & step 1 & 2 in Transmission Issues within CFE Updated webtrans references Updated step 1 | June 17, 2011 |
| 3.1 3.3 3.6 3.7 3.9 3.11 4.1 4.2 4.3 4.4 4.5 4.6 4.7 4.8 | 1.0 / 6 1.0 / 6 1.0 / 3 1.0 / 5 1.0 / 3 1.0 / 2 1.0 / 6 1.0 / 4 1.0 / 5 1.0 / 5 1.0 / 5 1.0 / 5 1.0 / 2 1.0 / 5 | Updated 1st Note and step 1 & 2 Updated step 1 Updated all steps Split procedure out, changed title and moved Transmission Issue within ERCOT to 4.5 Updated step 2 Updated steps 2, 4 and 5 Updated step 1, added steps 2 - 4 Updated all steps, added new step 3 Updated Turret phone label for SPP Tariff and all steps Changed section number from 4.4 to 4.3 and updated all steps Changed section number from 4.5 to 4.4 and updated all steps Changed section number from 4.6 to 4.5, updated all steps and moved Transmission Issues from 3.7 to 4.5 Changed section number from 4.7 to 4.6 Changed section number from 4.8 to 4.7 Changed section number from 4.9 to 4.8 and updated step 1 in Watch | July 20, 2011 |
| 2.3 3.1 3.2 3.3 3.6 3.7 3.8 3.9 3.11 4.1 4.2 4.3 4.5 4.6 4.8 | 1.0 / 3 1.0 / 7 1.0 / 4 1.0 / 7 1.0 / 4 1.0 / 6 1.0 / 3 1.0 / 4 1.0 / 3 1.0 / 7 1.0 / 5 1.0 / 6 1.0 / 6 1.0 / 6 1.0 / 6 | Updated step “Beginning of each Shift” Updated 1st note Updated steps 1, 2 & 3 Updated 1st, 4th note and step 1 Updated step 1 “Imports” and step 2 “Exports” Updated Steps 1, 2 and 4 in “CFE DC-Ties” Updated 2nd note and steps 1-3 Updated steps 1-3 Updated steps 1 and 2 Updated all steps Updated all steps Updated all steps Updated all steps Removed reference of Austin Control Room Added projected reserve capacity shortage and Extreme Hot Weather in Watch | September 1, 2011 |
| 3.1 3.3 4.1 4.2 4.3 | 1.0 / 8 1.0 / 8 1.0 / 8 1.0 / 6 1.0 / 7 | Updated step 2 Updated step 1 Updated Turret Phone, step 3a in Comision Federal de Electricidad (CFE) and step 5b to implement NPRR 379 Updated Turret Phone and step 3a in Comision Federal de Electricidad (CFE) Updated step 3 | October 1, 2011 |
| 4.6 | 1.0 / 7 | Updated step TO Hotline Call | November 1, 2011 |
| 3.1 3.3 4.6 4.8 | - / 9 1.0 / 9 1.0 / 8 1.0 / 7 | Updated step 2 Updated step 1 Added new section and updated all steps Updated Post in “Notifications” All procedures in this manual have been reviewed. | December 15, 2011 |
| 1.2 3.1 3.3 4.6 | 1.0 / 1 1.0 / 10 1.0 / 10 1.0 / 9 | Updated Scope Updated step 2 Updated step 1 Updated Hotline call scripts | January 19, 2012 |
| 2.1 2.3 3.1 3.2 3.7 4.1 4.2 4.3 4.5 4.8 | 1.0 / 1 1.0 / 4 1.0 / 11 1.0 / 5 1.0 / 7 1.0 / 9 1.0 / 7 1.0 / 8 1.0 / 7 1.0 / 8 | Added dispatch instructions paragraph Updated Desktop Guide reference Added 3rd Note Changed Shift Engineer to Operations Support Updated Desktop Guide references Updated Desktop Guide references Updated Desktop Guide references Updated Desktop Guide references Updated 2nd Note & all steps 1 – 3 Updated step 1 of Watch | March 1, 2012 |
| 3.1 3.3 3.7 3.8 3.9 4.54.6 4.8 | 1.0 / 12 1.0 / 11 1.0 / 8 1.0 / 4 1.0 / 5 1.0 / 8 1.0 / 10 1.0 / 9 | Updated step 2 Updated 3rd Note and step 1 Added posting and cancelling messages Updated overview Updated overview Updated procedure based on NPRR405 Updated W-N or N-H steps Updated OCN, Advisory, Watch and Emergency Notice for Cold Weather and Extreme Cold Weather | May 1, 2012 |
| 1.3 3.2 3.8 3.9 4.5 4.6 4.8 | 1.0 / 1 1.0 / 6 1.0 / 5 1.0 / 6 1.0 / 9 1.0 / 11 1.0 / 10 | Removed ERCOT Shift Supervisor paragraph Updated step 1 Updated step 4 Updated step 4 Added step Turret Phone & 1st Note, updated step 4 Updated several steps based on lessons learned from classroom training and simulation Updated all step 1’s | July 16, 2012 |
| 3.1 | 1.0 / 13 | Updated step 2 | August 29, 2012 |
| 2.2 3.2 4.5 4.6 | 1.0 / 1 1.0 / 7 1.0 / 10 1.0 / 12 | Added Hotline Call Communication Updated 1st Note Updated 1st and 2nd Note Updated steps West to North & North to Houston(IROL) All procedures in this manual have been reviewed. | November 1, 2012 |
| 3.1 3.10 4.6 | 1.0 / 14 1.0 / 3 1.0 / 13 | Updated step 2 Updated 2nd note Updated Additional Notifications on Systems Functional and Systems are not Functional | March 1, 2013 |
| 3.1 3.2 3.7 3.11 4.6 | 1.0 / 15 1.0 / 8 1.0 / 9 1.0 / 4 1.0 / 14 | Updated step 2 Updated step 1, deleted steps 2 & 3 Updated scripts Updated script Updated scripts, West to North & step North to Houston | June 1, 2013 |
| 3.6 4.3 4.4 4.5 4.6 | 1.0 / 5 1.0 / 9 1.0 / 6 1.0 / 11 1.0 / 15 | Updated Exports, step 1 Updated step 1 & 3 Updated step 1 Deleted 2nd Note, updated step 1, 2 & 4 Added Monitor Frequency and updated Constant Frequency | July 1, 2013 |
| 3.1 3.3 3.11 4.8 | 1.0 / 16 1.0 / 12 1.0 / 5 1.0 / 11 | Updated step 1 Updated 4th note Updated step 1 Updated step 1 in Watch & Emergency Notice | July 15, 2013 |
| 3.7 4.6 | 1.0 / 10 1.0 / 16 | Added CFE DC-Tie Derates and AEP DC-Tie Derates Removed HHGT TO reference | August 30, 2013 |
| 1.1 3.3 3.4 3.5 3.6 3.8 3.9 3.11 4.1 4.2 4.5 | 1.0 / 2 1.0 / 13 1.0 / 4 1.0 / 3 1.0 / 6 1.0 / 6 1.0 / 7 1.0 / 6 1.0 / 10 1.0 / 8 1.0 / 12 | Changed “Security” to “Reliability” Updated step 2 Updated both steps Updated last Note and step 3 Updated the Notes and step 1 and 2 Updated step 2 Updated step 2 New Loss of DC-Tie Operator E-tagging Updated step 6b Updated step 6b Added note to Transmission Issues within CFE All procedures in this manual have been reviewed. | December 13, 2013 |
| 3.8 4.1 4.2 4.3 4.4 4.5 4.8 | 1.0 / 7 1.0 / 11 1.0 / 9 1.0 / 10 1.0 / 7 1.0 / 13 1.0 / 13 | Updated step 2 Updated step Turret Phone, 3a, 6b, Note, & 7b Updated step Turret Phone, 3a, 6b, Note, & 7b Updated step 3 Updated step 2 Updated step Turret Phone & 4 Updated all step 1’s | January 29, 2014 |
| 3.3 3.6 3.7 3.9 3.10 3.11 3.12 4.1 4.2 4.3 4.5 | 1.0 / 14 1.0 / 7 1.0 / 11 1.0 / 8 1.0 / 0 1.0 / 4 1.0 / 7 1.0 / 12 1.0 / 10 1.0 / 11 1.0 / 14 | Updated 1st & 4th Note & step 1 to include Sharyland as Tie Operator Updated steps 1 & 2 Updated steps 1, 2, 3 & Cancel Message Updated 1st Note, step 2, 3 & 5 New procedure Updated section number Updated section number & step 2 Updated Turret Phone, 1st Note, CFE & SPP sections Updated Turret Phone, 1st Note, CFE & SPP sections Updated 1st None, steps 1, 2 & 3 Updated to include Sharyland change | February 25, 2014 |
| 3.1 3.4 3.5 3.7 3.8 3.9 3.10 3.11 3.12 4.1 4.24.3 4.4 4.5 4.6 4.7 4.8 | 1.0 / 17 1.0 / 5 1.0 / 4 1.0 / 12 1.0 / 8 1.0 / 9 1.0 / 1 1.0 / 5 - / 8 - / 13 - / 11 1.0 / 12 1.0 / 7 1.0 / 15 1.0 / 17 1.0 / 3 1.0 / 14 | Updated 1st Note Updated step 1 Updated steps 2 and 3 Updated step Post Message Updated steps Note through 5 Updated step 5 Updated step 5 Updated 1st Note, steps 1 to CFE DC-Ties and 2 to SPP DC-Ties Updated steps 2, 4 & 5 on Loss of ERCOT E-Tagging and step 1 on Loss of DC Tie Operator E-Tagging Updated steps Turret Phone, Note, 2b, 3b, 4b & 6b on Southwest Power Pool (SPP) Deleted ERCOT Declares EEA 2 or 3 Re-numbered procedure to 4.2 Delete Emergency Energy to SPP procedures Re-numbered procedure to 4.3 Re-numbered procedure to 4.4 Re-numbered procedure to 4.5 Re-numbered procedure to 4.6 | March 1, 2014 |
| 3.1 3.2 4.1 4.2 4.3 4.4 | 1.0 / 18 1.0 / 9 1.0 / 14 - / 13 - / 16 - / 18 | Updated step 2 Updated step 1 & 2 Updated VDI information Updated VDI information Updated VDI information Updated VDI information & Updated Guide Reference | April 4, 2014 |
| 2.2 3.1 3.3 3.8 3.9 3.10 4.1 4.6 | 1.0 / 2 1.0 / 19 1.0 / 15 1.0 / 9 1.0 / 10 1.0 / 2 1.0 / 15 1.0 / 15 | Added VDIs to Master QSEs Updated step 2 Updated step 1 Updated Monitor, deleted step Caution & added step 5 Updated Monitor & deleted step Caution Updated Monitor & deleted step Caution Updated title Added Note, updated Advisory & Watch | June 1, 2014 |
| 3.1 3.3 3.8 4.3 | 1.0 / 20 1.0 / 16 1.0 / 10 1.0 / 17 | Updated step 2 Updated step 1 & 2 Updated 2nd Note Updated step 4 in Emergency Condition within CFE | August 1, 2014 |
| 3.1 3.3 4.2 4.3 4.6 | 1.0 / 21 1.0 / 17 1.0 / 14 1.0 / 18 1.0 / 16 | Updated step 2 Updated step 1 Spilt step 3 into two steps for clarification Spilt step 4 into two steps for clarification Updated Generic Script | October 1, 2014 |
| 3.8 3.9 3.10 4.1 4.2 4.3 4.4 | 1.0 / 11 1.0 / 11 1.0 / 3 1.0 / 16 1.0 / 15 1.0 / 19 1.0 / 19 | Updated step 6 Updated step 5 Updated step 5 Updated step EEA Updated step Note Updated step 2nd Note Updated TO scripts, delete W-Ns & revised GTLs All procedures in this manual have been reviewed | December 15, 2014 |
| 2.2 3.8 4.1 4.2 4.3 4.4 | 1.0 / 3 1.0 / 12 1.0 / 17 1.0 / 16 1.0 / 20 1.0 / 20 | Added Dispatch and VDI definition Correction to step 5 Reformatted section Reformatted section Corrected VDI/Dispatch Instruction language Reformatted section | March 1, 2015 |
| 3.8 4.1 4.4 | 1.0 / 13 1.0 / 18 1.0 / 21 | Correction to step 2 Updated step 2 & 4 on DC-Ties with Southwest Power Pool (SPP) Updated GTL to new term GTC | May 1, 2015 |
| 3.1 3.3 | 1.0 / 22 1.0 / 18 | Updated step 2 Updated 4th Note and step 1 | July 15, 2015 |
| 4.1 | 1.0 / 19 | Added step 3, 4, and Log to DC-Ties with Comisión Federal de Electricidad (CFE) All procedures in this manual have been reviewed | December 31, 2015 |
| 1.3 2.1 | 1.0 / 2 1.0 / 2 | Removed Interchange Coordinator Updated System Operator Resonsibility and Authority | March 1, 2016 |
| 3.1 3.2 3.3 3.4 3.5 | 1.0 / 23 1.0 / 10 1.0 / 19 1.0 / 6 1.0 / 5 | Added Note 4 Updated steps 1, 2 & 3 Added Note 4, & renumbered steps Updated step 1 Updated steps 1, 2 & 3, deleted 2nd Note | April 29, 2016 |
| 2.1 2.2 4.1 4.2 4.3 4.4 4.6 | 1.0 / 3 1.0 / 4 1.0 / 20 1.0 / 17 1.0 / 21 1.0 / 22 1.0 / 17 | Updated for COM-002-4 Updated for COM-002-4 Updated for COM-002-4 Updated Step Electronic Dispatch Instruction Updated for COM-002-4 Updated Step Electronic Dispatch Instruction Updated for COM-002-4 Updated Step Electronic Dispatch Instruction Updated for COM-002-4 Updated for COM-002-4 | June 30, 2016 |
| 3.2 3.3 3.6 3.12 | 1.0 / 11 1.0 / 20 1.0 / 8 1.0 / 9 | Updated Note, Step 1 and Step 2. Removed Step 3 Updated Step 2 Updated Exports Step 1 Moved Exports step 2 to step 3 Added Exports Step 2 Updated Step 3 | September 30, 2016 |
| 3.2 3.3 | 1.0 / 12 1.0 / 21 | Updated Procedure Purpose Updated step Note Added step Adjustment Period Updated step 1 & 2 Updated step 2 | November 2, 2016 |
|  |  | All procedures in this manual have been reviewed | December 30, 2016 |
| 1.3 2.1 2.3 3.2 3.3 3.6 3.7 3.9 3.10 3.11 4.1 4.2 4.3 4.6 | 1.0 / 3 1.0 / 4 1.0 / 5 1.0 / 13 1.0 / 22 1.0 / 9 1.0 / 13 1.0 / 12 1.0 / 4 1.0 / 6 1.0 / 21 1.0 / 18 1.0 / 22 1.0 / 18 | Deleted section 1.3 Updated for IRO-001-4 Updated step NXT Updated CFE to CENACE Updated CFE to CENACE Updated CFE to CENACE Updated CFE to CENACE Updated CFE to CENACE Updated CFE to CENACE Updated CFE to CENACE Updated CFE to CENACE Updated CFE to CENACE Updated CFE to CENACE Updated heading title and OCN step 1 | March 31, 2017 |