- Power Operations Bulletin # 777

ERCOT has posted/revised the Shift Supervisor Desk manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

- http://www.ercot.com/mktrules/guides/procedures/index.html

## 2.1	System Operator Responsibility and Authority

Procedure Purpose: To ensure the System Operators know their roles, responsibility and authority.

| Protocol Reference | 6.5.1.1 | 6.5.1.2(3) | 6.5.2 | 6.5.3(1) |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.5.2(1) |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 5 | Effective Date: March 31, 2017 |
| --- | --- | --- |

ERCOT ISO as a Transmission Operator (TOP), the single Balancing Authority (BA), and only Reliability Coordinator (RC) registered within the ERCOT Interconnection shares all information between these roles simultaneously and acts concurrently as a single entity, satisfying coordination between the TOP, BA and RC.

The System Operator (SO) shall, in accordance with NERC Reliability Standards and ERCOT Protocols, have clear decision-making authority to act to address the reliability of its Reliability Coordinator Area by direct actions or by issuing Operating Instructions during both normal and emergency conditions.  These actions shall be taken without delay and may include shedding of firm load without obtaining approval from higher-level personnel.

- The SO on duty is, in accordance with the ERCOT Protocols, Operating Guides, and NERC Reliability Standards, and acting as the Balancing Authority, Transmission Operator, and Reliability Coordinator shall request and receive information required to continually monitor the operating conditions  which will assure security and reliability of the ERCOT system.

- The SO issues Dispatch Instructions / Operating Instructions for the Real-Time operation of Transmission Facilities to a TO, and to a QSE for the Real-Time operation of a Resource.

- The SO shall, on an ERCOT-wide basis, coordinate the ERCOT System Restoration (Black Start) Plan.  The SO shall implement the Black Start Plan and shall direct the reconnection efforts of the islands, established by restoration activities.

- The SO shall consider all equipment operating limits when issuing Dispatch Instructions / Operating Instructions.  During Emergency Conditions, the SO may verbally request QSEs to operate its Resources outside normal operating parameters. If a Dispatch Instruction conflicts with a restriction placed on equipment by a TO or QSE to protect the integrity of equipment, ERCOT shall honor the restriction.

- The SO performs security analyses on a Day Ahead and real-time basis and ensures all Forced Outages are entered into the Outage Scheduler. The SO shall obtain or arrange to provide emergency energy over the DC Tie(s) on behalf of ERCOT.

- The SO shall issue appropriate OCNs, Advisories, Watches, and Emergency Notices, and coordinate the reduction or cancellation of clearances, re-dispatch of generation, and request, order, or take other action(s) that the SO determines is necessary to maintain safe and reliable operating conditions on the ERCOT system in accordance with ERCOT Protocols, Operating Guides, and NERC Reliability Standards.  The SO will implement and terminate ERCOT Time Corrections, and will determine the need for and implement the operation of a Qualified Scheduling Entity (QSE) on Constant Frequency Control for loss of ERCOT’s load frequency control system.

The SPP DC-Tie processes, procedures, or plans that support or affect SPP shall be reviewed at least once every 3 years and updated if needed.  These would include any DC-Tie procedures, inadvertent energy procedures, and emergency procedures.

## 3.4	SSRG Conference Calls

Procedure Purpose: To communicate information concerning disturbances or unusual occurrences to appropriate parties in the ERCOT Region by making a SSRG conference call.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 10 | Effective Date: March 31, 2017 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | The SSRG conference call will be used to inform the SSRG members of suspected sabotage or sabotage events, including multi-site sabotage events affecting larger portions of the Interconnection. The SSRG conference call will also be used for the following: - When the Threat Alert Level has increased, - To disseminate information and develop plans related to system emergencies and business continuity threats, - To conduct quarterly tests with the minimum objective of reviewing and updating the contact list (test to be conducted in February, May, August and November); AND - For any other events as warranted by the Manager, System Operations and/or Designee Refer to Hotline and email scripts below for notifications. |
| Threat & Emergency Classifications | Threats and emergencies can be classified as, but are not limited to, the following four SSRG event-types: 1. Internal to ERCOT ISO: Physical Security: Verifiable attacks or sabotage, or threats of attacks or sabotage that could jeopardize the operation of physical equipment within the electrical boundaries of the ERCOT grid that have a direct effect on the reliability of the ERCOT grid. This could be, but is not limited to, generation equipment, transmission equipment, and communication equipment. b. Cyber Security: Verifiable loss of control of the ERCOT EMS or MMS that is identified by EMMS Production Support as an actual or probable act of sabotage or the loss of control by any TOs or QSEs EMS Systems that is reported to ERCOT as an act of sabotage. 2. External to ERCOT ISO: a. Physical Security: Verifiable attacks or sabotage, or threats of attacks or sabotage that could jeopardize the operation of physical equipment in any electrical sector outside of the boundaries of ERCOT. b. Cyber Security: Verifiable loss of control over the EMS System of any participant in the electrical sector outside of the boundaries of ERCOT that is identified as an actual or probable act of sabotage. 3. Pandemic 4. Other unforeseen business continuity events (not to include grid instability) |
| QSE Notification | Using the Hotline, notify the QSEs of the SSRG conference call: Typical Hotline Script: “This is [first and last name] at ERCOT. There will be an SSRG conference call today at [time] Central Prevailing Time. The topic will be [quarterly test call, physical security, cyber security, pandemic or other topic]. Please notify your SSRG representative. The conference call number is 1-866-642-1665. Participants pass code is [code]. Any questions? Thank you.” |
| TO Notification | Using the Hotline, notify the TOs of the SSRG conference call: Typical Hotline Script: “This is [first and last name] at ERCOT. There will be an SSRG conference call today at [time] Central Prevailing Time. The topic will be [quarterly test call, physical security, cyber security, pandemic or other topic]. Please notify your SSRG representative. The conference call number is 1-866-642-1665. Participants pass code is [code]. Any questions? Thank you.” |
| Send E-mail | Send an e-mail to “1 SSRG” to make notification of the SSRG conference call. Typical Subject line for e-mail: SSRG conference call Typical Script for e-mail: An SSRG conference call has been scheduled for today at [time] Central Prevailing Time (CPT). The topic will be [quarterly test call, physical security, cyber security, pandemic or other topic]. The conference call number is 1-866-642-1665. Participant pass code is [code]. Participation is mandatory. Include signature on email. |
| Log | Log all actions. |

## 4.1	Resource Testing and In-Service Approvals

Procedure Purpose: This procedure provides direction and guidelines for conducting various testing and approval processes for resources and transmission elements.

| Protocol Reference | 3.3.1 | 6.5.7.8(1) | 8.5.1.1 | 8.5.1.2 |
| --- | --- | --- | --- | --- |
| Guide Reference | 3.3.2.2 |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 12 |  |  | Effective Date: March 31, 2017 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Step |  | Action |  |  |  |  |  |
| ### Unit Testing |  |  |  |  |  |  |  |
| NOTE |  | QSEs will submit test requests to shiftsupv@ercot.com. If e-mail is down, a fax will be accepted at (512) 248-6858. Test request forms are located on the ERCOT website under ‘Operating Procedures’. |  |  |  |  |  |
| 1 |  | As requests for unit tests are received, make every reasonable effort to accommodate testing. Reasons for not accommodating testing: - Unit has best shift factor to manage congestion for an outage. Without unit, contingency may reach max shadow price and become unsolvable, - The request exceeds 7 days, - A pattern of repeated requests for the same unit(s) indicate that abuse of the testing privilege may be taking place. If any request is refused for this reason, notify the Manager, System Operations and/or Designee. |  |  |  |  |  |
| CAUTION |  | If deployment of the testing unit is necessary to maintain system security, instruct the test be canceled and deploy as needed. |  |  |  |  |  |
| NOTE |  | The tests mentioned below are not an exhausted list, they are tests that required coordination with other ERCOT departments. |  |  |  |  |  |
| OK to Test |  | If the testing can be accommodated, RESPOND via e-mail or fax to the requesting party similar to the following: “ERCOT approves. ERCOT intends to make system adjustments to accommodate this testing to the extent possible consistent with system security. This intent is NOT a guarantee of accommodation”. ___________________ (Shift Supervisor) |  |  |  |  |  |
| Not OK to Test |  | IF the request cannot be accommodated, RESPOND via e-mail or fax to the requesting party similar to the following: “ERCOT cannot accommodate the request for the following reason(s) : <List reasons>”. __________________ (Shift Supervisor) |  |  |  |  |  |
| ### Approved Resources to be ONTEST |  |  |  |  |  |  |  |
| Approval |  | - As Resource tests are approved, update “Approved Unit Tests” spreadsheet located on the System Operations SharePoint. - All operators will be able to view the list to determine which resources are approved to use the status of ONTEST. |  |  |  |  |  |
| ### In Service Approval (or Approval to Energize) |  |  |  |  |  |  |  |
| 1 |  | IF: - A TO or QSE makes a request to energize new or relocated equipment; THEN: - Review notification provided by Operations Support Engineering, - Approve the request if notification has been provided; IF: - The equipment has not been approved by Operations Support Engineering, THEN: - Delay the request and notify Operations Support Engineer. |  |  |  |  |  |
| ### Ancillary Service Testing Coordination |  |  |  |  |  |  |  |
| 1 |  | Ancillary Service Qualification Testing will be done in coordination with Operations Analysis and EMMS Production Support. IF: - A QSE requests an Ancillary Service Qualification Test; VERIFY: - A Wholesale Account Manager is in the notification or instruct the QSE representative to notify their Wholesale Account Manager to start the process. |  |  |  |  |  |
| 2 |  | The coordination of the testing times will be between System Operations, Operations Analysis and EMMS Production Support. When contacted by Operations Analysis: - Wholesale Account Manager will notify QSE of scheduled test, - Ensure reliable conditions exist at all times. |  |  |  |  |  |
| Log |  | Log all actions. |  |  |  |  |  |
| ### Coordinated Reactive Tests |  |  |  |  |  |  |  |
| NOTE |  | The Resource Entity requesting to perform a Coordinated Test will provide ERCOT Operations and the TO with notice of the proposed test date before 1500 on the day prior to the day of the test. Requests shall be made between 0800 and 1700 on Business Days. Upon receipt of a request for test, ERCOT Operations and the TO will evaluate the expected conditions and determine whether ERCOT System conditions are conducive to a valid test can be created through coordinated network switching, modification of the generation reactive dispatch of nearby Generation Resources, or by some other means. Having established that suitable ERCOT System conditions exist or can be created, ERCOT Operations, and the TO shall confirm with the Resource Entity and the QSE the agreed upon test time and date or a rejection of the test time and date before 1700 on the day prior to the day of the test. |  |  |  |  |  |
| 1 |  | Coordinated Reactive Tests will be done in coordination with System Operations, Operations Analysis, the Transmission Operator (TO), and the Qualified Scheduling Entity (QSE). WHEN: - A QSE makes a request for a Coordinate Reactive Test; VERIFY: - Date/Time of Testing - MVAR Leading and/or Lagging expected during the test - CURL/D-Curve is attached - Estimated MW output If all information is included in the test request, proceed to step 2. If not, reply to e-mail from QSE and request the missing information. |  |  |  |  |  |
| 2 |  | The coordination of the testing times will be between System Operations, Operations Analysis and the Transmission Operator (TO). WHEN: - All information above is received; VERIFY: - TO has approved the test, - TO can approve verbally on a recorded line or by email Once the TO has approved and all information is accurate, approve the QSE test request. Include for following in the approval: - Operations Analysis - Shift Supervisors |  |  |  |  |  |
| OK to Test |  | If the testing can be accommodated, RESPOND via e-mail to the requesting party similar to the following: “ERCOT recognizes the need of <Company Name> to perform a Coordinated Reactive test with its unit <name> on <date and time>. ERCOT intends to make system adjustments to accommodate this testing to the extent possible consistent with system security. [TO] concurs with the test as long as real-time conditions allow for it. This will require the Generator Operator to contact the local transmission company prior to test initiation. This intent is NOT a guarantee of accommodation”. ___________________ (Shift Supervisor) |  |  |  |  |  |
| Not OK to Test |  | If the request cannot be accommodated, RESPOND via e-mail to the requesting party similar to the following: “ERCOT cannot accommodate the request of <Company Name>for a unit test on <date and time> for the following reason(s) : <List reasons>”. __________________ (Shift Supervisor) |  |  |  |  |  |
| Approval |  | - As Resource tests are approved, update “Approved Unit Tests” spreadsheet located on the System Operations SharePoint. - All operators will be able to view the list to determine which resources are approved to be ONTEST. |  |  |  |  |  |
| Log |  | Log all actions. |  |  |  |  |  |

## 5.1	Providing Technical and Operational Support

Procedure Purpose: Technical and operational support duties for the Shift Supervisor

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 3 | Effective Date: March 31, 2017 |
| --- | --- | --- |

The Shift Supervisor is responsible for ensuring operations are in compliance with ERCOT Protocols, NERC Reliability Standards, Operating Guides, and Operating Procedures.  The Shift Supervisor must have a very good understanding of the ERCOT Protocols, Operating Guides, and NERC Reliability Standards.

The Shift Supervisor may consult with Operations Support, Operations Analysis, Market Operations, or any resource he deems necessary to resolve and clarify market related issues.  She/he will assist the System Operators in resolving market issues.

The Shift Supervisor also monitors and ensures that adequate coordination between the ERCOT Region, MISO, SPP and CENACE is maintained.  To this effect the Shift Supervisor monitors the communications and coordination between the DC-Tie Operator, MISO, SPP and CENACE.

The Shift Supervisor is responsible for running primary operations from the Alternate Control Center once per month.  This is to ensure all desks are functional in the case of an emergency.

The Shift Supervisor has the authority to coordinate additional support to assist during emergencies, system and weather related disturbances, and high demand periods as deemed necessary.  Support may be required from Operations Support, Operations Analysis, Market Operations, Outage Coordinators, and System Operators assigned to the Alternate Control Center.  The Shift Supervisor also has the authority to assign temporary duties to this additional support staff.

Finally, other Shift Supervisor duties may require the on-shift Shift Supervisor to leave the Control Center from time to time.  On these occasions, the Shift Supervisor may delegate his duties to another system operator on a temporary basis.  The Shift Supervisor shall remain in contact and accessible to the control center via available communication means.

## 5.3	Notification of Protective Relay or Equipment Failures and Updates

Procedure Purpose:  Be aware and respond if needed to protective relay system failures when notified by a QSE or TO.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 6.2.3 | 6.2.4 |  |  |
| NERC Standard | PRC-001-1 R2, R2.2 |  |  |  |

| Version: 1 | Revision: 11 | Effective Date: March 31, 2017 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Protective Relay or Equipment Failure |  |
| NERC | “If a protective relay or equipment failure reduces system reliability, the Transmission Operator shall notify its Reliability Coordinator and affected Transmission Operators and Balancing Authorities. The Transmission Operator shall take corrective action as soon as possible.” |
| NOTE | Protective relay systems include: relays, associated communications systems, voltage and current sensing devices, station batteries, and DC control circuitry |
| 1 | When notified by a QSE or TO that a protective relay or equipment failure reduces system reliability: - Ask the QSE or TO how it reduces ERCOT Grid system reliability and if any corrective actions have been taken, - Ask the QSE or TO if notifications have been made to any other affected TOs, - Notify the Operations Support Engineer to verify that system reliability has been affected. If so, a corrective action must be taken within 30 minutes, - Determine if other TOs are affected by this failure and make notification by phone. |
| 2 | - After notification from a TO or QSE, NOTIFY by e-mail: - OPS Support Engineering - Operations Analysis - TransRep - Shift Supervisors - The subject line of the e-mail should read “Protective Relay”, “Equipment Failure”, or “Equipment Updates”. - Include in the e-mail: - Entity Name - Brief description - Contact information - Any significant information |
| 3 | If a TO or QSE e-mails a – “Mis-Operation Relay report that has occurred in the past, forward to the above identified e-mail address. |
| 4 | Log all actions. |
| ### Protective Relay Outages |  |
| NOTE | Protective relay maintenance that ERCOT ISO has been made aware of can be found on the Outage Calendar located on the System Operations SharePoint. |
| Planned Outage | IF: - Notified that a relay is going to be removed from service (Planned); THEN: - Verify information is on the Outage Calendar located on the System Operations SharePoint Site; IF: - Notification is posted; THEN: - Notify the TO or QSE they can proceed with work; IF: - Notification is NOT posted; THEN: - The relay can’t be removed from service unless there are secondary/back up relays that will be functional and no system degradation will occur; |
| Forced Outage | IF: - Notified that a primary relay has been removed from service (forced); THEN: - Ask if the secondary/back up relay is functional; IF: - There is no secondary/back up relay; THEN: - The equipment will need to be removed from service since it is no longer protected. |
| Log | Log all actions. |
| ### Protection System Setting Notifications |  |
|  | - WHEN: - Protection system setting notifications are received - FORWARD TO: - OPS Support Engineering - Operations Analysis - TransRep - Shift Supervisors |

## 5.4	Outage Coordination

Procedure Purpose:  Ensure Protocols are followed for Outage Coordination.

| Protocol Reference | 3.1 |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | IRO-017-1 R2 |  |  |  |

| Version: 1 | Revision: 2 | Effective Date: March 31, 2017 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - Real-time functional desks are not authorized to approve outages outside the timelines - The Transmission Outage Approval process has been specifically designed to allow the market time to respond and achieve a market solution. Therefore, outages cannot be moved forward from one day to the next out of the approved timeframe without impacting the market solution - The ERCOT Protocols clearly define the timelines for outage approval. At this time, no one (Outage Coordinator, System Operator, or Engineer) can approve a Planned Transmission Outage for the next day - The only outages that are allowed for the next day are Level 1 outages and Remedial Switching Actions reported by the Transmission Operator |
| 1 | Direct any questions about scheduling of transmission outages and generation outages to the Outage Coordination personnel. |
| NOTE | Under extreme emergencies the Shift Supervisor may enter a Forced Outage for a TO or QSE. |
| 2 | Navigate to the market Outage Scheduler in the Market Information System. - MIS; Applications; ERCOT Applications; Outage Scheduler |
| 3 | Open Outage Scheduler |
| 4 | Select a Category of outage: - Transmission - Generation |
| 5 | Select the TO or QSE Name: |
| 6 | Select Change User to access the TO or QSE data |
| 7 | Select Create New Outage: - Choose Forced |
| 8 | Select Actual Start: - Enter Date and Time |
| 9 | Select Planned End: - Enter Date and Time |
| 10 | Enter the Emergency Restoration in HRS - Must be = or < than outage duration |
| 11 | Select the Nature of work: - Choose a description from the dropdown |
| 12 | Select a Station Name: - Choose a station from the dropdown |
| 13 | Select the Equipment Type: - Choose the Equipment Type from the dropdown |
| 14 | Select the Equipment: - Choose a piece of equipment from the dropdown |
| 15 | If known: - Enter Supporting Information for outage |
| 16 | Select the Submit button. |
| 17 | If errors or problems are detected, consult with the Outage Coordinator. |
| Log | Log all actions. |

## 5.5	Supervise Coordination with SPP, MISO and CENACE

Procedure Purpose:  To ensure proper notification and coordination takes place.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 7 | Effective Date: March 31, 2017 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | The ERCOT ISO is only connected to another RC through asynchronous ties. The coordination and communication that must take place with SPP, MISO and CENACE is outlined below. It is the responsibility of the Shift Supervisor to ensure this coordination takes place. - DC-Tie Tagging Activities - EEA Levels - Outages on DC-Ties - BLT’s - Arming of the Monticello RAS - Switchable Generation - ERCOT System Blackout Communications with CENACE will be coordinated through AEP Corpus for the Eagle Pass and Laredo DC-Tie and Sharyland for the Railroad DC-Tie. |
| DC-Ties | Confirm that the DC Tie schedules and E-Tags were properly verified. Ensure that the “after-the-fact checkout” is performed each night and e-mailed to the appropriate entities as outlined in the DC-Tie Procedures. |
| EEA | ERCOT’s EEA status must be communicated to the SPP Reliability Coordinator (Turret phone button labeled SPP RC) as outlined in the DC-Tie procedures. |
| Outages | All planned and forced outages that affect the DC-Ties shall be coordinated with the Tie Operator(s) and SPP (if SPP DC-Ties affected). A message must also be posted on the MIS Public using Notice Builder for planned outages on any commercial DC-Ties. |
| BLT | Notify the SPP or MISO Reliability Coordinator when a BLT is initiated between ERCOT and SPP or MISO, as outlined in the Transmission & Security procedures. |
| RAS | Notify the SPP Reliability Coordinator when the Monticello RAS arms. If the RAS activates, the DC-E will trip. |
| ### Switchable Generation Resource |  |
| NOTE | Switchable Generation Resource (SGR) can be connected to either the ERCOT grid or MISO or SPP. ERCOT has coordination agreements with both SPP and MISO, if any entity enters or foresees entering into an emergency, the RC with the emergency can request help to mitigate the emergency. This help will consist of requesting one or more SGRs to switch into the grid with the emergency. |
| 1 | IF: - MISO or SPP call to request one or more SGR be switched into them; THEN: - Within one hour, determine that by releasing the SGRs it does not cause an Adverse Reliability Impact for ERCOT. IF: - No Adverse Reliability Impacts; THEN: - Notify the RC and the QSE for the SGR, it is up to the QSE as to whether they want to switch. Follow the same process if ERCOT requests a SGR be switched into ERCOT. |

## 5.6	Equipment Limitation and Rating Changes

Procedure Purpose:  To ensure line rating changes are documented and correct.

| Protocol Reference | 6.5.3(2) |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 6 | Effective Date: March 31, 2017 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Line Rating Changes |  |
| NOTE | Normally line rating changes can only be changed when a NOMCR is received. |
| 1 | IF: - Notified by a TO of an incorrect line rating; THEN: - Notify the Operations Support Engineer. |
| Log | Log all actions. |
| ### TO Temporary Equipment Limitation Notifications |  |
| 1 | IF: - Notified by a TO of any limitations on the Transmission Facilities that may affect Dispatch Instructions / Operating Instructions; THEN: - Notify the Operations Support Engineer. |
| 2 | IF: - The Operations Support Engineer confirmed the Temporary Equipment Limitation Notifications may affect Dispatch Instructions / Operating Instructions; THEN: - Notify the Manager, System Operations and/or Designee to post on the MIS Secure Area the Transmission Facility limitations that may affect Dispatch Instructions / Operating Instructions. |
| Log | Log all actions. |

## 5.7	TO or QSE Backup Control Center Transfer

Procedure Purpose:  To provide internal notification.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 4 | Effective Date: March 31, 2017 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| 1 | If notified by a QSE or TO that they will be transferring to their backup control center, or from their backup to primary, - Send e-mail to 1 ERCOT System Operators |
| 2 | - If experiencing issues with communications, ICCP, etc. contact the Help Desk. |
| Log | Log all actions. |

## 5.9	Approval for Telecommunication and EMMS Outages and Maintenance

Procedure Purpose:  To provide System Operators with the authority to approve planned outages and maintenance of its telecommunication, monitoring and analysis capabilities.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | IRO-002-4 R2 | TOP-001-3 R16, R17 |  |  |

| Version: 1 | Revision: 0 | Effective Date: March 31, 2017 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | System Operators have the authority to approve planned outages and maintenance of its telecommunication, monitoring and analysis capabilities. This includes providing approval for planned maintenance such as database loads, site failovers, ICCP links, etc. This authority applies to TOs and QSEs planned outages of telemetering, control equipment, and associated communication channels when reliability of the grid is in jeopardy. |
| 1 | WHEN: - Notified by the Telecommunication group or the EMMS group to approve a planned outage or maintenance of any telecommunication, monitoring or analysis capability; THEN: - Provide approval only if it won’t impede with the reliability of the grid. IF: - Approval cannot be granted at the time request, suggest another time that may be more suitable. |
| Log | Log all actions. |

## 6.1	Reports

Procedure Purpose: Provide reporting criteria and instructions for the daily reports sent to the PUC, the process to report certain events to the Texas Reliability Entity, posting EEA notices to RCIS and the process for reporting system disturbances to NERC and DOE.

| Protocol Reference | 22 (B) | 6.5.1.2 (4) |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 3.2.3 | 4.7 |  |  |
| NERC Standard | EOP-011-1 R2.1, R2.2.2, R2.2.3.2, R2.2.3.3, R2.2.5, R6 | EOP-004-3 R1, R2, R3 | EOP-010-1 R2 |  |

| Version: 1 | Revision: 30 | Effective Date: March 31, 2017 |
| --- | --- | --- |

| Step | Action |  |
| --- | --- | --- |
| ### PUCT Daily Report |  |  |
| Initial Report | Complete the PUCT Daily Report template between 0300 – 0400 and again between 1400 – 1500 each day. |  |
| E-Mail Report | E-mail the report to the distribution list entitled “PUC-Available Generating Resources.” |  |
| Update Report | Update and resend report when system conditions change that cause concern. Some examples are below: - The probability of an EEA event increases. Give reason(s) for concerns - When Off-Line Non-Spin is deployed for capacity (provide times) - A special update is not needed; provide information next time report is updated. - Conditions change that required new notices to be issued or cancelled - OCN, Advisory, Watch, or Emergency Notice (excluding GMD Advisory’s) - Clarify whether Transmission Watch/Emergency is due to a planned or forced outage (state the area of the state) noting the date and time - A special update is not needed for DAM/DRUC delays; provide information on the 1500 update - Do NOT update report for tool outages. - The Gibbons Creek Bryan East/Green Prairie 138 kV double circuit transmission line trips, or if unplanned outages of generation units cause security problems in the Bryan-College Station area - Localized gas curtailments, not expected to cause reliability issues (be specific, how much is derated) - A DCS event - Deployment of Load Resources - Any Nuclear Resource issues (including trips, coming off-line, high risk activities, de-ratings, etc.) Do Not use abbreviations, spell words out. Send updated report when conditions have returned to normal. |  |
| Weather Information | The temperatures are automatically pulled from the EMS, however please verify temperatures from a National or Local Weather Service for each city listed and adjust as necessary. |  |
| Guidelines for Determining EEA Potential | Use the following guidelines to determine the potential for EEA when completing the PUCT Daily Report: Potential for EEA Level 1 - Low - Sufficient capacity to cover peak demand - An Advisory is in effect for Physical Responsive Capability. - Medium - A Watch is in effect for Physical Responsive Capability. - Loss or delay of generation availability during peak demand that may diminish Physical Responsive Capabilities - Excel MAI shows multiple hours of insufficient reserves and there is belief it is a significant threat - High - A Watch is in effect for Physical Responsive Capability and trending downward after procuring quick-start capacity - Excel MAI shows multiple hours of insufficient reserves AND ERCOT has been unable to correct the capacity insufficiency over several hours AND ERCOT believes it is a significant threat - Critical - EEA Level 1 in effect Potential for EEA Level 2 - Low - Sufficient capacity to cover peak demand - An Advisory is in effect for Physical Responsive Capability - Medium - EEA Level 1 in effect - High - Physical Responsive Capability ≤ 1750 MW and trending downward - Critical - Physical Responsive Capability ≤ 1375 MW and trending downward Potential for EEA Level 3 - Low - Sufficient capacity to cover peak demand - High - EEA Level 2 in effect - Physical Responsive Capability < 1000 MW and trending downward, OR - Unable to maintain frequency ≥ 59.8 Hz - Critical - EEA Level 3 in effect |  |
| ### 7-Day Outlook |  |  |
| Report | Complete the 7-Day Outlook Report between 1500 – 1530 each day. |  |
| Open | The 7 Day Forecast file is located: P:\SYSTEM OPERATIONS drive in the “7-Day Outlook” Folder. |  |
| Verify | Data looks to be correct. |  |
| E-Mail Report | E-mail the report to the 7-Day Load and Capacity Outlook distribution list by selecting “Report” and confirming. |  |
| ### Unit Trip Posting |  |  |
| Report | Complete the Unit Trip posting for the previous day between 0000 – 0800 each day of the week. |  |
| Analyze | Review: - Any unit trips from the previous day, - Post an Operational Information message, low priority, on MIS Public |  |
| <450 MW | IF: - No trips are greater than 450 MW, - Post the following message example on MIS Public |  |
| Post | No sudden loss of generation greater than 450 MW occurred on <Date>. |  |
| ≥450 MW | IF: - A trip was 450 MW or more, - Post the following message example on MIS Public |  |
| Post | On <Date>, a sudden loss of generation occurred at <Time> totaling *** MW. Frequency declined to **.*** Hz, ERCOT load was **,*** MW. |  |
| Multiple Trip Example | On <Date>, a sudden loss of generation occurred at <Time> totaling *** MW. Frequency declined to **.*** Hz, ERCOT load was **,*** MW. Another sudden loss of generation occurred at <Time> totaling *** MW. Frequency declined to **.*** Hz, ERCOT load was **,*** MW. |  |
| ### Event Analysis Reporting |  |  |
| 1 | WHEN an event occurs that is listed on the “event list” below, before shift is over: - E-mail information to Manager, System Operations and Designee - The subject line of the e-mail should read “TRE Event.” |  |
| Event List | For purposes of the event analysis program, brief reports must be completed with 5 days. Most events listed are either OE-417 or EOP-004 reportable, those timelines and forms will be used in place of the EA brief report. Category 1 Events: - An unexpected outage, contrary to design, of three or more BES Facilities caused by a common disturbance: - The sustained outage of a combination of three or more BES Facilities - The outage of an entire generation station of three or more generators (aggregate generation of 500 MW to 1,999 MW); each combined cycle unit is counted as one generator - Intended and controlled system separation by the proper operation of a RAS - Failure or misoperation of BES RAS - System-wide voltage reduction of 3% or more that lasts more than 15 continuous minutes due to a BES emergency - Unintended BES system separation that results in an island of 100 MW to 999 MW. This excludes BES radial connections, and non-BES (distribution) level islanding - The loss of generation of 1,000 MW to 1,999 MW - Loss of monitoring or control, at a control center, such that it significantly affects the entity’s ability to make operating decisions for 30 continuous minutes or more Examples include, but are not limited to the following: - Loss of operator ability to remotely monitor or control BES elements - Loss of communications from SCADA RTU - Unavailability of ICCP links reducing BES visibility - Loss of the ability to remotely monitor and control generating units via AGC - Unacceptable state estimator or contingency analysis solutions Category 2 Events: - Complete loss of Interpersonal Communication and Alternative Interpersonal Communication capability affecting its staffed BES control center for 30 continuous minutes or more - Voltage excursions within a Transmission Operator’s footprint equal to or greater than 10% lasting more than 15 continuous minutes - Complete loss of off-site power (LOOP) to a nuclear generating station per the Nuclear Plant Interface Requirement - Unintended system separation that results in an island of 1,000 MW to 4,999 MW - Unintended loss of 300 MW or more of firm load for more than 15 minutes - IROL Violation for time greater than Tv. Category 3 Events: - Unintended loss of load or generation of 2,000 MW or more - Unintended system separation that results in an island of 5,000 MW to 10,000 MW Category 4 Events: - Unintended loss of load or generation from 5,001 MW to 9,999 MW - Unintended system separation that results in an island of more than 10,000 MW Category 5 Events: - Unintended loss of load of 10,000 MW or more - Loss of generation of 10,000 MW or more |  |
| ### NERC and DOE Reporting |  |  |
| NOTE | - Contact the Manager, System Operations and/or Designee when a NERC or DOE reporting event occurs. If available, they will be responsible to complete the required form - In the body of the e-mail, type the following: - "Contains Privileged Information and/or Critical Energy Infrastructure Information - Do Not Release.". - NERC 24-hour Emergency Hotline (404) 446-9780), |  |
| OE-417 Reporting Events | DOE OE-417 forms can be downloaded at: http://www.eia.gov/survey/form/oe_417/form.pdf. The items in bold/grey must be reported within 1 hour of the incident. The others must be reported within 6 hours. All final reports must be submitted within 48 hours. OE-417 reports are required for the following events: - Actual physical attack that causes major interruptions or impacts to critical infrastructure facilities or to operations - Actual cyber or communications attack that causes major interruptions of electrical system operations - Complete operation failure or shut-down of the transmission and/or distribution electrical system - Electrical System separation (Islanding) where part or parts of a power grid remain(s) operational in an otherwise blacked out area or within the partial failure of an integrated electrical system - Uncontrolled loss of 300 MW or more of firm system loads for more than 15 minutes from a single incident - Load shedding of 100 MW or more implemented under emergency operational policy - System-wide voltage reduction of 3% or more - Public appeal to reduce the use of electricity for purpose of maintaining the continuity of the electric power system (ERCOT process each EEA) - Suspected physical attacks that could impact electric power system adequacy or reliability; or vandalism which target components of any security systems - Suspected cyber or communications attacks that could impact electric power system adequacy or vulnerability - Loss of electric service to more than 50,000 customers for 1 hour or more - Fuel supply emergencies that could impact system adequacy or reliability |  |
| Event Reporting EOP-004-3 | NERC Preliminary Disturbance reports are to be completed within 24 hours of recognition of meeting an event type threshold for reporting or by the end of the next business day if the event occurs on a weekend (which is recognized to be 4 PM local time on Friday to 8 AM Monday local time). Events that are also DOE reportable, the OE-417 form should be used. For the other events, use the EOP-004 – Attachment 2 Event Reporting Form: - Damage or destruction of a Facility that results in actions to avoid a BES Emergency - Damage or destruction of a Facility that results from actual or suspected intentional human action - Physical threats to a Facility excluding weather or natural disaster related threats, which has the potential to degrade the normal operation of the Facility or suspicious device or activity at a Facility. Do not report theft unless it degrades normal operation of a Facility - Physical threats to its BES control center, excluding weather or natural disaster, which has the potential to degrade the normal operation or suspicious device or activity at its BES control center - Public appeal for load reduction event - System wide voltage reduction of 3% or more - Manual firm load shedding 100 MW or more - Automatic firm load shedding 100 MW or more (via automatic undervoltage or underfrequency load shedding schemes or RAS - Voltage deviation of 10% or more of nominal voltage sustained for 15 or more continuous minutes - Operate outside the IROL for time greater than IROL Tv (30 minutes) - Loss of firm load for 15 minutes or more: - 300 MW or more for entities with a previous year’s demand of 3,000 MW or more - 200 MW or more for all other entities - Each system separation resulting in an island 100 MW or more - Loss of generation of 1,000 MW or more - Complete loss of off-site power affecting a nuclear generating station per the Nuclear Plant Interface Requirement - Unexpected loss within its area, contrary to design, of three or more BES Elements caused by a common disturbance (excluding successful automatic reclosing - Unplanned evacuation from BES control center facility for 30 continuous minutes or more - Complete loss of voice communication capability affecting a BES control center for 30 continuous minutes or more - Complete loss of monitoring capability affecting a BES control center for 30 continuous minutes or more such that analysis capability (i.e., State Estimator or Contingency Analysis) is rendered inoperable |  |
| 1 | When required to file or forward a report, the Manager, of System Operations or the Designee will be responsible. File or forward disturbance report to entities that have not received: - NERC System Awareness (systemawareness@nerc.net) - NERC (operations@eisac.com), requirement for cyber and courtesy copy for all other reports - Fax (404) 446-9770, if internet down - Phone (404) 446-9780 - DOE when required above (doehqeoc@oem.doe.gov) - Fax (202) 586-8485, if internet down - Phone (202) 586-8100 - NERC and DOE Disturbance Reporting e-mail list |  |
| NOTE | Please be aware that for phone calls to NERC, you will be prompted by a computerized auto-attendant to press 1 for operational issues or 2 for cyber-security issues. |  |
| ### RCIS Reporting |  |  |
| EEA Postings | There are four levels of Emergency Energy Alert (EEA). As ERCOT enters each level, postings must be made on the RCIS under “Energy Emergency Alert”: - “ERCOT is declaring EEA 1” - “ERCOT is declaring EEA 2” - “ERCOT is declaring EEA 3” - “ERCOT is in EEA 0 and back to normal operations.” |  |
| ### NXT Notification Requirements |  |  |
| Beginning of each Shift |  | Log into the NXT Communicator at the beginning of each shift in order to make the required notification quickly. - If issues arise and you are unable to log into the NXT Communicator with your user name, notify the helpdesk and request immediate assistance. |
| NOTE |  | NXT notification should be coordinated with the Shift Engineer. |
| Watch |  | IF: - A Watch for Physical Responsive Capability is initiated, THEN: - Select the “SO Watch PRC below 2500” Scenario and activate notification, WHEN: - A Watch for Physical Responsive Capability has been cancelled, THEN: - Select the “SO Watch for PRC Cancelled” Scenario and activate notification. |
| EEA Implementation Levels |  | IF: - ERCOT initiates EEA Level 1, THEN: - Select the “SO EEA Level 1” Scenario and activate notification, IF: - ERCOT initiates EEA Level 2, THEN: - Select the “SO EEA Level 2” Scenario and activate notification, IF: - ERCOT initiates EEA Level 3 without Load Shed, THEN: - Select the “SO EEA Level 3, NO Load Shed” Scenario and activate notification. IF: - ERCOT initiates EEA Level 3 with Load Shed, THEN: - Select the “SO EEA Level 3, WITH Load Shed” Scenario and activate notification. |
| EEA Termination Levels |  | WHEN: - EEA Level 3 is terminated, THEN: - Select the “SO EEA Level 3 to EEA Level 2” Scenario and activate notification, WHEN: - EEA Level 2 is terminated, THEN: - Select the “SO EEA Level 2 to EEA Level 1” Scenario and activate notification, WHEN: - EEA Level 1 is terminated, THEN: - Select the “SO EEA Level 1 Cancellation” Scenario and activate notification. |
| Loss of Firm Load |  | IF: - An Operator (ERCOT or TO) has issued a request for firm load shed of ≤ 100 MW, THEN: - Notify the Manager, System Operations and/or Designee immediately. WHEN: - An Operator (ERCOT or TO) has issued a request for firm load shed of ≥ 100 MW, THEN: - Notify the Manager, System Operations and/or Designee immediately, - Select the “SO Request Firm Load Shed” Scenario and activate notification. |
| NXT Testing |  | WHEN: - Performing Shift Supervisor Procedure 9.2 Monthly Testing of Non-Routinely used Telecommunications Facilities, THEN: - Select the “SO ENS Test” Scenario and activate notification. |
| ### ERCOT Morning Report |  |  |
| NOTE | - This report is currently only required Monday – Friday. - The Morning Report form is located on the _Operations Official Spreadsheets folder |  |
| 1 | Weather Information: - Enter temperatures from a National or a Local Weather Service for each city listed. - Enter the current day forecast conditions for each city listed. |  |
| 2 | Load Data: - The All-Time Peak MW and Seasonal Peak MW will be provided as needed. - Verify the Projected Peak MW and peak hour for the current day. Use the most reasonable forecast, which may not be the highest. - Verify the Previous Day Actual MW. |  |
| 3 | Interchange: - Verify the net flow across the DC-Ties for the peak hour. This can be obtained from the MOI under “DC Tie Scheduling” or from the Excel MAI. |  |
| 4 | Transmission Line Outages: - Verify the number of 345 kV line segment outages for the peak hour. |  |
| 5 | Generation MW Totals: - Verify the Generation scheduled outage MW total. - Verify the Generation forced outage MW total. |  |
| 6 | Projected MW Reserves: - Verify the Responsive Reserve requirement at the Project Peak. - Verify the anticipated operating reserves available at time of peak. - The anticipated operating reserves can be found by adding the “Max Cap. Room” and Responsive Reserve requirement. |  |
| 7 | Recent ERCOT Congestion Activity: - No action needed |  |
| 8 | Comments: - List any active OCNs, Advisories, Watches or Emergency notices. |  |
| 9 | Select: Create Report |  |
| EMAIL | The file is transferred to P:\SYSTEM OPERATIONS drive in the NERC Morning Report Folder. This report should be sent as an attachment by 0700 using the e-mail distribution list entitled “ERCOT Morning Report.” The subject line of the e-mail should read “ERCOT Morning Report for <date>” |  |
| ### RMR Unexcused Misconduct Events |  |  |
| NOTE | - For a RMR unit, a “Misconduct Event” means any hour or hours during which Participant is requested to, but does not; deliver the energy at a level of at least 98% on each hour of the level shown in the Availability Plan. - For a Synchronous Condenser Unit, a “Misconduct Event” means any hour or hours during which Participant is requested to, but does not, synchronize the Unit to the ERCOT Transmission Grid during any hour in which the Unit is shown in the Availability Plan |  |
| 1 | IF: - An RMR or Synchronous Condenser fail to deliver the energy when requested to; THEN: - Notify the Manager of System Operations and/or Designee. - The manager will gather the detailed information and send an e-mail to “Nodal Settlements and Billing” with the subject line “Action Required – RMR Unexcused Misconduct Event”. |  |
| ### Shift Schedule |  |  |
| NOTE | - Shift Schedules will be posted to the MIS under GRID on the Transmission Page in the Transmission Supporting Information section. - The posting of the schedule will be current at all time to be compliant with the Protocols. |  |
| ### GEO-Magnetic Disturbance (GMD) |  |  |
| NOTE | Solar storms or Geo magnetic disturbances (GMDs) are caused by the interaction of coronal mass ejections (solar flares) with the Earth’s Ionosphere. This interaction produces ionospheric currents in the magnitude of millions of amperes which disturb Earth’s magnetic field. This disturbance induces voltage potential at Earth’s surface which results in geomagnetically induced currents (GICs) in conducting paths such as long transmission lines, pipelines, cables etc. GICs are low frequency or quasi-DC currents which enter and exit the power system at transformer groundings and grounded transmission lines. GICs of 100’s of amperes in magnitude have been recorded. Hence the GICs have the potential to disrupt the normal operation of power system and may damage transformers. GICs may also lead to the loss of reactive power support and hence may cause voltage instabilities. |  |
| Monitor | Monitor forecasted and current space weather: - Reliability Coordinator Information System (RCIS) at https://rcis.nerc.net - NOAA’s Space Weather Prediction Center http://www.swpc.noaa.gov/ |  |
| Warning (Forecasted) | WHEN: - A forecasted GMD Warning is issued for K-7 and greater or G3 and greater; THEN: - Post message on MIS Public - Notice Type: Operational Information - Notice Priority: Low Typical MIS Posting: The Space Weather Prediction Center has issued a GMD Warning of [state level] until [date and time]. Notify Operations Support to run power flow studies to identify 345kV transformers loaded above 70% and develop a mitigation plan if needed. |  |
| Extend | IF: - The Warning is extended or K level increases/decreases; THEN: - Post new message on MIS Public and - Cancel the older message Typical MIS Posting: The Space Weather Prediction Center has extended the GMD Warning of [state level] until [date and time]. |  |
| Cancel | WHEN: - The Warning is no longer valid; THEN: - Cancel the MIS posting. |  |
| Alert (Current) | WHEN: - An Alert for a GMD is issued for K-7 and greater or G3 and greater, or the K level increases/decreases; THEN: - Instruct the Transmission & Security and Real-Time Operators to implement their GMD procedures to make additional postings and Hotline calls. |  |
| Extend | IF: - The Alert is extended or the K level is increased/decreases; THEN: - Instruct the Operators to extend the Alert and/or make notifications regarding storm severity. |  |
| Cancel | WHEN: - K levels drop below K7 or when the Warning is no longer valid; THEN: - Instruct the Operators to cancel the Advisory for the Alert. |  |
| Issues | IF: - Any TO reports an issue due to the GMD event; THEN: - Send e-mail to the following with the details - Operations Analysis - Operations Support - Shiftsupv |  |
| ### Gas Restrictions |  |  |
| 1 | Once notified by a QSE of gas restrictions - Send an e-mail to “Gas Company Notifications”. This will notify all appropriate ERCOT staff. |  |
| 2 | Determine: - If the gas restriction could impact electric power system adequacy or reliability, THEN: - Proceed to “Reports” procedure for NERC/DOE reporting requirements, AND - Consider fuel switching for the generation that has this capability This data can be viewed at ERCOT SharePoint > System Operations – Control Center > Quick Links > Fuel Oil Capability |  |
| ### Remedial Action Schemes (RAS) |  |  |
|  | IF: - A Monthly RAS report is received by e-mail; THEN: - Forward reports to: - OPS Support Engineering - Shift Supervisors |  |

## 7.2	EEA Implementation Checklist

shift Supervisor – EEA IMPLEMENTATION Check List

| Time | Action | Comment |
| --- | --- | --- |
|  | Administrative tasks applicable to each step: |  |
|  | - Hotline calls made |  |
|  | - NXT System activated |  |
|  | - MIS message posted |  |
|  | - SPP RC Notified |  |
|  | - RCIS Posting |  |
|  | - PUCT Report updated |  |
|  | - Ensure 3-part communication is used |  |
|  | EEA Level 1 Implementation | PRC <2300 MW and is not projected to be recovered above 2300 MW within 30 minutes without the use of EEA Level 1 |
|  | - Non-Spin deployed |  |
|  | - 30 MIN ERS deployed, if deploying in Level 1. This includes Weather-Sensitive if June – September and Time Periods TP3 & TP4 |  |
|  | - Resource testing suspended |  |
|  | - Online RMRs loaded to full output |  |
|  | - Emergency Energy procedures implemented across CENACE DC-Ties |  |
|  | - EEA 1 Schedule requested across SPP DC-Ties |  |
|  | - RUC VDI/electronic Dispatch Instruction confirmation, as appropriate/including EMR |  |
|  | - TOs load management program deployed if deemed necessary if June - September |  |
|  | - OE-417 for public appeals |  |
|  | EEA Level 2 Implementation Maintain steady state system frequency at a minimum of 59.91 Hz and maintain PRC above 1000 MW | PRC <1750MW or unable to maintain system frequency at a minimum of 59.91 Hz and is not projected to be recovered above 1750 MW within 30 minutes without the use of EEA Level 2 |
|  | - Load Resources deployed and/or ERS Resources - Block 1 (<1750MW) - Block 2 (as needed) - Both (<1375MW) |  |
|  | - 30 MIN ERS deployed, if not deployed in Level 1. This includes Weather-Sensitive |  |
|  | - 10 MIN ERS deployed, if deemed necessary |  |
|  | - TOs load management program deployed if available |  |
|  | - Emergency Energy Procedures implemented across SPP DC-Ties |  |
|  | - TOs notified of Load Resource deployment |  |
|  | - Distribution voltage reduction, as appropriate |  |
|  | - RUC VDI/electronic Dispatch Instruction confirmation, as appropriate/including EMR |  |
|  | EEA Level 3 Implemention | PRC < 1000 MW or unable to maintain Freq at 59.8 Hz and is not projected to be recovered above 1000 MW within 30 minutes without the use of EEA Level 3. |
|  | - PRC <1375 MW |  |
|  | - Firm Load shed ordered (100 MW blocks) |  |
|  | - QSEs notified of Firm Load shed |  |
|  | - Load shed achieved |  |

## 7.6	Extreme Hot Weather

Procedure Purpose: To ensure ERCOT, TOs and QSEs are prepared for Extreme Hot weather operations.

| Protocol Reference | 6.3.2(3)(a)(ii) | 6.5.9.3(2)&(3) | 6.5.9.3.1(4) | 6.5.9.3.2(4) |
| --- | --- | --- | --- | --- |
|  | 6.5.9.3.3 (5) | 6.5.9.3.4 (1) |  |  |
| Guide Reference | 4.2.1 | 4.2.2 | 4.2.3 | 4.2.4 |
| NERC Standard | EOP-011-1 R1.1, R2.1, R2.2.9 |  |  |  |

| Version: 1 | Revision: 7 | Effective Date: March 31, 2017 |
| --- | --- | --- |

| Step |  | Action |
| --- | --- | --- |
| NOTE |  | Extreme Hot weather notifications are issued when: Temperatures are forecasted to be 103°F or above in the North Central and South Central weather zones. – OR – Temperatures are forecasted to be 94°F or above in the North Central and South Central weather zones during the following months (October – May). |
| OCN |  | When extreme hot weather is forecasted approximately 5 days away: - Ensure OCN is issued - Continue to monitor the weather - Coordinate with Outage Coordination for the review of Planned and existing outages for the possibility of withdrawing or restoring equipment |
| Advisory |  | When extreme hot weather is forecasted approximately 3 days away: - Ensure Advisory is issued - Continue to monitor the weather - Continue to coordinate with Outage Coordination for the review of Planned and existing outages to be withdrawn, rejected, or restored |
| Watch |  | When extreme hot weather is forecasted approximately 1 day away: - Ensure Watch is issued - Continue to monitor the weather - Continue to coordinate with Outage Coordination for the review of Planned and existing outages to be withdrawn, rejected, or restored - Contact Operations Support to run studies to determine the impact of current and future outages - Review emergency operating procedures |
| Emergency Notice |  | When extreme hot weather has arrived and is beginning to have an adverse impact on the ERCOT System: - Ensure Emergency Notice is issued - Implement emergency procedures as needed |
| Issues |  | Notify the ERCOT Manager, System Operations or Designee of any issues. |
| Log | Log all actions. |  |

## 9.1	Interpersonal Communication Devices

Procedure Purpose: To define the Interpersonal Communication capability devices as well as the Alternate Interpersonal Communication capability devices.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | COM-001-2.1 R1.1, R6.2 |  |  |  |

| Version: 1 | Revision: 1 | Effective Date: March 31, 2017 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Interpersonal Communication | Interpersonal Communication is defined as “Any medium that allows two or more individuals to interact, consult, or exchange information”. This is referring to voice only, not data. Interpersonal Communication are classified as the following device: - Turret phone, which includes the hotline and OPX located in the Turret. |
| NOTE: | The Satellite phone in the turret will be classified as an Alternative Interpersonal Communication device since the modem portion of the call takes a different route then the OPX and hotline. |
| Alternative Interpersonal Communication | Alternative Interpersonal Communication is defined as Any Interpersonal Communication that is able to serve as a substitute for, and does not utilize the same infrastructure (medium) as, Interpersonal Communication used for day-to-day operation. Alternative Interpersonal Communication devices are classified as the following devices: - Satellite phone in the Turret - Satellite stand-alone phone - PBX (Nortel) - PBX Bypass land-line - Cell phone |
| 1 | ERCOT must have Interpersonal Communication capability and Alternate Interpersonal Communication capability with the following entities: - TOs - QSEs - DC-Tie Operator in SPP area |

## 9.2	Interpersonal Communication Failures

Procedure Purpose: To test the satellite phone system between ERCOT and the Transmission Operators to ensure communication capability via the Satellite Phone System.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | COM-001-2.1 R10 |  |  |  |

| Version: 1 | Revision: 1 | Effective Date: March 31, 2017 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| 1 | IF: - The Turret phone becomes inoperable, either hotline or OPX lines; THEN: - Attempt to use the lines from the Alternate Control Room. IF: - The Hotline or OPX lines from the Alternate Control Room are also inoperable; THEN: - Use one of your Alternate Interpersonal Communication tools listed in Section 9.1 |
| 2 | IF: - There is a failure at both the Primary and Alternate Control Rooms for Hotline and/or OPX lines; THEN: - If failure is expected to last 30 minutes or longer, notification must be made to the following entities within 60 minutes of the detection of failure. - TOs - QSEs - DC-Tie Operator in SPP area Note: The list of OPX and long distance numbers can be found on SharePoint titled “OPX & LD Phone Numbers”. |
| Log | Log all actions. |

## 9.3	Testing of Alternative Interpersonal Communications

Procedure Purpose: To test the Alternative Interpersonal Communications capability at least once each calendar month.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | COM-001-2.1 R9 |  |  |  |

| Version: 1 | Revision: 11 | Effective Date: March 31, 2017 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Primary Control Center |  |
| 1st Weekend Of Every Month | On the first weekend of each month, between the hours of 0000 Saturday and 0500 Monday, test each Alternative Interpersonal Communication devices as listed in steps below. |
| PBX | - Using the Nortel phone, make a call to an OPX extension - Make a log entry listing the device tested, who the test call was made to, and if it was successful. |
| PBX By-Pass | - Using the PBX By-Pass phone, make a long distance call - Make a log entry listing the device tested, who the test call was made to, and if it was successful. |
| Cell Phone | - Using the Control Room cell phone, make a call to the ERCOT Helpdesk cell phone. - Make a log entry listing the device tested, who the test call was made to, and if it was successful. |
| Stand Alone Satellite | - Using the Standalone Satellite phone, make a call (not necessary to call a satellite number). Refer to Desktop Guide Common to Multiple Desks Section 2.7.5. - Make a log entry listing the device tested, who the test call was made to, and if it was successful. |
| Satellite Modem | Coordinate the following test with the ERCOT DC Tie Operator at the alternate control center. - Using the turret, call each programmed Satellite desk phone at the alternate control center. - Make a log entry listing the device tested, who the test call was made to, and if it was successful. |
| Unsuccessful Test | IF: - Any of the above devices proved to be unsuccessful; THEN: - Open a help ticket and cc: “shiftsupv”, AND - Designate a replacement device IF: - An Alternative device cannot serve as a replacement; THEN: - Ensure the help ticket knows that capability must be restored within 2 hours. |
| Replacement/ Alternative device Examples | Designate a replacement device: The [Device] phone on the [RUC] Desk at the Primary Control Center will be used if needed until the [Device] phone on the [Supervisor] Desk is repaired. Alternative devices cannot serve as a replacement: All Alternative Interpersonal Communication phones at the Primary Control Center and the same device from the Alternate Control Center are inoperable. Helpdesk has been notified with a high priority ticket to restore one within 2 hours. |
| NXT Test | The NXT is not an Alternative Interpersonal Communication device; however it will be tested monthly. - Using the NXT Communicator, activate the “SO ENS Test” scenario between the hours of 0800-2200. - If any issues are found, open help ticket and cc: “shiftsupv”. |
| Log | Log all actions. |
| Alternate Control Center |  |
| Once a Month | - When working out of the alternate Control Room during the monthly scheduled dates, test each Alternative Interpersonal Communication devices as listed in steps below. |
| PBX | - Using the Nortel phone, make a call to an OPX extension - Make a log entry listing the device tested, who the test call was made to, and if it was successful. |
| PBX By-Pass | - Using the PBX By-Pass phone, make a long distance call - Make a log entry listing the device tested, who the test call was made to, and if it was successful. |
| Cell Phone | - Using the Control Room cell phone, make a call to the ERCOT Helpdesk cell phone. - Make a log entry listing the device tested, who the test call was made to, and if it was successful. |
| Stand Alone Satellite | - Using the Standalone Satellite phone, make a call (not necessary to call a satellite number). Refer to Desktop Guide Common to Multiple Desks Section 2.7.5. - Make a log entry listing the device tested, who the test call was made to, and if it was successful. |
| Satellite Modem | Coordinate the following test with the DC Tie Operator at the other control center. - Using the turret, call each programmed Satellite desk phone at the other control center - Make a log entry listing the device tested, who the test call was made to, and if it was successful. |
| Unsuccessful Test | IF: - Any of the above devices proved to be unsuccessful; THEN: - Open a help ticket and cc: “shiftsupv”, AND - Designate a replacement device (can one of the other Alternative devices adequately serve as a replacement, or can you use the same device from the alternate control center?) IF: - An Alternative device cannot serve as a replacement; THEN: - Ensure the help ticket knows that capability must be restored within 2 hours. |
| Replacement/ Alternative device Examples | Designate a replacement device: The [Device] phone on the [RUC] Desk at the Alternate Control Center will be used if needed until the [Device] phone on the [Supervisor] Desk is repaired. Alternative devices cannot serve as a replacement: All Alternative Interpersonal Communication phones at the Alternate Control Center and the same device from the Primary Control Center are inoperable. Helpdesk has been notified with a high priority ticket to restore one within 2 hours. |
| NXT Test | The NXT is not an Alternative Interpersonal Communication device; however it will be tested monthly. - Log into the Bastrop ENS link when working out of the alternate Control Room in Bastrop, - Using the NXT Communicator, activate the “SO ENS Test” scenario between the hours of 0800-2200. - If any issues are found, open help ticket and cc: “shiftsupv”. |
| Log | Log all actions. |

## 10.2		EMMS and Interface System Failures

Procedure Purpose: Provide guidance to the Shift Supervisor for coordinating with the ERCOT IT Help Desk if critical functions or systems fail such that system operators and/or participants are precluded from performing and complying with their obligations and therefore jeopardizing the security of the system.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 7.3.3(4) |  |  |  |
| NERC Standard | TOP-001-3 R9 |  |  |  |

| Version: 1 | Revision: 12 | Effective Date: March 31, 2017 |
| --- | --- | --- |

| Step |  | Action |  |
| --- | --- | --- | --- |
| 1 |  | If any Control Room computer systems (ICCP, Web Portal, MIS, or API) events, failures, or incidents that affect normal operations occur, - DETERMINE criticality and impact to the reliability to the grid, - CONTACT the ERCOT Help Desk immediately from the Supervisor Help Desk button on the Turret Phone or extension 6804. If necessary, contact the on-call IT person first then contact the Help Desk. |  |
| NOTE |  | For a complete EMMS failure, see Real-Time Procedure Section 3.1 Frequency Control Operating Procedure and 3.3 System Failures. |  |
| 2 |  | IF: - Any of the aforementioned systems fail and are effecting ERCOT systems or multiple TOs and/or QSEs and will be unavailable for longer than 15 minutes; THEN: - Notify TOs and QSEs of the problem and expected duration via Hotline, - Request additional assistance from other support staff. |  |
| 3 |  | When the problem is resolved, Notify all TOs and QSEs via Hotline of the problem resolution. |  |
| 4 |  | RECORD the following information: - Date - Time of event - Description of system alarms, events, failures, or incident - Actions taken and resolution - Time of system or function restoration |  |
| Log |  | Log all actions. |  |
| ## Data and/or Voice Communication Failures |  |  |  |
| 1 |  | Notify the Help Desk of the loss and REQUEST assistance to re-establish voice and/or data communications. - Telecommunications group will be responsible for voice communications. - EMMS Production group will be responsible for data communications |  |
| 2 |  | Use back-up communications if needed such as the Control Room cell phone, Standalone Satellite phone or the PBX Bypass phones to maintain communications with the other control room, TOs, QSEs, SPP and any other entities as needed. The list of phone numbers is located in the Phone Book at Shift Supervisor’s Desk and also programmed into the cell phone. |  |
| 3 |  | IF: - The criticality and impact of events or failures is such that TOs and/or QSEs are, or will be affected before the problem can be resolved, THEN: - Instruct ERCOT System Operator to NOTIFY the other ERCOT Control Room and all TOs and QSEs via Hotline of the problem and expected duration. If Hotline is unavailable utilize any of the following methods: - Control Room cell phone, PBX Bypass phones, or Standalone Satellite phone. - REQUEST additional assistance from other support staff, as needed. |  |
| NOTE |  | Steps 4 & 5 may be performed in any order. |  |
| 4 |  | RECORD the following: - Date - Time of event - Description of events, failures, or incident - Actions taken and resolution - Time of system or function restoration |  |
| 5 |  | When the problem is resolved, NOTIFY all participants via Hotline of the problem resolution. |  |
| Log |  | Log all actions. |  |
| ## Dynamic Rating, SCED Status, EMBP, SE, RTCA or RLC Alarms |  |  |  |
| NOTE |  | - Normal status for the Dynamic Rating, SCED Status, EMBP, SE, RTCA and RLC Status is indicated by each status box constant green on the “ERCOT & QSE Summary Page” in the PI system. - Failure of the PI server is indicated by abnormal status of Dynamic Rating, SE and RLC, accompanied by the PI system “flat-lining” - Dynamic Rating, SE and RLC status boxes flashing red AND PI flat-lining may indicate failure of the EMS. |  |
| Monitor |  | PERFORM the following as applicable to the indicated conditions: - IF only the Dynamic Ratings status box is flashing red, CONTACT the ERCOT Help Desk - TELL them the Dynamic Rating Alarm status in Processbook is flashing red and the dynamic ratings are not being sent to the SCADA in the EMS. - REQUEST they notify the on-call EMMS Production person of the situation. - IF only the RLC status box is flashing yellow/red, CONTACT the ERCOT Help Desk - TELL them the RLC Alarm status in Processbook is not green - Greater than 5 minutes but less than 10 minutes turns - Yellow - Greater than 10 minutes turns - Red - Instruct them to notify the on-call EMMS Production person of the situation. - IF only the SCED Status box is flashing red, - Follow the Managing SCED Failures in the Real Time Desk Procedure. - If SCED failure can’t be resolved CONTACT the ERCOT Help Desk and instruct them to notify the on-call EMMS Production person of the situation. - IF only the EMBP box is flashing red, - Determine the reason Emergency Base Point are being issued, - Remove the Emergency Base Point flag when condition allow, - If EMBP can’t be resolved CONTACT the ERCOT Help Desk and instruct them to notify the on-call EMMS Production person of the situation. - IF only the SE status box is flashing red, CONTACT the Operations Support Engineer - TELL them the SE Alarm status in Processbook is flashing red - IF only the RTCA status box is flashing yellow or red, CONTACT the Operations Support Engineer - RTCA executes every 5 minutes, if RTCA doesn’t complete within the desired threshold the display changes colors - Greater than 7 minutes but less than 10 minutes turns - Yellow - Greater than 10 minutes turns - Red - TELL them the RTCA Alarm status in Processbook is flashing yellow/red - Greater than 15 minutes, inform QSEs for STP and CPSES. |  |
| ## Building Security and Fire Alarms |  |  |  |
| NOTE | The Shift Supervisor or designee will ensure staff members adhere to emergency evacuation procedures and evacuate all team members from the Control Room if an emergency evacuation is required. |  |  |
| 1 | IF: - Building security or fire alarm sounds, THEN: - Contact Security’s Emergency Number if Security has not already made communications with the Control Room. |  |  |
| 2 | IF: - Control Room personnel are in danger or ordered to be evacuated, THEN: - Transfer control of the Grid to the Alternate Control Center (see “Loss of Primary Control Center Functionality” procedure Section 4.6 in the DC Tie Desk Procedure), - Request additional assistance from other support staff, - Evacuate the Control Room to a safe area for Zone #1, - Report to the Alternate Control Center if necessary. |  |  |
| 3 | Notify the Manager, System Operations and/or Designee as soon as practical. |  |  |
| ## Failure of the Emergency Generator |  |  |  |
| 1 | If the Facilities emergency generator fails to start, you will be notified by the Facilities Staff. |  |  |
| 2 | If the Facilities Staff or the Shift Supervisor determines that it will be more than 20 minutes before the emergency generator can be started, the Shift Supervisor may consider initiating the “Loss of Primary Control Center Functionality” procedure. |  |  |
| 3 | The Shift Supervisor or his/her delegated representative should notify the Manager, System Operations and/or Designee that the controls have been transferred to the other control center. |  |  |
| 4 | REQUEST additional assistance from other support staff as needed. |  |  |
| NOTE | See Desktop Guide Shift Supervisor Section 2.1. |  |  |
| ## Telemetering, Control Equipment and Communication Outages |  |  |  |
| NOTE | TOs are required to inform ERCOT of all planned outages, and unplanned outages of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between the affected entities. Telemetering, Control Equipment and Communication outages that ERCOT ISO has been made aware of can be found on the Outage Calendar located on the System Operations SharePoint. |  |  |
| Planned Outage | WHEN: - Notified of a planned outage by email; THEN: - Record the information on the Outage Calendar located on the System Operations SharePoint Site for coordination; IF: - The outage(s) cause State Estimator or Contingency Analysis solution issues; NOTIFY: - Shift Engineer as manual updates may be needed to correct any reliability issue; |  |  |
| Forced Outage | WHEN: - Notified of a forced outage; THEN: - Ask if the secondary/back up redundancy is available and functional; IF: - There is no redundancy available and functional; NOTIFY: - Shift Engineer as manual updates may be needed to correct issues with the State Estimator or Contingency Analysis solution. |  |  |
| Log | Log all actions. |  |  |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Frosch, Hartmann, Stone, and Barcalow | Preparers | November 10, 2010 |
| Frosch and Hartmann | Procedure writers and editors | November 29, 2010 |
| Frosch, Hartmann, and Moore | Procedure writers and editors | January 26, 2011 |
| Frosch and Hartmann | Procedure writers and editors | March 23, 2011 |
| Frosch and Hartmann | Procedure writers and editors | April 20, 2011 |
| Frosch and Hartmann | Procedure writers and editors | June 6, 2011 |
| Frosch and Hartmann | Procedure writers and editors | July 18, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 30, 2011 |
| Frosch and Hartmann | Procedure writers and editors | September 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | October 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 16, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | April 25, 2012 |
| Frosch and Hartmann | Procedure writers and editors | May 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | May 30, 2012 |
| Frosch and Hartmann | Procedure writers and editors | July 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | August 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | October 26, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 26, 2013 |
| Frosch and Hartmann | Procedure writers and editors | May 28, 2013 |
| Frosch and Hartmann | Procedure writers and editors | July 10, 2013 |
| Frosch and Hartmann | Procedure writers and editors | August 7, 2013 |
| Frosch and Hartmann | Procedure writers and editors | August 28, 2013 |
| Frosch and Hartmann | Procedure writers and editors | December 11, 2013 |
| Frosch and Hartmann | Procedure writers and editors | January 27, 2014 |
| Frosch, Gaddy, and Hartmann | Procedure writers and editors | April 1, 2014 |
| Frosch and Hartmann | Procedure writers and editors | May 27, 2014 |
| Frosch and Hartmann | Procedure writers and editors | July 29, 2014 |
| Frosch and Hartmann | Procedure writers and editors | September 29, 2014 |
| Frosch and Hartmann | Procedure writers and editors | December 10, 2014 |
| Frosch and Hartmann | Procedure writers and editors | February 25, 2015 |
| Frosch and Hartmann | Procedure writers and editors | March 25, 2015 |
| Frosch and Hartmann | Procedure writers and editors | April 29, 2015 |
| Frosch and Hartmann | Procedure writers and editors | July 13, 2015 |
| Frosch, Hartmann and Gaddy | Procedure writers and editors | September 25, 2015 |
| Frosch, Hartmann and Gaddy | Procedure writers and editors | December 22, 2015 |
| Frosch, Hartmann and Gaddy | Procedure writers and editors | February 23, 2016 |
| Hartmann and Gaddy | Procedure writers and editors | April 22, 2016 |
| Frosch, Hartmann and Gaddy | Procedure writers and editors | June 24, 2016 |
| Frosch, Hartmann and Gaddy | Procedure writers and editors | September 26, 2016 |
| Hartmann, Gaddy and Frosch | Procedure writers and editors | December 23, 2016 |
| Hartmann, Gaddy and Frosch | Procedure writers and editors | March 27, 2017 |

Manual Change History

| Procedure | Ver/Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All Sections | 1.0 / 0 | New procedures for all sections for Nodal implementation | November 28, 2010 |
| 3.1 4.2 6.1 10.2 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Updated steps 1 and 5, deleted steps 6, 7 and 8 Updated VDI, Testing Rules and Retest Updated PUCT Daily Report step “Update Report”. Updated all steps of Texas RE Event Reporting. Updated Title (Dynamic Rating, SCED Status, EMBP, SE, RTCA or RLC Alarms), 1st Note and Monitor | December 1, 2010 |
| 3.2 3.3 3.7 4.2 6.1 10.2 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 2 1.0 / 2 - / 2 | Updated step 1,3 and added step 4 in “Capacity Monitoring” Updated step 4 Updated step No SCED Solution Updated VDI, Retest, and Notify, added Completion Updated step OE-417 Reporting Events in NERC, DOE Reporting and step 2 on GEO-Magnetic Disturbance (GMD) Updated step Monitor on “Dynamic Rating, SCED Status, EMBP, SE, RTCA or RLC Alarms” | January 31, 2011 |
| 3.2 5.3 5.5 6.1 7.2 7.3 9.2 | 1.0 / 2 1.0 / 1 1.0 / 1 1.0 / 3 1.0 / 1 1.0 / 1 1.0 / 1 | Updated step 3 “Capacity Monitoring” Updated step 1 & 3 Updated 1st note & step 2 Updated PUCT Daily Report, Texas RE Event Reporting & NXT Notification Updated EEA Checklist Updated EEA Restoration Checklist Added new steps “SAT modem testing” & updated NXT Tests | March 25, 2011 |
| 4.2 5.1 7.1 7.3 | 1.0 / 3 1.0 / 1 1.0 / 1 1.0 / 1 | Updated “Unannounced Resource Testing” 1st note Updated 2nd & 6th paragraphs Updated “System Disturbance” NERC, step 2 and “Degraded Weather” step 3 Updated Table | April 22, 2011 |
| 5.3 5.7 6.1 7.1 7.4 7.5 7.6 8.3 | 1.0 / 2 1.0 / 1 1.0 / 4 1.0 / 2 1.0 / 1 1.0 / 0 1.0 / 1 1.0 / 1 | Updated step 2 Updated all steps Updated all steps in Texas RE Event Reporting and NERC and DOE Reporting Updated steps in Degraded Weather Updated all steps Added new procedure Updated all steps Updated step 2 and deleted step 3 | June 8, 2011 |
| 3.6 4.1 4.2 6.1 7.2 7.3 9.2 | 1.0 / 1 1.0 / 1 1.0 / 4 1.0 / 5 1.0 / 1 1.0 / 1 1.0 / 2 | Updated step 3 Removed Initial Synchronization of New Resource Updated Testing Rules Updated step Event List Updated EEA Implementation Checklist Updated EEA Restoration Checklist Added Notice Builder test in Primary Control Center section | July 20, 2011 |
| 4.2 5.5 6.1 7.2 7.3 7.7 9.2 10.1 | 1.0 / 5 1.0 / 2 1.0 / 6 1.0 / 2 1.0 / 3 1.0 / 0 1.0 / 3 1.0 / 1 | Updated step Caution Updated 1st Note Updated step 1 in Texas RE Event Reporting and NXT Testing in NXT Notification Requirements Updated EEA Implementation checklist Updated EEA Restoration checklist Added Extreme Hot Weather Updated NXT Test in Alternate Control Center Updated step 3 | September 1, 2011 |
| 3.4 6.1 7.2 7.3 9.2 | 1.0 / 1 1.0 / 7 1.0 / 2 1.0 / 3 1.0 / 4 | Grammar changes Combined EEA 2A & B per NPRR 379 Updated to implement NPRR 379 Updated to implement NPRR 379 Updated Phone Test in Alternate Control Center | October 1, 2011 |
| 3.7 7.2 10.2 | 1.0 / 2 1.0 / 3 1.0 / 3 | Changed title & all steps Updated EEA checklist Updated 1st Note | November 1, 2011 |
| 3.3 6.2 6.3 | 1.0 / 2 1.0 / 1 1.0 / 1 | Updated all steps Updated step 2 Updated step 1 & 2 All procedures in this manual have been reviewed. | December 15, 2011 |
| 1.2 4.2 5.7 | - / 1 - / 6 - / 2 | Updated Scope Updated all steps of procedure Updated Market Participant Backup Control Center Transfer | January 19, 2012 |
| 2.1 3.3 3.4 3.7 3.8 4.1 4.2 5.3 5.6 5.8 6.1 7.1 9.1 9.2 10.2 | 1.0 / 1 1.0 / 3 1.0 / 2 1.0 / 3 1.0 / 1 1.0 / 2 1.0 / 7 1.0 / 3 1.0 / 1 1.0 / 1 1.0 / 8 1.0 / 3 1.0 / 1 1.0 / 5 1.0 / 4 | Updated paragraph 4 Updated Step 3 Updated Threat & Emergency Classifications & Desktop Guide reference Changed Shift Engineer to Operations Support Corrected grammar on step 1 Changed Shift Engineer to Operations Support Updated procedure Changed Shift Engineer to Operations Support Corrected grammar on step 2 Updated step 2 Updated Texas RE Event Reporting, OE-417 reporting & Desktop Guide reference Updated Desktop Guide reference Updated Desktop Guide reference Updated Desktop Guide reference Changed Shift Engineer to Operations Support and updated Desktop Guide reference | March 1, 2012 |
| 2.1 3.3 3.6 5.6 6.1 7.1 7.4 7.5 7.6 | 1.0 / 2 1.0 / 4 1.0 / 2 1.0 / 2 1.0 / 9 1.0 / 4 1.0 / 2 1.0 / 2 1.0 / 2 | Changed TSP/DSP to TO Updated 3rd Note Updated purpose Changed TSP to TO and Transmission Facility Updated step Update Report & changed ARR to PRC and ERCOT Morning Report Updated step NERC and Degraded Weather Updated OCN, Advisory, & Watch steps Deleted Cold Weather, not Extreme Cold Weather Section number changed, Added OCN, Advisory and Emergency Notice | May 1, 2012 |
| 3.2 | 1.0 / 3 | Updated to reflect changes in the TAC approved Non-Spin document | May 14, 2012 |
| 7.2 7.3 | 1.0 / 3 1.0 / 4 | Updated EILS to ERS per NPRR 451 & added TO load management program Updated EILS to ERS per NPRR 451 & added TO load management program | June 1, 2012 |
| 3.3 4.2 6.1 | 1.0 / 5 1.0 / 8 1.0 / 10 | Updated step 3 Added Desktop Guide to VDI reference Updated PUCT Daily Report, NERC and DOE Reporting and RCIS Posting | July 16, 2012 |
| 3.4 4.2 5.9 6.1 7.2 | 1.0 / 3 1.0 / 9 1.0 / 1 1.0 / 11 1.0 / 4 | Added CPT to procedure and Typical Subject line for e-mail Added Log to procedure Deleted Procedure Updated NERC and DOE Reporting Added 30 MIN ERS deployed to EEA 1 | August 29, 2012 |
| 2.2 3.1 5.3 6.1 7.6 9.1 | 1.0 / 1 1.0 / 2 1.0 / 4 1.0 / 12 1.0 / 3 1.0 / 2 | Added Hotline Call Communication Updated step 5 Updated and added Planned and Forced Outage sections. Added Weather Information section to PUCT Daily Report. Updated step 1 in NERC and DOE Reporting and ERCOT Morning Report section. Updated OCN, Advisory, & Watch Updated step E-mail All procedures in this manual have been reviewed. | November 1, 2012 |
| 3.2 3.3 3.4 3.5 3.6 3.7 3.8 4.1 5.2 5.3 5.5 5.6 5.8 6.1 6.2 6.3 7.4 7.5 7.6 8.3 8.6 9.2 10.1 10.2 11.0 | 1.0 / 4 1.0 / 6 1.0 / 4 1.0 / 1 1.0 / 3 1.0 / 4 1.0 / 2 1.0 / 3 1.0 / 1 1.0 / 5 1.0 / 3 1.0 / 3 1.0 / 2 1.0 / 13 1.0 / 2 1.0 / 2 1.0 / 3 1.0 / 3 1.0 / 4 1.0 / 2 1.0 / 1 1.0 / 6 1.0 / 2 1.0 / 5 1.0 / 1 | Updated step 1, Capacity Monitoring and deleted Reserve Monitoring Updated step 3 Updated notes and Management Notifications Updated purpose and step 1 Updated step 2 Updated step TCM & renamed LMP Map Delete procedure for large wind ramp events Updated step 1 Grammatical correction Updated step 3 Protective Relay or Equipment Failure Added MISO Reliability Coordinator Updated step 2 TO Temporary Equipment Limitation Notifications Updated purpose Updated step 1 Texas RE Event Reporting, Note and step 1 NERC and DOE Reporting, Loss of Firm Load NXT Notification Requirements, step 1 Weather Information section to ERCOT Morning Report, step 1 RMR Unexcused Misconduct Events, GMD, step 2 Gas Restrictions and added Special Protection Systems (SPSs) Deleted procedure Renamed to 6.2 and updated procedure Updated step Reporting Updated step Reporting Updated Log Updated step 2 Updated procedure Deleted Notice Builder Updated step 3 Updated step monitor, step 4 Building Security and Fire Alarms and step 3 Failure of the Emergency Generator Updated procedure Review New Communications from Manager and/or Control Room Operations Manager and step 4 Implement ERCOT Personnel and Company Standards | March 1, 2013 |
| 3.3 3.4 6.1 | 1.0 / 7 1.0 / 5 1.0 / 14 | Updated all steps Added 1st Note, deleted 2nd & 3rd Notes, Management Notification, updated QSE Notification, TO Notification Updated step Update Report | June 1, 2013 |
| 4.1 5.1 6.1 10.2 | 1.0 / 4 1.0 / 2 1.0 / 15 1.0 / 6 | Updated Ancillary Service Testing Coordination and added Coordinated Reactive Tests Added MISO Updated PUCT Daily Report & step 1 on NERC and DOE Reporting and added Note to NXT Notification Requirements Updated 1st Note and step #3 on Building Security and Fire Alarms | July 15, 2013 |
| 3.4 4.1 6.1 7.3 | 1.0 / 6 1.0 / 5 1.0 / 16 1.0 / 5 | Updated QSE Notification, TO Notification & Send E-mail Updated Coordinated Reactive Tests Added 7-Day Outlook, updated Event List on Texas RE Event Reporting & step 2 on GEO-Magnetic Disturbance (GMD) Updated table | August 9, 2013 |
| 3.3 | 1.0 / 8 | Removed HHGT TO reference | August 30, 2013 |
| 3.3 3.4 4.1 4.2 5.3 5.4 5.6 5.7 6.1 7.6 8.1 8.2 8.3 9.1 9.2 10.2 | 1.0 / 9 1.0 / 7 1.0 / 6 1.0 / 10 1.0 / 6 1.0 / 1 1.0 / 4 1.0 / 3 1.0 / 17 1.0 / 5 1.0 / 1 1.0 / 1 1.0 / 3 1.0 / 3 1.0 / 7 1.0 / 7 | Updated step 1 and Log Updated step Log Updated step Log Updated step Log Updated step 4, Planned Outage, Forced Outage and added Log Updated step Log Updated step Log Updated step 1 and added Log Updated step Update Report, TRE Event Reporting changed to Event Analysis Report and event list updated, and NERC and DOE Reporting updated Added step Issues and updated Log Updated step 3 and added Log Updated step 3, 5 and added Log Updated step 3 Updated step Log Updated steps Log Added step 4 and updated Log All procedures in this manual have been reviewed. | December 13, 2013 |
| 4.1 6.1 7.2 7.3 | 1.0 / 7 1.0 / 18 1.0 / 5 1.0 / 6 | Updated for NOGRR125 & OK to test on Coordinated Reactive Tests Updated NERC and DOE Reporting Updated EEA Implementation Checklist Updated EEA Restoration Checklist | January 29, 2014 |
| 3.2 4.2 5.5 6.1 6.2 | 1.0 / 5 1.0 / 11 1.0 / 4 1.0 / 19 1.0 / 3 | Updated VDI information Updated VDI information Updated Note Updated Update Report on PUCT Daily Report and step 1 on NERC and DOE Reporting Updated step 1 | April 4, 2014 |
| 2.2 7.1 | 1.0 / 2 1.0 / 5 | Added VDIs to Master QSEs Updated step 1 | June 1, 2014 |
| 4.2 6.1 6.2 7.2 | 1.0 / 12 1.0 / 20 1.0 / 4 1.0 / 6 | Updated 1st Note, Retest and added Demonstration Test Updated step Update Report Updated steps 1 & 4 Updated checklist | August 1, 2014 |
| 3.3 3.4 4.1 4.2 9.2 | 1.0 / 10 1.0 / 8 1.0 / 8 1.0 / 13 1.0 / 8 | Added step 2 Corrected spelling on Send E-mail Updated script for Unit Testing Added new reference Updated new section on Phone Tests | October 1, 2014 |
| 3.6 3.7 4.2 6.1 | 1.0 / 4 1.0 / 5 1.0 / 14 1.0 / 21 | Changed title and removed references to W-N Added step RTMONI Updated Testing Rules and Scripts Added 2nd note to NERC and DOE Reporting & updated GMD procedure All procedures in this manual have been reviewed | December 15, 2014 |
| 2.2 3.2 3.3 4.2 5.3 5.5 6.1 7.2 7.5 | 1.0 / 3 1.0 / 6 1.0 / 11 1.0 / 14 1.0 / 7 1.0 / 5 1.0 / 22 1.0 / 7 1.0 / 4 | Added Dispatch and VDI definitions Updated step 4 Updated step 1 in Suspected Sabotage or Sabotage Events Moved procedure to Resource desk Updated title and added Protection System Setting Notifications Added Switchable Generation Resource Added Unit Trip Posting Updated checklist Updated Note | March 1, 2015 |
| 5.3 6.1 | 1.0 / 8 1.0 / 23 | Clarification to step 2 Clarifications to GMD procedure | March 30, 2015 |
| 3.3 3.4 3.6 3.7 4.1 5.6 6.1 6.2 7.6 8.3 8.6 10.1 10.2 11 | 1.0 / 12 1.0 / 9 1.0 / 5 1.0 / 6 1.0 / 9 1.0 / 5 1.0 / 24 1.0 / 5 1.0 / 6 1.0 / 4 1.0 / 2 1.0 / 3 1.0 / 8 1.0 / 2 | Updated contact information Updated contact information Updated contact information Updated contact information Updated contact information Updated contact information Updated contact information Updated contact information Updated contact information Updated contact information Updated contact information Updated contact information Updated contact information Updated contact information | May 1, 2015 |
| 6.1 10.2 | 1.0 / 25 1.0 / 9 | Updated GMD procedure Added new Telemetering, Control Equipment and Communication Outages process | July 15, 2015 |
| 9.1 9.2 9.3 9.4 | 1.0 / 0 1.0 / 0 1.0 / 9 1.0 / 4 | New procedure for COM-001-2 New procedure for COM-001-2 Updated procedure for COM-001-2 Updated section number | October 1, 2015 |
| 6.1 7.2 9.3 | 1.0 / 26 1.0 / 8 1.0 / 10 | Updated Event Analysis Reporting step Event List Implement NPRR708 for EEA Added Primary Control Center step Replacement/Alternative Device Examples Added Alternate Control System step Replacement/Alternative Device Examples All procedures in this manual have been reviewed | December 31, 2015 |
| 2.1 6.1 | 1.0 / 3 1.0 / 27 | Updated System Operator Responsibility and Authority Updated Guidelines for Determining EEA Potential | March 1, 2016 |
| 5.3 10.2 | 1.0 / 9 1.0 / 10 | Updated Protective Relay or Equipment Failure step 2 Deleted step 2 and updated step 3 | April 29, 2016 |
| 2.1 2.2 3.2 4.1 5.37.2 7.3 8.2 8.6 10.2 | 1.0 / 4 1.0 / 4 1.0 / 7 1.0 / 10 1.0 / 10 1.0 / 9 1.0 / 7 1.0 / 2 1.0 / 3 1.0 / 11 | Updated steps for COM-002-4 Updated steps for COM-002-4 Updated steps for COM-002-4 Updated steps for COM-002-4 Updated Protection System Setting Notification Updated steps for COM-002-4 Updated steps for COM-002-4 Updated steps for COM-002-4 Updated steps for COM-002-4 Updated steps for COM-002-4 | June 30, 2016 |
| 3.3 6.1 7.2 10.1 | 1.0 / 13 1.0 / 28 1.0 / 9 1.0 / 4 | Updated step Updated Step 1 of NERC and DOE Reporting Updated checklist Updated step 2 | September 30, 2016 |
| 3.3 4.1 5.5 6.1 | 1.0 / 14 1.0 / 11 1.0 / 6 1.0 / 29 | Updated Note Added Unit Testing Note Updated Approved Resources to be ONTEST Step Approval Deleted Turbine Governor Updated Note, renamed SPS to RAS & updated RAS Updated Event Analysis Reporting Step Event List, Event Reporting EOP-004-2 & Step 1 Renamed Special Protection Systems (SPS) to Remedial Action Schemes (RAS) & updated Remedial Action Schemes (RAS) All procedures in this manual have been reviewed | December 30, 2016 |
| 2.1 3.4 4.1 5.1 5.3 5.4 5.5 5.6 5.7 5.9 6.1 7.2 7.6 9.1 9.2 9.3 10.2 | 1.0 / 5 1.0 / 10 1.0 / 12 1.0 / 3 1.0 / 11 1.0 / 2 1.0 / 7 1.0 / 6 1.0 / 4 1.0 / 0 1.0 / 30 1.0 / 10 1.0 / 7 1.0 / 1 1.0 / 1 1.0 / 11 1.0 / 12 | Updated for IRO-001-4 Updated Threat & Emergency Classifications step Updated In Service Approval step 1 Deleted paragraph to create new procedure in 5.9 Updated CFE to CENACE Updated Protective Relay Outages step Updated second note, step 5 & 6 Updated CFE to CENACE Updated TO Temporary Equipment Limitation Notifications step 2 Updated Heading title and step 1 New procedure for IRO-002-4 R2 Updated with Event Analysis v3.1 changes and EOP-004-3 and EOP-011 Updated checklist Updated title Updated step 1 Updated step 2 Updated Satellite Modem Updated TOs, QSEs along with Telemetering, Control Equipment and Communication Outages | March 31, 2017 |