- Power Operations Bulletin # 796

ERCOT has posted/revised the Resource Desk manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

- http://www.ercot.com/mktrules/guides/procedures/index.html

## 7.2	Implement EEA Levels

Procedure Purpose:  To provide for maximum possible continuity of service while maintaining the integrity of the ERCOT system to reduce the chance of cascading outages.

| Protocol Reference | 6.5.7.6.2.2(1)(b) & (13) | 6.5.9.4 | 6.5.9.4.2 |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.5.3 | 4.5.3.1 | 4.5.3.2 | 4.5.3.3 |
|  | 4.5.3.4 |  |  |  |
| NERC Standard | EOP-011-1 R2.1, R2.2.3, R2.2.3.1, R2.2.3.4, R2.2.7 | IRO-001-4 R1 | TOP-001-3 R2 |  |

| Version: 1 | Revision: 19 | Effective Date: June 30, 2017 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - IF steady state system frequency falls below 59.91 Hz, ERCOT CAN immediately implement EEA 3. - IF steady state system frequency falls below 59.5 Hz, ERCOT SHALL immediately implement EEA 3. |
| ERS-30 | ERS with a thirty-minute ramp period. |
| ERS-10 | ERS with a ten-minute ramp period. |
| WS-ERS | Each Standard Contract Term(SCT) Request for Proposal (RFP) will state what time periods in that SCT weather sensitive can provide offers for. |
| TCEQ | When increased generation is requested during EEA events, Texas Commission on Environmental Quality (TCEQ) will exercise enforcement discretion for exceedances of emission limits as well as operational limits for power generating plants for Generators who exceed air permit limits in order to maximize generation for the duration of the EEA event. ERCOT General Council will send out a Market Notice each time ERCOT enters into an EEA with this reminder. |
| ### Implement EEA Level 1 |  |
| 1 | IF: - PRC < 2300 MW; THEN: - Deploy all available Non-Spin (if not previously deployed) (see Desktop Guide Resource Desk Section 2.1.1). - Determine whether system conditions require the deployment of ERS-30 (see Desktop Guide Resource Desk Section 2.3.2). - Make EEA 1 posting to MIS Public - Use preformatted notice “EEA Level 1” |
| 2 | IF: - ERS-30 is deployed; THEN: - Also deploy WS ERS if available - Notify the Real-Time Operator when XML message has been completed. ERS must be deployed before hotline call is made. |
| 3 | Verify all measures have been implemented. |
| Log | Log all actions. |
| ### Implement EEA Level 2 |  |
| 1 | IF: - PRC < 1750 MW or unable to maintain system frequency at 59.91 Hz and is not projected to be recovered above 1750 MW within 30 minutes without the use of EEA Level 2; THEN: - Determine when system conditions require the deployment of ERS-30 / ERS-10 / Load Resources - (Do Not forget the WS ERS if available): - Deploy ERS-30 if not already done in EEA1 - Deploy ERS-10 - Deploy Load Resources Group 1 and/or 2 - Notify the Real-Time Operator when XML message has been completed. ERS / Load Resources/ must be deployed first before hotline call is made, - Desktop Guide Resource Desk (Section 2.2.1 for Load Resources; Section 2.3.2 for ERS). - Make EEA 2 posting to MIS Public - Use preformatted notice “EEA Level 2” |
| ERS Time Period Changes | IF: - ERS Resources are deployed, and the Time Period is changing and if ERS is still needed; THEN: - Deploy next Time Period - Take into consideration the time requirement for the ERS-10 and ERS-30 - Notify the Real-Time Operator when XML message has been completed. ERS must be deployed before hotline call is made. |
| 2 | IF: Went straight to EEA Level 2; THEN: - Ensure tasks in EEA Level 1 are complete. |
| 3 | Verify all measures have been implemented. |
| Log | Log all actions. |
| ### Implement EEA Level 3 |  |
| PRC <1375 MW | ERCOT will declare an EEA Level 3 when PRC cannot be maintained above 1,375 MW. IF: - PRC <1375; THEN: - Make EEA3 posting to MIS Public. ## Typical MIS Public Posting: At [time] ERCOT has entered EEA 3 for PRC less than 1375 MW. Firm Load Shed has not been instructed by ERCOT. |
| EEA3 Unable to Maintain 59.91 Hz or PRC <1000 MW | IF: - PRC <1000 MW and is not projected to be recovered above 1,000 MW within 30 minutes or unable to maintain system frequency at 59.91 Hz for 25 consecutive minutes; THEN: - Make EEA 3 posting to MIS Public - Use preformatted notice “EEA Level 3” |
| 1 | Verify all measures have been implemented. |
| Log | Log all actions. |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Frosch, Hartmann, Stone, and Barcalow | Preparers | November 10, 2010 |
| Frosch and Hartmann | Procedure writers and editors | November 29, 2010 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2010 |
| Frosch and Hartmann | Procedure writers and editors | January 26, 2011 |
| Frosch and Hartmann | Procedure writers and editors | March 23, 2011 |
| Frosch and Hartmann | Procedure writers and editors | April 20, 2011 |
| Frosch and Hartmann | Procedure writers and editors | May 10, 2011 |
| Frosch and Hartmann | Procedure writers and editors | June 6, 2011 |
| Frosch and Hartmann | Procedure writers and editors | July 18, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 30, 2011 |
| Frosch and Hartmann | Procedure writers and editors | September 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | October 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 16, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | April 25, 2012 |
| Frosch and Hartmann | Procedure writers and editors | May 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | May 30, 2012 |
| Barcalow, Frosch and Hartmann | Procedure writers and editors | July 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | August 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | October 26, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 26, 2013 |
| Frosch and Hartmann | Procedure writers and editors | May 28, 2013 |
| Frosch and Hartmann | Procedure writers and editors | July 8, 2013 |
| Cheng, Frosch and Hartmann | Procedure writers and editors | August 7, 2013 |
| Frosch and Hartmann | Procedure writers and editors | September 25, 2013 |
| Frosch and Hartmann | Procedure writers and editors | December 11, 2013 |
| Frosch, Gaddy and Hartmann | Procedure writers and editors | April 1, 2014 |
| Frosch, Gaddy and Hartmann | Procedure writers and editors | May 27, 2014 |
| Frosch and Hartmann | Procedure writers and editors | July 29, 2014 |
| Frosch and Hartmann | Procedure writers and editors | September 29, 2014 |
| Frosch and Hartmann | Procedure writers and editors | December 10, 2014 |
| Frosch and Thompson | Procedure writers and editors | December 19, 2014 |
| Frosch and Hartmann | Procedure writers and editors | February 25, 2015 |
| Frosch and Hartmann | Procedure writers and editors | April 29, 2015 |
| Frosch and Hartmann | Procedure writers and editors | July 13, 2015 |
| Hartmann and Gaddy | Procedure writers and editors | September 4, 2015 |
| Hartmann and Gaddy | Procedure writers and editors | September 25, 2015 |
| Frosch, Gaddy and Hartmann | Procedure writers and editors | October 27, 2015 |
| Hartmann and Gaddy | Procedure writers and editors | December 22, 2015 |
| Hartmann, Gaddy and Frosch | Procedure writers and editors | January 22, 2016 |
| Hartmann and Gaddy | Procedure writers and editors | February 23, 2016 |
| Hartmann and Gaddy | Procedure writers and editors | April 22, 2016 |
| Hartmann, Gaddy and Frosch | Procedure writers and editors | June 24, 2016 |
| Hartmann and Gaddy | Procedure writers and editors | December 23, 2016 |
| Hartmann, Gaddy and Frosch | Procedure writers and editors | March 27, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | May 26, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | June 23, 2017 |

Manual Change History

| Procedure | Ver/Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All Sections | 1.0 / 0 | New procedures for all sections for Nodal implementation | November 28, 2010 |
| 3.1 3.4 3.5 3.7 4.1 5.1 5.1 5.2 6.1 7.2 | 1.0 / 1 1.0 / 1 - / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Deleted WGR section, in section “Monitor QSE Ancillary Services Obligation”, updated step Infeasible A/S Capacity from RUC & A/S Difference in COP Updated Note Updated step 3 Updated whole procedure Updated step 2 In section “Procurement of Ancillary Services due to DAM Failure”, “ERCOT Increases the Amount of Ancillary Services”, “Replacement of Ancillary Service Due to Infeasibility/Failure to Provide”, “Replacement of Ancillary Services in Real Time”, Updated step 1 Updated whole procedure In section “Timeline Deviations”, Updated 2nd Note In section “Returning from Planned Outage Early”, Updated Deny In section “Implement EEA Level 1”, Updated step 1 | December 1, 2010 |
| 3.1 3.7 3.8 5.1 | 1.0 / 2 1.0 / 2 1.0 / 0 1.0 / 2 | Deleted “Monitor Base Point Deviations” and updated “A/S Difference in COP” Deleted step Note, Deployment, & Termination New Procedure Updated “Procurement of Ancillary Services due to DAM Failure”, “ERCOT Increases the Amount of Ancillary Services” and “Replacement of Ancillary Service Due to Infeasibility/Failure to Provide“ step 3 and 4 | December 15, 2010 |
| 3.1 3.2 3.4 3.3 3.5 3.7 4.1 5.1 5.2 7.1 7.2 7.3 8.2 | 1.0 / 3 1.0 / 1 1.0 / 2 1.0 / 1 1.0/ 2 1.0 / 3 1.0 / 2 1.0 / 3 - / 2 - / 1 - / 2 1.0 / 1 1.0 / 1 | Updated step Telemetered Status, step 1 in Manual Override Checks and removed workaround step “Real Time A/S shortage” in Monitor QSE Ancillary Services Obligation Updated all steps Updated steps “Deployment” and “Termination” Updated step 1 on “Cancelation” Updated all steps and added note Updated all steps Updated and deleted Notes and step 1 Updated “Procurement of Ancillary Services due to DAM Failure”, “ERCOT Increases the Amount of Ancillary Services”, “Replacement of Ancillary Service Due to Infeasibility/Failure to Provide“ step 3 and added note on Replacement of Ancillary Services in Real Time Updated Second Note on “Timeline Deviations” Updated Hotline on “Scripts” Updated Step 1 on ” Implement EEA Level 1” and “Implement EEA Level 2A” Updated Steps 1 on “Move from EEA Level 3 to EEA Level 2B” and “Cancel Watch” Deleted Site Failover Notification procedure & changed 8.3 to 8.2 | January 31, 2011 |
| 3.3 3.4 3.7 5.1 7.1 | 1.0 / 2 1.0 / 3 1.0 / 4 1.0 / 4 1.0 / 2 | Updated step 1 in “Watch” & step 1 in “Cancelation” Updated “Deployment” and “Termination” Updated “Issue Watch & Deploy Non-Spin” and “Recall Non-Spin” Updated step 2 in “Replacement of Ancillary Service Due to Infeasibility/Failure to Provide” Updated “Watch” and “Emergency Notice” | March 25, 2011 |
| 3.5 7.1 7.3 | 1.0 / 3 1.0 / 3 1.0 / 2 | Updated NERC Recovery Criteria Updated step 1 in Watch and Emergency Notice and step Post Updated 1st and 2nd script in Restore Firm Load, Updated 1st in Move From EEA Level 3 to EEA Level 2B | April 22, 2011 |
| 3.8 3.9 5.1 8.1 | 1.0 / 0 1.0 / 1 1.0 / 5 1.0 / 1 | Added new procedure Changed section number from 3.8 to 3.9 Updated steps 3-5 in Replacement of A/S due to Infeasibility/Failure to Provide, deleted Replacement of A/S in Real-Time Change section name, updated step 2 & 3 | May 11, 2011 |
| 3.3 3.4 3.6 3.7 3.8 7.1 | 1.0 / 3 1.0 / 4 1.0 / 1 1.0 / 5 1.0 / 1 1.0 / 4 | Updated step 1 in Advisory and Watch Updated step Deployment Updated step 1 Updated step Deploy Non-Spin & Post & Deploy Load Resources & Post Updated step Post Updated all steps | June 8, 2011 |
| 3.3 3.4 3.5 3.8 4.1 5.2 7.1 7.2 7.3 9.1 | 1.0 / 4 1.0 / 5 1.0 / 4 - / 2 1.0 / 3 1.0 / 3 1.0 / 5 1.0 / 3 1.0 / 3 1.0 / 1 | Updated step 1 in Advisory and Watch Updated step on Deployment Updated step on PRC Below 2300 Added step Termination, updated steps on Post and Cancel Posting Updated step 2 in Approve/Reject Decommitment QSE Requests in Operating Period Updated step 1 and deleted 2nd note in Timeline Deviations Updated step Watch Updated all steps Updated all steps Added Market Participant Backup Control Center Transfer procedure | July 20, 2011 |
| 3.3 3.4 5.1 7.1 7.2 7.3 8.2 | 1.0 / 5 1.0 / 6 1.0 / 6 1.0 / 6 - / 4 1.0 / 4 1.0 / 2 | Updated step 1 in Cancelation Updated Note, added steps Additional Deployment & Commit, updated steps Note & Deployment Updated 1st Note Added projected reserve capacity shortage and Extreme Hot Weather in Watch Updated 2nd Note, step 1 & 2 in EEA Level 1, step 1 in EEA Level 2A, added note in EEA Level 2B Updated step 1 in Cancel Watch Updated 4th Note and step 1 | September 1, 2011 |
| 7.2 7.3 8.1 | 1.0 / 5 1.0 / 5 1.0 / 2 | Combined EEA 2A & B per NPRR 379 Combined EEA 2A & B per NPRR 379 Updated step 2 | October 1, 2011 |
| 3.1 3.4 3.6 3.8 3.9 4.1 5.1 8.1 | 1.0 / 4 1.0 / 7 1.0 / 2 1.0 / 3 1.0 / 2 1.0 / 4 1.0 / 7 1.0 / 3 | Changed desktop guide reference in Monitor QSE Ancillary Services Obligation Updated step Commit Updated procedure title and all steps Updated steps 1 & Termination, added step 2 Deleted procedure due to protocol change Added 2nd Note Updated steps 1 – 3 in Procurement of A/S due to DAM Failure, steps 1 -2 in ERCOT Increased the Amount of A/S, steps 1 & 4 in Replacement of A/S Due to Infeasibility/Failure to Provide Added Note 2 & 3 | November 1, 2011 |
| 3.3 3.4 3.7 3.8 7.1 | 1.0 / 6 1.0 / 8 1.0 / 6 1.0 / 4 1.0 / 7 | Add Note in Watch Added second Note Added second Note Added Note Updated Post in “Scripts” All procedures in this manual have been reviewed. | December 15, 2011 |
| 1.2 3.1 3.4 4.1 5.1 | 1.0 / 1 1.0 / 5 1.0 / 9 1.0 / 5 1.0 / 8 | Updated Scope Updated Monitor QSE A/S Obligation procedure Updated 1st Note Updated steps 1 & 2 Updated step 2, 3 & 4 | January 19, 2012 |
| 2.1 3.1 3.3 3.4 3.5 3.7 3.8 4.1 5.1 7.1 7.2 7.3 8.2 9.1 | 1.0 / 1 1.0 / 6 1.0 / 7 1.0 / 10 1.0 / 5 1.0 / 7 1.0 / 5 1.0 / 6 1.0 / 9 1.0 / 8 1.0 / 6 1.0 / 6 1.0 / 3 1.0 / 2 | Updated paragraph 4 Updated Desktop Guide references Updated Desktop Guide references Updated Desktop Guide references Updated Desktop Guide references Updated Desktop Guide references Updated Desktop Guide references Updated 1st Note & step 1 Updated Desktop Guide references, step 3s & 4 Updated step 1 of Watch Updated Desktop Guide references Updated Desktop Guide references Updated Desktop Guide references Updated QSE Override, QSE unable to Override, Backup/Alternate Control Center Transfer, QSE Issues & step Power System Stabilizers (PSS) & Automatic Voltage Regulators (AVR) | March 1, 2012 |
| 2.1 3.1 3.5 3.6 3.7 4.1 5.1 7.1 9.1 | 1.0 / 2 1.0 / 7 1.0 / 6 1.0 / 3 1.0 / 6 1.0 / 7 1.0 / 10 1.0 / 9 1.0 / 3 | Changed TSP/DP to TO Updated step Not Dispatchable to SCED Deleted Potential DCS Event, changed section number for System Failures Changed section number Changed section number & added step 3 Updated step 1 Updated information needed in e-mail Updated all step 1’s Changed Shift Engineer to Ops Support Engineer | May 1, 2012 |
| 3.3 3.4 | 1.0 / 8 1.0 / 11 | Updated to reflect changes in the TAC approved Non-Spin document Updated to reflect changes in the TAC approved Non-Spin document | May 14, 2012 |
| 7.2 7.3 | 1.0 / 7 1.0 / 7 | Updated EILS to ERS per NPRR 451 Updated EILS to ERS per NPRR 451 | June 1, 2012 |
| 1.3 4.1 6.1 7.1 7.2 7.3 8.2 | 1.0 / 1 1.0 / 8 1.0 / 2 1.0 / 10 1.0 / 8 1.0 / 8 1.0 / 4 | Removed ERCOT Shift Supervisor paragraph Added Desktop Guide to VDI reference Added Desktop Guide to VDI reference and updated Maintenance Level 2 and 3 outages Updated all step 1’s Added Desktop Guide to VDI reference, updated step 1 Implement EEA Level 2 and added ERS Updated step 1 Move from EEA Level 3 to EEA Level 2 Updated 4th note | July 16, 2012 |
| 3.1 7.2 | 1.0 / 8 1.0 / 9 | Updated step ONTEST Updated step 1 of Implement EEA Level 1 | August 29, 2012 |
| 2.2 7.2 8.1 | 1.0 / 1 1.0 / 10 1.0 / 4 | Added Hotline Call Communication Updated Implement EEA Level 1 step 2, Implement EEA Level 2 step 1 and ERS Business Hour Changes Updated 1st Note, step 1, 2 & 3. Added step 4 and Log All procedures in this manual have been reviewed. | November 1, 2012 |
| 3.3 3.4 3.6 3.7 4.1 5.1 7.3 | 1.0 / 9 1.0 /12 1.0 / 9 1.0 / 7 1.0 / 8 1.0 / 11 1.0 / 9 | Non-Spin deployment messages are now automated Non-Spin deployment messages are now automated Non-Spin deployment messages are now automated Non-Spin deployment messages are now automated Updated steps 1 & 2 Updated steps Note, Procurement Timeline & 1. Added new procedure, Daily Reconfiguration SASM Updated step 1 of Cancel Watch | March 1, 2013 |
| 3.3 3.5 5.1 5.2 7.1 7.2 7.3 8.1 9.1 | 1.0 / 10 1.0 / 4 1.0 / 12 1.0 / 4 1.0 / 11 1.0 / 11 1.0 / 10 1.0 / 5 1.0 / 4 | Removed notice builder reference Removed notice builder reference Updated steps 1 & 5 in ERCOT Increased the amount of A/S & steps in Daily Reconfiguration SASM Updated step 1 Updated Scripts Removed notice builder reference & Updated Scripts Removed notice builder reference Updated Script Updated Script | June 1, 2013 |
| 3.1 7.1 | 1.0 / 9 1.0 / 12 | Deleted 1st Note, added step Log, moved Not Dispatchable to SCED, Control Block Up/Down, & Real-Time RRS A/S Shortages to Real-Time procedure, deleted Manual Override Checks Updated step 1 in Watch & Emergency Notice | July 15, 2013 |
| 5.1 5.2 | 1.0 / 13 1.0 / 5 | Updated 1st Note for R4 changes, Daily SASM Timeline Updated 1st Note for R4 changes | August 9, 2013 |
| 5.1 6.1 | 1.0 / 14 1.0 / 3 | Updated 1st Note, Daily SASM Timeline Updated to reflect SCR770 changes | September 27, 2013 |
| 3.1 3.2 3.3 3.5 3.6 3.7 4.1 5.1 6.1 6.2 7.1 7.2 7.4 8.2 9.1 | 1.0 / 10 1.0 / 2 1.0 / 11 1.0 / 5 1.0 / 10 1.0 / 8 1.0 / 10 1.0 / 15 1.0 / 4 1.0 / 1 1.0 / 13 1.0 / 12 1.0 / 1 1.0 / 5 1.0 / 5 | Added Monitor QSE A/S Obligation Title Updated Evaluate Request Updated step Log Updated step Log Updated step Log Updated step Log Updated step 3 Updated step Log Updated Accept Maintenance Outage, Coordinate Maintenance Outage, Coordinate Maintenance Level 2 and 3 and Log Updated step Log Updated step Log Updated last step and added Log Updated step Log Updated step Log Updated and added step Log All procedures in this manual have been reviewed. | December 13, 2013 |
| 3.4 3.5 3.74.1 6.1 7.1 7.2 7.3 8.1 | 1.0 / 13 1.0 / 7 1.0 / 9 1.0 / 11 1.0 / 5 1.0 / 14 1.0 / 13 1.0 / 11 1.0 / 6 | Updated VDI information Updated for NPRR542 Updated VDI information Updated VDI information Updated VDI information Updated to incorporate NPRR542 Updated ERS, Media appeal, TCEQ, VDI language, and moved steps to RUC desk Updated Reserves and step 1 Updated step 1 & 3, added step 5 | April 4, 2014 |
| 2.2 3.1 3.3 3.4 4.1 5.1 5.2 7.1 | 1.0 / 2 1.0 / 11 1.0 / 12 1.0 / 14 1.0 / 12 1.0 / 16 1.0 / 6 1.0 / 15 | Added VDIs to Master QSEs Updated Monitor QSE AS Obligations steps Updated steps in Watch Updated title, step Deployment & Termination Updated step 1 & 2 Updated section titles & steps Updated Timeline Deviations Added Note, updated Advisory & Watch | June 1, 2014 |
| 3.1 3.4 3.6 3.7 4.1 5.1 6.1 7.2 7.3 | 1.0 / 12 1.0 / 15 1.0 / 11 1.0 / 10 1.0 / 13 1.0 / 17 1.0 / 6 1.0 / 14 1.0 / 12 | Updated Desktop references Updated Desktop references Updated Desktop references Updated Desktop references Updated Desktop reference Updated steps 1, 4-6 in Replacement of A/S due to infeasibility or failure to provide, & Desktop references Updated Forced Derate Updated Desktop references Updated Desktop references | August 1, 2014 |
| 7.1 | 1.0 / 16 | Updated Scripts | October 1, 2014 |
| 3.4 3.6 4.1 6.2 | 1.0 / 16 1.0 / 12 1.0 / 14 1.0 / 2 | Deleted Note & added Log Changed title & added Rio Grande Valley Re-worded procedure Added step 2 All procedures in this manual have been reviewed | December 15, 2014 |
| 5.1 | 1.0 / 18 | Added new procedure “Increasing A/S for Extreme Cold Weather and changed title for “Increasing A/S for other reasons and updated timeline | December 22, 2014 |
| 2.2 3.3 3.4 3.5 3.6 3.7 5.1 5.2 6.1 | 1.0 / 3 1.0 / 13 1.0 / 8 1.0 / 13 1.0 / 11 1.0 / 0 1.0 / 19 1.0 / 7 1.0 / 7 | Added Dispatch and VDI definitions Combined section 3.3 & 3.4 into one procedure Updated section number Updated section number Updated section number and Corrected VDI vs. Dispatch Instruction New, moved procedure from Shift Supervisor desk Added SASM Failure and reformatted Deleted procedure Corrected VDI vs. Dispatch Instruction | March 1, 2015 |
| 3.2 3.3 3.5 3.6 5.1 7.1 8.1 9.1 | 1.0 / 3 1.0 / 14 1.0 / 14 1.0 / 12 1.0 / 20 1.0 / 17 1.0 / 7 1.0 / 6 | Updated step Evaluate Request Combined step in Watch Updated GTL to GTC Updated step 2 Moved scripts to script procedure Moved scripts to script procedure Combined Note steps & moved scripts to script procedure Moved script to script procedure | May 1, 2015 |
| 5.1 | 1.0 / 21 | Added a “Q” for QSE scripts Updated per NPRR 682 | July 15, 2015 |
| 5.1 | 1.0 / 22 | Updated per NPRR 701 | September 9, 2015 |
| 5.1 | 1.0 / 23 | Updated Reconfiguration Supplemental Ancillary Service Market (RSASM) | October 1, 2015 |
| 3.5 | 1.0 / 15 | Updated to include calls for deployment and recalls of Load Resources. | October 30, 2015 |
| 3.3 3.4 3.7 5.1 7.1 7.2 7.3 8.1 9.1 | 1.0 / 15 1.0 / 9 1.0 / 1 1.0 / 24 1.0 / 18 1.0 / 15 1.0 / 13 1.0 / 8 1.0 / 7 | Updated Advisory step Issue Advisory Typical MIS Posting Updated Watch step Issue Watch & Deploy Off-Line Non-Spin Typical MIS Posting Updated Watch step Recall Non-Spin Typical MIS Posting Updated step 1 Typical MIS Posting Updated Unannounced Resource Testing step Testing Rules and Scripts Typical Script Updated Increasing Ancillary Services for Extreme Cold Weather step 1 & 2 Typical Scripts Updated Increasing Ancillary Services for other reasons step 1 & 2 Typical Scripts Updated Daily RSASM step 1 & 2 Typical MIS Postings Updated Operating Condition Script step Hotline Q#46 Updated Operating Condition Script step Hotline Cancellation Q#47 First Note, Updated Implement EEA Level 2 step 1, and Implement NPRR708 for EEA Updated Move from EEA Level 2 to EEA Level 1 step 1 Updated step 2 Q#75 Updated Courtesy Hotline Calls for ERCOT Application Issues step 1 Q#76 All procedures in this manual have been reviewed | December 31, 2015 |
| 2.1 3.6 5.1 7.2 8.1 | 1.0 / 3 1.0 / 13 1.0 / 25 1.0 / 6 1.0 / 9 | Updated System Operator Responsibilities and Authority Updated NERC Standard Reference Updated step WS-ERS Updated Replacement of Ancillary Service Due to Infeasibility or Failure to Provide step 1 with Hotline call Changed Business Hours to Time Periods Updated Alert Levels | February 1, 2016 February 10, 2016 |
| 1.3 5.1 | 1.0 / 2 1.0/ 26 | Removed Interchange Coordinator Updated Failure to Provide script title Q#72 | March 1, 2016 |
| 5.1 | 1.0 / 27 | Added Increasing Ancillary Services for Extreme Cold Weather step 1 MIS Posting Typical Script Added Increasing Ancillary Services for other reasons step 1 MIS Posting Typical Script | April 29, 2016 |
| 2.1 2.2 3.7 6.1 7.1 | 1.0 / 4 1.0 / 4 1.0 / 2 1.0 / 8 1.0 / 19 | Updated for COM-002-4 Updated for COM-002-4 Updated for COM-002-4 Updated for COM-002-4 Updated for COM-002-4 | June 30, 2016 |
| 9.1 | 1.0 / 8 | Added Real-Time Data Issues known by the QSE Deleted Telemetry Issues that could affect SCED and/or LMPs All procedures in this manual have been reviewed | December 30, 2016 |
| 1.3 2.1 7.1 7.2 | 1.0 / 3 1.0 / 5 1.0 / 20 1.0 / 17 | Deleted Roles/Responsbilities section Updated section Updated title and all 1st steps Added Implement EEA Level 3 step PRC < 1375 MW | March 31, 2017 |
| 5.1 7.2 | 1.0 / 28 1.0 / 18 | Updated Increasing Ancillary Services for Extreme Cold Weather step 1 Updated Implement EEA Level 3 step PRC <1375 | June 1, 2017 |
| 7.2 | 1.0 / 19 | Updated 1st Note and Implement EEA Level 3 steps | June 30, 2017 |