- Power Operations Bulletin # 800

ERCOT has posted/revised the Real Time manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

- http://www.ercot.com/mktrules/guides/procedures/index.html

## 2.4	Load Forecast Errors affecting the Resource Limit Calculator

Procedure Purpose: Make changes between Short Term Load Forecast (STLF) and Mid Term Load Forecast (MTLF) for proper calculation and deployment of Generation To Be Dispatched (GTBD). The selection of a correct load forecast is needed to contribute to Reliable System Performance.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 5 | Effective Date: July 28, 2016 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | The Load Forecast factor from STLF internal, STLF external and MTLF is calculated every 3rd and 8th minute. This procedure outlines steps to select the STLF external or MTLF from default STLF internal in Resource Limit Calculator (RLC) for GTBD calculation in the event there may be an error. |
| Review | Periodically review the Short Term Load Forecast (STLF) to verify its accuracy. |
| STLF Issues | IF: - The Operator determines the STLF internal forecast error is too high or there has been a telemetry spike causing STLF internal to spike up/down, THEN: - Evaluate STLF external option for forecast errors. IF: - If forecast errors are reasonable, THEN: - Check the box “External: InUse” on the Short-Term Forecast display, IF: - STLF external forecast error is too high or there has been a telemetry spike causing STLF external to spike up/down, THEN: - Check the box “Using MTLF in GTBD Calculation” in the parameter text box in RLC display. REVIEW REFERENCE DISPLAY: - EMP Applications>Resource Limit Calculator>Parm |
| Notify | Call the Load Forecast Analyst supporting the LF application and notify them of the STLF issue and REQUEST immediate support to resolve the issue. |
| Send E-mail | Notify by e-mail the following distribution lists of the issue: - 1 ERCOT EMMS Production - Load Forecasting & Analysis - Operations Analysis - 1 ERCOT Shift Supervisors |
| STLF Resolved | WHEN: - STLF is normal and telemetry spike issues have been resolved, THEN: - Ensure the correct STLF internal or STLF external “InUse” flag is checked. - Uncheck the box “Using MTLF in GTBD Calculation” in the parameter text box in RLC display. This will make STLF internal or STLF external the default forecast for calculating GTBD again, depending on which STLF “InUse” flag is set, VERIFY: - The duration of bad-telemetry or spike has been over-written with good data otherwise this will affect the STLF internal in the future. REVIEW REFERENCE DISPLAY: - EMP Applications>Load Forecast>Related Display>Short-Term Forecast (STLF)>Short-Term LF Forecast - Chart |
| Send E-mail | Notify by e-mail the above identified e-mail addresses when unchecking the box “Using MTLF in GTBD Calculation” in the parameter text box in RLC display. |
| Log | Log all actions. |

## 3.1	Frequency Control Operating Procedure

Procedure Purpose: To control frequency within defined limits.

| Protocol Reference | 6.5.7.6.1 | 6.5.7.6.2.2(7) | 6.5.9.1(1)(b) |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 2.2.4 | 2.2.8 |  |  |
| NERC Standard | BAL-001-2 R1, R2 | IRO-001-4 R1 | NUC-001-3 R4.1, R4.2, R9.2.1, R9.4.2 | TOP-001-3 R2, R11 |

| Version: 1 | Revision: 25 | Effective Date: July 28, 2017 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Maintain System Frequency |  |
| Objective | - Frequency should be maintained within +/- 0.03 Hz of schedule - Attempt to maintain CPS1 scores over 100 - Operate within the BAAL - Frequency Bias set to 764MW/0.1Hz |
| CPS1 less than 100 | IF: - Performance drops below 100 for over three consecutive hours; THEN: - LOG the event and the possible cause of the poor performance. |
| BAAL | Corrective action shall be taken whenever the clock-minute average ACE is outside its clock-minute average Balancing Authority ACE Limit (BAAL). This is to ensure that the Balancing Authority ACE does not remain outside the BAAL for more than 30 consecutive clock-minutes. |
| Caution | NEVER (unless directed by EMMS Production or Support Engineer): - Change other tuning parameters (including QSE ramp rates, dead bands, thresholds, gains, time constraints) |
| Base Point Deviation | REVIEW REFERENCE DISPLAY: EMP Applications>Generation Area Status>Related Displays>Expected Generation and Load Details Not-Tracking Units tab IF: - A QSE has a Resource with a large Base Point deviation (not tracking unit flag), AND - Their generation is not moving in the proper direction to correct their Base Point Deviation; THEN: - Notify the QSE of the issue. |
| Frequency Deviations | IF: - Frequency deviations are equal to or greater than +/- 0.10 Hz, OR - Sudden loss of generation greater than 450 MW; THEN: - Ensure frequency recovers to pre-disturbance within 15 minutes - Manually run SCED or use offset as needed. LOG: - Log the following information: - Possible reasons, if known (Base Point deviation, large schedule change, unit trip, DC-Tie trip, etc.) - If unit trip: - Time of unit trip or DC-Tie, - Name of unit or DC-Tie, - Approximate net MW, - Approximate lowest TrueTime frequency (use 3 decimals), - Amount of RRS deployed (if any), AND - Approximate ERCOT load. |
| Hydro Generation Operating in Synchronous Condenser Fast Response Mode | IF: - Hydro Resources operating in synchronous condenser fast-response mode who provide MW to the System in response to a frequency event without a Responsive Reserve deployment; THEN: - QSE will request an electronic Dispatch Instruction confirmation - Choose Resource tab - Choose requesting QSE for Participant Name - Choose Resource name - Enter MW amount deployed in Current Operating Level - Choose Other For Resource for Instruction Type - State Hydro deployed in response to frequency in Other Information - Initiation Time, and - Completion Time When issuing a VDI or the confirmation, ensure the use of three-part communication: - Issue the Operating Instruction - Receive a correct repeat back - Give an acknowledgement - An electronic Dispatch Instruction confirmation will be needed for each Resource. IF: - QSE contacts ERCOT to determine if it is allowed to recall and reset; THEN: - ERCOT grants approval to come off-line once the frequency recovers to pre-disturbance level or 60 Hz, whichever is lower, OR - Request QSE to remain On-line - May not exceed 30 minutes per deployment for each frequency deviation or event - Shall not exceed two hours per a 12-hour period in aggregate unless an EEA is declared |
| ### Response to High Frequency |  |
| BAAL Sheet | Located on the realtime drive in the _Operations Official Spreadsheets folder. Open BAAL ERCOT Interconnection and select Control T simultaneously. |
| Monitor | IF: - Frequency goes above 60.05 Hz and exceeds 60.05 Hz > 5 minutes AND - Regulation Down service remains and is deploying; THEN: - Manually run SCED - Call QSEs with Resources that have positive Base Point deviations and issue an Operating Instruction to bring their Base Point deviations to zero. IF: - Frequency goes above 60.05 Hz, AND - Out of Down Regulation; THEN: - CHECK the GEN-LDL or Cap to decrease BP on the EMS to ensure there is adequate down room, - Enter manual offset (the offset will continue until removed). IF: - There is no generation left for SCED to lower; THEN: - Coordinate with the Shift Supervisor and Transmission Operator to select a Resource to decommit, - Request RUC Operator to issue an Operating Instruction to decommit Resource. |
| 10 MINUTES | REFERENCE DISPLAY:EMP Applications>Generation Unit Status>Related Displays>Expected Generation and Load Details>Top Ten button ANDMarket Operation>Real-Time Market>SCED Displays>DSI Displays>DSI Data Processes>DSI Generation Requirement Manual AdjustmentIF: - 10 consecutive minutes of ACE above BAALHigh (60.09 Hz); THEN: - Call QSEs with Resources that have positive Base Point deviations and issue an Operating Instruction to bring their Base Point deviations to zero, - Verify SCEDs capacity to decrease Base Points GEN-LDL, - Enter manual offset, - Manually run SCED (do not run SCED more than once between SCED runs). |
| Notify | If it is recognized that Frequency is or expected to be outside +/- 0.1 Hz for a non-transient event and will not recover within 15 minutes, notify the Nuclear Power Plants QSEs. |
| 15 Minutes | IF: - 15 consecutive minutes of ACE above BAALHigh (60.09 Hz); THEN: - Call QSEs with Resources that have positive Base Point deviations and issue an Operating Instruction to bring their Base Point deviations to zero, - Verify SCEDs capacity to decrease Base Points GEN-LDL, - Re-adjust manual offset, - Manually run SCED, - Log the event and notify Operations Support Engineer to send an event notification to OperationsAnalysis@ercot.com. IF: - There is no generation left for SCED to lower; THEN: - Coordinate with the Shift Supervisor and Transmission Operator to select a Resource to decommit, - Request RUC Operator to issue Operating Instruction to decommit Resource. |
| 20 Minutes | IF: - 20 consecutive minutes of ACE above BAALHigh (60.09 Hz) and Frequency is above 60.10 Hz; THEN: - Call QSEs with Resources that have positive Base Point deviations and issue an Operating Instruction to bring their Base Point deviations to zero - Curtail appropriate amount of DC-Tie imports (issue an Emergency), - Coordinate with Shift Supervisor, Transmission Operator to select an additional Resource to decommit, - Request RUC Operator to issue Operaring Instruction to decommit Resource. |
| 25 Minutes | IF: - 25 consecutive minutes of ACE above BAALHigh (60.09 Hz) and Frequency is above 60.10 Hz; THEN: - Call QSEs with Resources with positive Base Point deviations and issue an Operating Instruction to take their Resource off-line. - Coordinate with Shift Supervisor, Transmission Operator to select an additional Resource to decommit, - Request RUC Operator to issue Operating Instruction to decommit Resource. |
| Stable | IF: - A manual offset was used; THEN: - Ensure that it has been removed. |
| Log | Log all actions. |
| ### Response to Low Frequency |  |
| BAAL Sheet | Located on the realtime drive in the _Operations Official Spreadsheets folder. Open BAAL ERCOT Interconnection and select Control T simultaneously. |
| NOTE | UFRs will deploy as follows: - Hydro RRS - 59.80 Hz - Load Resource providing RRS – 59.70 Hz |
| Monitor/ Deploy | IF: - Frequency drops below 59.95 Hz, AND - Regulation Up service remains and is deploying; THEN: - Manually run SCED (do not run SCED more than once between SCED runs) - Call QSEs with Resources with negative Base Point deviations and issue an Operating Instruction to bring their Base Point deviations to zero. IF: - Frequency drops below 59.95 Hz, AND - Out of Up Regulation; THEN: - Check the GTBD2[HDL] on the Splunk SCED GEN ONLINE Dashboard or Cap to increase BP or HDL-Gen on the EMS and enter appropriate manual offset - If using Splunk Dashboard, do not enter an offset > than GTBD2[HDL] - If using EMS, do not enter an offset > than Cap to increase BP or HDL-Gen IF: - Frequency is below 59.95 Hz and out of Up Regulation, AND - There is not adequate up room; THEN: - Manually deploy Responsive Reserve using the ERCOT Nodal Summary display on the EMS - Check the box labeled “Activate Manual Responsive Reserve” to activate, - Enter the “Desired RRS MW”, - Select Enter, - Select Commit. - QSE’s have one minute to update schedule to free up the capacity, SCED will automatically run after one minute. - Remember to remove the manual RRS amount when frequency has recovered. |
| 10 Minutes | REFERENCE DISPLAY: EMP Applications>Generation Unit Status>Related Displays>Expected Generation and Load Details>Top Ten button AND Market Operation>Real-Time Market>SCED Displays>DSI Displays>DSI Data Processes>DSI Generation Requirement Manual Adjustment IF: - 10 consecutive minutes of ACE is less than BAALLow (59.91 Hz); THEN: - Call QSEs with Resources with negative Base Point deviations and issue an Operating Instruction to bring their Base Point deviations to zero, - Confirm Responsive Reserve has been deployed, - Verify SCEDs capacity to increase Base Points, - Enter manual offset - If room is available - Manually run SCED IF: - There is no generation left for SCED to increase; THEN: - Confirm with the Resource Operator that Non-Spin has been deployed, - Manually deploy Generation Responsive Reserve using the ERCOT Nodal Summary display on the EMS - Check the box labeled “Activate Manual Responsive Reserve” to activate, - Enter the “Desired RRS MW”, - Select Enter, - Select Commit. - QSE’s have one minute to update schedule to free up the capacity, SCED will automatically run after one minute. - Remember to remove the manual RRS amount when frequency has recovered. - Notify the Shift Supervisor of the need to possibly commit additional Resources. |
| Note | ERCOT may declare an EEA Level 2 when the clock-minute average system frequency falls below 59.91 Hz for 15 consecutive minutes. |
| Notify | If it is recognized that the Frequency is or expected to be outside +/- 0.1 Hz for a non-transient event and will not recover within 15 minutes, notify the Nuclear Power Plants QSEs. |
| 15 Minutes | IF: - 15 consecutive minutes of ACE less than BAALLow (59.91 Hz ); THEN: - Curtail appropriate amount of DC-Tie export (issue an Emergency), - Instruct the Resoure Operator to manually deploy one block of Load Resources providing Responsive Reserve, - Call QSEs with Resources that have negative Base Point deviations and issue an Operating Instructon to bring their Base Point deviations to zero, - Verify SCEDs capacity to increase Base Points (HDL-GEN), - Re-adjust manual offset, - If room is available - Manually run SCED, - Log the event and notify Operations Support Engineer to send notification of the event to OperationsAnalysis@ercot.com. |
| 20 Minutes | IF: - 20 consecutive minutes of ACE less than BAALLow (59.91 Hz); THEN: - Implement EEA Level 2 - EEA2 PRC <1750 - Call QSEs with Resources that have negative Base Point deviations and issue an Operating Instruction to bring their Base Point deviations to zero, - Verify SCEDs capacity to increase Base Points (HDL-GEN), - If room is available, re-adjust manual offset, - Manually run SCED, - Monitor RRS Load Resource deployments. - Make Hotline call to QSE’s |
| ERS Resources | Q#7 - Typical Hotline Script for EEA2 deploying ERS-10 / ERS-30 / both ERS-10 and ERS 30 / ERS-30 including Weather Sensitive ERS / ERS-10 and ERS-30 including Weather Sensitive |
| Load Resources | Q#8 - Typical Hotline Script for EEA2 deploying Load Resources Group 1 / Load Resources Group 1 and 2 |
| 25 Minutes | IF: - 25 consecutive minutes of ACE less than BAALLow (59.91 Hz ); THEN: - Implement EEA Level 3 - EEA3 Unable to Maintain 59.91 Hz or PRC <1000 MW - Verify SCEDs capacity to increase Base Points, - Re-adjusted manual offset, - Do Not enter an offset > than (HDL-GEN) - Manually run SCED as needed, - Monitor RRS Load Resource deployments, - Monitor DC-tie curtailments, - Instruct the Transmission and Security Operator to shed an appropriate amount of firm load. - Make Hotline call to QSE’s ## Q#11 EEA3 With Firm Load Shed: |
| Stable | IF: - Firm load was shed; THEN: - Instruct the Transmission and Security Operator to restore firm load. - Make Hotline call to QSE’s ## Q#13 Restoring Firm Load: IF: - RRS was manually deployed; THEN: - Uncheck the Activate Manual Responsive Reserve, IF: - An manual offset was used; THEN: - Ensure that it has been removed. |
| Log | Log all actions. |
| ### Monitor Frequency for the Loss of EMS or Site Failover |  |
|  | The ability to view an adequate Frequency source may be limited during a site-failover, database load, or if AGC is temporarily unavailable. To view the System Frequency during these conditions you may monitor the following sources. - ERCOT Control Room digital wall frequency displays - PI ProcessBook → ERCOT → TrueTime Frequency (Taylor) and/or - PI ProcessBook → ERCOT → TrueTime Frequency (Bastrop) It may be necessary to reload the PI ProcessBook “ERCOT Main Summary” display to show the historical data. |
| ### Actions When Frequency Telemetry is Incorrect |  |
|  | REVIEW REFERENCE DISPLAY: EMP Applications>Generation Control>Generation Area Status>Current Frequency Deviation from Nominal IF: - Frequency is believed to be incorrect; THEN: - Check the current Frequency and switch to a different source, - Select Skip on the incorrect Frequency device, - Contact the Help Desk. |

## 5.3	Implement EEA Levels

Procedure Purpose:  To provide for maximum possible continuity of service while maintaining the integrity of the ERCOT System to reduce the chance of Cascading Outages.

| Protocol Reference | 6.5.7.6.2.2(1)(b) & (12) | 6.5.9.3.4(6) | 6.5.9.4 | 6.5.9.4.2 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.4.3 |  |  |  |
| Guide Reference | 4.5.3 | 4.5.3.1 | 4.5.3.2 | 4.5.3.3 |
|  | 4.5.3.4 |  |  |  |
| NERC Standard | EOP-011-1 R1.1, R1.2.4, R2.1, R2.2.2, R2.2.3, R2.2.3.1, R2.2.3.4, R2.2.4, R2.2.7 | IRO-001-4 R1 | PER-004-2 R2 | TOP-001-3 R2 |

| ### Version: 1 | Revision: 24 | Effective Date: July 28, 2017 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - IF steady state system frequency falls < 59.91 Hz, ERCOT CAN immediately implement EEA 3. - IF steady state system frequency falls < 59.5 Hz, ERCOT SHALL immediately implement EEA 3. |
| NOTE | Confidentiality requirements regarding Transmission Operations and System Capacity information will be lifted, as needed to restore reliability. |
| ERS-30 | ERS with a thirty-minute ramp period. |
| ERS-10 | ERS with a ten-minute ramp period. |
| TCEQ | When increased generation is requested during EEA events, Texas Commission on Environmental Quality (TCEQ) will exercise enforcement discretion for exceedances of emission limits as well as operational limits for power generating plants for Generators who exceed air permit limits in order to maximize generation for the duration of the EEA event. ERCOT General Council will send out a Market Notice each time ERCOT enters into an EEA with this reminder. |
| Media Appeal | When an ERCOT-wide appeal through the public news media for voluntary energy conservation is made. Notify the QSEs by hotline. |
| ### Implement EEA Level 1 |  |
| EEA 1 PRC<2300 | IF: - PRC < 2300 MW and is not projected to be recovered above 2300 MW within 30 minutes without the use of EEA Level 1; THEN: - Select the activate EEA flag in EMS, - Maintain steady state system frequency near 60 Hz and maintain PRC above 1750 MW, - Determine whether system conditions warrant the deployment of ERS-30. Refer to the ERS tab on the Real-Time Values Spreadsheet for amounts in each time period and number of times deployed: - Consider the peak hour, deploy all ERS-30 if needed to prevent PRC from falling < 1750 MW, - When deploying the ERS-30, also deploy the weather-sensitive ERS if available for the current time period. - Using the Hotline, notify all QSEs to implement EEA 1. Q#5 - Typical Hotline Script for EEA1 NOT deploying ERS OR IF: - Deploying ERS, the Resource Operator must complete the XML deployment of the ERS before the Hotline call is made. - Deploy all ERS Resources as a single group - If it is June – September and during time period TP3 or TP4 on a business day, use this script. Q#6 - Typical Hotline Script for EEA1 deploying ERS-30 / ERS-30 including Weather Sensitive |
| RRS Release to HASL | REVIEW REFERENCE DISPLAY: EMP Applications>Generation Area Status>Nodal Operations Status>Responsive Reserve Service Summary Data IF: - PRC < 2000 MW; THEN: - Activate Manual Responsive Reserve - Manually deploy all remaining RRS |
| Log | Log all actions. |
| ### Implement EEA Level 2 |  |
| Note | ERCOT may declare an EEA Level 2 when the clock-minute average system frequency falls below 59.91 Hz for 15 consecutive minutes. |
| EEA 2 PRC<1750 | IF: - PRC < 1750 MW or unable to maintain system frequency at a minimum of 59.91 Hz and is not projected to be recovered above 1750 MW within 30 minutes without the use of EEA Level 2; THEN: - Verify with Shift Supervisor a public appeal has been issued - Maintain steady state system frequency at a minimum of 59.91 Hz and maintain PRC above 1,375 MW, - Determine when system conditions require the deployment of Load Resources and/or ERS Resources (Do Not forget the WS ERS if available): - Deploy ERS-30 if not already done in EEA 1 - Deploy ERS-10 - Deploy Load Resources Group 1 and/or 2 - Using the Hotline, notify all QSEs to implement EEA 2 and any measures associated with EEA 1, if not already implemented. |
| ERS Resources | IF: - Deploying ERS, the Resource Operator must complete the XML deployment of the ERS before the Hotline call is made. - Deploy all ERS Resources as a single group. - If it is June – September and during time period TP3 or TP4 on a business day Q#7 - Typical Hotline Script for EEA2 deploying ERS-10 / ERS-30 / both ERS-10 and ERS 30 / ERS-30 including Weather Sensitive ERS / ERS-10 and ERS-30 including Weather Sensitive |
| Load Resources | IF: - Deploying Load Resources, the Resource Operator must complete the XML deployment of the Load Resources before the Hotline call is made. - PRC < 1750 MW, deploy Group 1 - PRC < 1375 MW, deploy both Groups 1 and 2 simultaneously Q#8 - Typical Hotline Script for EEA2 deploying Load Resources Group 1 / Load Resources Group 1 and 2 |
| When ERS Time Periods Change | IF: - ERS Resources are deployed and the Time Period is changing - If it is June – September and during time period TP3 or TP4 on a business day; THEN: - After Resource Operator has completed the XML deployment, make the QSE hotline call Q#9 - Typical Hotline Script for EEA2 deploying ERS-10 / ERS-30 / both ERS-10 and ERS-30 / ERS-10, ERS-30 including Weather Sensitive Script |
| NOTE | - All Load Resources, 10 MIN ERS, and 30 MIN ERS must be deployed before firm load |
| Media Appeal | - Unless already in effect, verify with the Shift Supervisor that the communications group has issued an appeal through the public news media for voluntary energy conservation, - Notify QSEs, via Hotline, that a media appeal for conservation is in effect. Q#10 - Typical Hotline Script for Media Appeal |
| Log | Log all actions. |
| ### Implement EEA Level 3 |  |
| Note | ERCOT may declare an EEA Level 3 when the clock-minute average system frequency falls below 59.91 Hz for 20 consecutive minutes. |
| EEA3 PRC <1375 MW | ERCOT will declare an EEA Level 3 when PRC cannot be maintained above 1,375 MW. Using the Hotline, notify all QSEs to implement EEA 3 Without Firm Load Shed and any measures associated with EEA 1 and 2, if not already implemented. Q#103 - Typical Hotline Script for EEA3 PRC <1375 Without Firm Load Shed |
| LOG | Log all actions. |

| EEA3 Unable to Maintain 59.91 Hz or PRC <1000 MW | IF: - PRC < 1000 MW and is not projected to be recovered above 1,000 MW within 30 minutes or unable to maintain system frequency at 59.91 Hz for 25 consecutive minutes; THEN: - Using the Hotline, notify all QSEs to implement EEA 3 Firm Load Shed and any measures associated with EEA 1 and 2, if not already implemented. Q#11 - Typical Hotline Script for EEA3 With Firm Load Shed |
| --- | --- |
| When ERS Time Periods Change | IF: - ERS Resources are deployed and the Time Period is changing - If it is June – September and during time period TP3 or TP4 on a business day; THEN: - After Resource Operator has completed the XML deployment, make the QSE hotline call Q#12 - Typical Hotline Script for EEA3 deploying ERS-10 / ERS-30 / both ERS-10 and ERS-30 / ERS-10, ERS-30 including Weather Sensitive |
| Log | Log all actions. |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Frosch, Hartmann, Stone, and Barcalow | Prepares | November 10 , 2010 |
| Frosch and Hartmann | Procedure writers and editors | November 29, 2010 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2010 |
| Frosch, Foster and Hartmann | Procedure writers and editors | January 3, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 26, 2011 |
| Frosch and Hartmann | Procedure writers and editors | March 23, 2011 |
| Frosch and Hartmann | Procedure writers and editors | April 20, 2011 |
| Frosch and Hartmann | Procedure writers and editors | June 6, 2011 |
| Frosch and Hartmann | Procedure writers and editors | July 18, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 1, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 30, 2011 |
| Frosch and Hartmann | Procedure writers and editors | September 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | October 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 16, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | April 25, 2012 |
| Frosch and Hartmann | Procedure writers and editors | May 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | May 30, 2012 |
| Barcalow, Frosch and Hartmann | Procedure writers and editors | July 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | August 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | October 26, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 26, 2013 |
| Frosch and Hartmann | Procedure writers and editors | May 28, 2013 |
| Frosch and Hartmann | Procedure writers and editors | July 8, 2013 |
| Frosch and Hartmann | Procedure writers and editors | August 7, 2013 |
| Frosch and Hartmann | Procedure writers and editors | September 25, 2013 |
| Frosch and Hartmann | Procedure writers and editors | December 11, 2013 |
| Frosch and Hartmann | Procedure writers and editors | December 20, 2013 |
| Frosch, Gaddy, Hartmann and Solis | Procedure writers and editors | April 1, 2014 |
| Frosch, Gaddy and Hartmann | Procedure writers and editors | May 27, 2014 |
| Frosch and Hartmann | Procedure writers and editors | July 29, 2014 |
| Frosch and Hartmann | Procedure writers and editors | September 29, 2014 |
| Drummond, Frosch and Hartmann | Procedure writers and editors | December 10, 2014 |
| Frosch and Thompson | Procedure writers and editors | December 19, 2014 |
| Frosch and Hartmann | Procedure writers and editors | February 25, 2015 |
| Frosch and Hartmann | Procedure writers and editors | March 25, 2015 |
| Frosch and Hartmann | Procedure writers and editors | April 29, 2015 |
| Frosch, Hartmann and Gaddy | Procedure writers and editors | July 13, 2015 |
| Hartmann and Gaddy | Procedure writers and editors | December 22, 2015 |
| Hartmann, Gaddy and Frosch | Procedure writers and editors | February 23, 2016 |
| Hartmann and Gaddy | Procedure writers and editors | April 22, 2016 |
| Hartmann, Gaddy and Frosch | Procedure writers and editors | June 24, 2016 |
| Hartmann and Gaddy | Procedure writers and editors | July 15, 2016 |
| Hartmann, Gaddy and Frosch | Procedure writers and editors | September 26, 2016 |
| Hartmann and Gaddy | Procedure writers and editors | October 31, 2016 |
| Hartmann, Gaddy and Frosch | Procedure writers and editors | December 23, 2016 |
| Hartmann, Gaddy and Frosch | Procedure writers and editors | March 24, 2017 |
| Hartmann and Gaddy | Procedure writers and editors | April 5, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | May 26, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | June 23, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | July 24, 2017 |

Manual Change History

| Procedure | Ver/Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All Sections | 1.0 / 0 | New procedures for all sections for Nodal implementation | November 28, 2010 |
| 2.4 3.1 3.2 3.4 3.5 3.6 4.2 5.3 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Updated Categories and Priorities Updated Response to High Frequency steps 15, 20 and 25 minutes and Response to Low Frequency step 15 Updated steps Failure Indication/Issues and QSE Capacity Issues Updated steps AGC/RLC Issues, System Wide Capacity Issue and AGC/RLC Issues Resolved Updated step 1 Updated step Capacity Surplus Updated step 2, 3, 4 and 5 Updated all steps of “Implement Level 2B” | December 1, 2010 |
| 4.1 4.2 5.2 | 1.0 / 1 1.0 / 2 1.0 / 1 | Updated step “MP unable to Override” Updated step 1 & 2 Updated step 1 in sections WATCH and Advisory | December 15, 2010 |
| 3.1 3.2 3.3 3.4 4.1 5.1 5.4 | 1.0 / 2 1.0 / 2 1.0 / 1 1.0 / 2 1.0 / 2 1.0 / 1 1.0 / 1 | Updated step “BAAL” Updated step “AGC Issues Resolved” Updated step “Hotline” Updated step “Failure Indications, AGC/RLC Issues, System Wide Capacity Issue, AGC/RLC Issues Resolved” Updated step 2 in “Workflow Controller Messages”, added new procedure “Exceeding West – North Stability Limit”, updated Note in “Generation Resource Shut-down/Start-up Process” Updated step 1 in “Watch” and step Hotline in “Scripts” Updated step 1 in “Move from EEA level 3 to EEA lever 2B” | January 5, 2011 |
| 2.4 2.5 2.6 2.7 3.1 3.2 3.3 3.4 3.5 4.1 4.2 5.1 5.2 5.3 5.4 5.5 6.1 6.2 6.3 | 1.0 / 0 1.0 / 2 1.0 / 0 1.0 / 0 1.0 / 3 1.0 / 3 1.0 / 2 1.0 / 2 1.0 / 1 1.0 / 3 1.0 / 3 1.0 / 2 1.0 / 2 1.0 / 2 1.0 / 2 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Added new procedure Changed procedure number Added new procedure Added new procedure Updated sections “Maintain System Frequency”, “Response to High Frequency”, “Response to Low Frequency” and “Actions when Frequency Telemetry in Incorrect. Combined sections 3.3, 3.4 & 4.2 into 3.2 Changed 3.5 “Potential DCS Event” to 3.3 & updated whole procedure Changed 3.6 “Monitor Capacity Reserves & Respond to Capacity Issues to 3.4 Changed 3.7 “Monitor and Control Time Error Correction to 3.5 & updated script Deleted Exceeding West-North Stability Limit Deleted Procedure Updated script Updated step 1 in “Advisory” and “Watch” Updated all steps Updated all steps Updated all steps Updated all steps Updated all steps Updated OCN | January 31, 2011 |
| 2.6 3.2 3.3 3.4 3.6 5.1 5.2 | 1.0 / 1 1.0 / 4 1.0 / 3 - / 3 1.0 / 0 1.0 / 3 1.0 / 3 | Updated step Site Failovers Updated step 3 in SCED Failure, step 4 in RLC Failure, Note in LFC (AGC) Failure and step 2 in EMS (LFC and RLC/SCED Failure Updated step 3 Updated step Capacity Shortage Added new procedure Updated Watch and Emergency Notice All step 1’s | March 25, 2011 |
| 2.6 3.1 3.2 3.3 3.6 5.1 5.4 5.5 | 1.0 / 2 1.0 / 4 1.0 / 5 1.0 / 4 1.0 / 1 - / 4 1.0 / 3 1.0 / 2 | Added steps and updated whole procedure Added new step to Maintain System Frequency and updated Response to High Frequency & Response to Low Frequency Updated steps 2, 3, 5 in SCED Failure; steps 2, 3, 4, 6 in RLC Failure; steps 1, 3 in LFC (AGC) Failure; steps 2, 5 in EMS (LFC and RLC/SCED) Failure Updated NERC Recovery Criteria, step 1 & 4 Updated 1st script Updated step 1 in Watch and Emergency Notice and step Post Updated 1st and 2nd script in Restore Firm Load, Updated 1st in Move From EEA Level 3 to EEA Level 2B Updated step 3 | April 22, 2011 |
| 3.3 5.1 5.3 5.4 6.1 6.2 6.3 6.4 | 1.0 / 5 1.0 / 5 1.0 / 3 1.0 / 4 1.0 / 2 1.0 / 0 1.0 / 2 1.0 / 2 | Updated step NERC Recovery Criteria Updated all step 1’s Updated step 1 in Implement EEA Level 1, step 1 in Implement EEA Level 2A, added note and updated step 2 in Implement EEA Level 2B, step 1 in Implement EEA Level 3 Updated all step 1’s Updated all steps Added new procedure Updated section number and all steps Updated section number and all steps | June 8, 2011 |
| 2.6 3.1 5.1 5.2 5.3 5.4 8.1 | 1.0 / 3 1.0 / 5 1.0 / 6 1.0 / 4 1.0 / 4 1.0 / 5 1.0 / 1 | Added step If EBPs are needed”, updated step IF EBPs are needed and W-N was Active before site failover started Added step Hydro, updated step Frequency Deviations Updated step Watch Updated all steps Updated 1st note, step 1 in EEA level 1 & 2A Updated step 1 in Move for EEA level 1 to 0 Added Market Participant Backup Control Center Transfer procedure | July 20, 2011 |
| 3.1 3.2 3.4 4.1 6.4 6.5 | 1.0 / 6 1.0 / 6 1.0 / 4 1.0 / 4 1.0 / 0 1.0 / 3 | Updated step Monitor, 15 minutes, 20 minutes and 25 minutes in Response to High Frequency Updated step 2 in LFC Failure, step 4 & 5in EMS Failure Updated step Capacity Surplus Updated step 2 in Workflow Controller Messages Added new procedure “Extreme Hot Weather” Changed section number | August 3, 2011 |
| 2.7 3.1 5.1 5.2 5.3 5.4 6.4 7.1 | 1.0 / 1 1.0/ 7 1.0 / 7 1.0 / 5 1.0 / 5 1.0 / 6 1.0 / 1 1.0 / 1 | Updated step Hotline Call Updated NERC Standard reference table Added projected reserve capacity shortage and Extreme Hot Weather in Watch Updated step 1 in Advisory & Watch Updated 2nd Note, step 1 in Implement EEA 1, step Media Appeal & 1 in Implement EEA 2A, 1st Note & step 2 in Implement EEA 2B Added Note to Move From EEA 3 to EEA 2B and Move From EEA 2A to EEA 1 Updated temperature from 102 to 103 Updated 4th note and step 1 | September 1, 2011 |
| 3.2 5.3 5.4 | 1.0 / 7 1.0 / 6 1.0 / 7 | Updated SCED Failure step 2 and 3, RLC Failure step 3 and LFC (AGC) Failure step 3 Combined EEA 2A & B per NPRR 379 Combined EEA 2 A & B per NPRR 379 | October 1, 2011 |
| 3.2 | 1.0 / 8 | Updated script for LFC and EMS Failure | November 1, 2011 |
| 2.4 2.6 4.1 5.1 6.3 | 1.0 / 1 1.0 / 4 1.0 / 5 1.0 / 8 1.0 / 3 | Added step Review, Updated “Site Failover with W-N Active” Added Note to Large Resource Trips or Runbacks Updated Post in “Scripts” Updated “OCN” and “Advisory” All procedures in this manual have been reviewed. | December 15, 2011 |
| 1.2 3.1 4.1 8.1 | 1.0 / 1 1.0 / 7 1.0 / 6 - / 2 | Updated Scope Updated Response to High Frequency & Response to Low Frequency Updated Large Resource Trips or Runbacks, Quick Start Generation Resource Updated Market Participant Backup Control Center Transfer | January 19, 2012 |
| 2.1 3.1 5.1 5.3 7.1 8.1 | 1.0 / 1 1.0 / 8 1.0 / 7 1.0 / 9 1.0 / 7 1.0 / 2 1.0 / 3 | Updated paragraph 4 Updated BAAL Updated Desktop Guide reference & step QSE Override & QSE unable to Override Updated step 1 in Watch Updated Step 1 in Implement EEA Level 1 Updated Desktop Guide references Changed title names, updated steps 1 & 3 & step Power System Stabilizers (PSS) & Automatic Voltage Regulators (AVR) | March 1, 2012 |
| 2.1 3.1 3.2 3.3 3.5 4.1 5.1 6.2 6.3 6.4 8.1 | 1.0 / 2 1.0 / 9 1.0 / 9 1.0 / 6 1.0 / 2 1.0 / 8 1.0 / 10 1.0 / 4 1.0 / 2 1.0 / 4 1.0 / 4 | Changed TSO, DSP to TO Changed Shift Engineer to Operations Support Engineer, removed Automatic SCED Runs & Hydro Generation in Fast Response Mode, updated Note, Monitor/Deploy, 15 minutes, 20 minutes in Response to Low Frequency Updated step 2, 4 & 5, added SCED Data Input Failure, updated RLC Failure, LFC Failure, & EMMS Failure sections Updated Nerc Recovery Criteria step & step 3 Updated Requirements and Notes Changed Shift Engineer to Operations Support Engineer, deleted Large Resource Trips or Runbacks section Updated OCN, Advisory, Watch, Emergency Notice sections Deleted Cold Weather, replaced with Extreme Cold Weather Section changed to Extreme Hot Weather, added OCN and Emergency Notice steps Section number changed Changed Shift Engineer to Operations Support Engineer | May 1, 2012 |
| 3.1 3.4 5.2 | 1.0 / 10 1.0 / 5 1.0 / 6 | Added back step Hydro Generation Operating in Synchronous Condenser Fast Response Mode Updated to reflect changes in the TAC approved Non-Spin document Updated to reflect changes in the TAC approved Non-Spin document | May 14, 2012 |
| 2.6 5.3 5.4 6.3 | 1.0 / 5 1.0 / 8 1.0 / 8 1.0 / 3 | Updated Site Failover step Updated EILS to ERS per NPRR 451 Updated EILS to ERS per NPRR 451 Updated EILS to ERS per NPRR 451 | June 1, 2012 |
| 1.3 2.6 5.1 5.3 5.4 6.2 6.3 7.1 | 1.0 / 1 1.0 / 6 1.0 / 11 1.0 / 9 1.0 / 9 1.0 / 5 1.0 / 4 1.0 / 3 | Removed ERCOT Shift Supervisor paragraph Updated all steps Updated all step 1’s Updated 2nd note, added TCEQ, & XML for ERS Clarified LR and ERS recalls Updated script for Emergency Notice Updated script for Emergency Notice Updated 4th note | July 16, 2012 |
| 2.6 3.1 4.1 5.3 | 1.0 / 7 1.0 / 11 1.0 / 9 1.0 / 10 | Added note to step Database Load Updated Frequency Deviations and Monitor Frequency for the Loss of EMS or Site Failover Incorporated NPRR348 Added 30 MIN ERS and updated steps 1, 2 & 3 on Implement EEA Level 1 | August 29, 2012 |
| 2.2 2.5 3.5 4.1 5.3 | 1.0 / 1 1.0 / 3 1.0 / 3 1.0 / 10 1.0 / 11 | Added Hotline Call Communication Updated step 3 Updated per NOGRR100 Added Note to Shut-down/Start-up Process and new Combine Cycle Generation Resources section Updated ERS scripts All procedures in this manual have been reviewed. | November 1, 2012 |
| 2.5 3.1 3.2 3.3 3.4 3.5 3.6 3.7 5.4 | 1.0 / 4 1.0 / 12 1.0 / 0 1.0 / 10 1.0 / 7 1.0 / 6 1.0 / 4 1.0 / 2 1.0 / 10 | Updated step 3 Updated BAAL New procedure, Monitor Large Ramp Events Updated section # & SCED failure step 2 Updated section # Updated section # Updated section # Updated section # Updated Cancel Watch All procedures in this manual have been reviewed. | March 1, 2013 |
| 2.6 2.7 3.1 3.2 3.3 3.4 3.7 4.1 5.1 5.2 5.3 5.4 5.5 6.1 6.2 6.3 6.4 | 1.0 / 8 1.0 / 2 1.0 / 13 1.0 / 1 1.0 / 11 1.0 / 8 1.0 / 3 1.0 / 11 1.0 / 12 1.0 / 8 1.0 / 12 1.0 / 11 1.0 / 3 1.0 / 3 1.0 / 6 1.0 / 5 1.0 /5 | Updated scripts Updated scripts Updated Monitor Frequency for the Loss of EMS or Site Failover & Actions when Frequency Telemetry is Incorrect Updated scripts Updated scripts Updated script Updated scripts Added QSGR Decommitment step to QSGR Added Generic and Specific scripts Updated Note and scripts Updated TCEQ section and scripts Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts Correct spelling and updated script | June 1, 2013 |
| 2.6 3.1 3.2 3.8 5.1 5.3 5.4 | 1.0 / 9 1.0 / 14 1.0 / 2 1.0 / 0 1.0 / 13 1.0 / 13 1.0 / 12 | Changed title name & updated step EMS Changes & added MMS Changes Updated steps Base Point Deviation & 10 Minutes Updated 1st note Moved procedures from Resource desk Updated step 1 in Watch & Emergency Notice Updated step Pilot Project WS ERS Updated step Reserves | July 15, 2013 |
| 2.6 3.2 3.8 4.1 | 1.0 / 10 1.0 / 3 1.0 / 1 1.0 / 12 | Updated MMS Changes Updated 1st Note Updated Unit & Load RRS Shortage & Not Dispatchable to SCED Updated Shutdown/Startup | August 9, 2013 |
| 3.8 | 1.0 / 2 | Updated Unit RRS Shortage, Load RRS Shortage, REG Shortage, & added Real-Time Non-Spin Shortage | September 27, 2013 |
| 2.4 3.1 3.2 3.3 3.4 3.5 3.7 4.1 5.1 5.2 5.3 5.4 5.5 6.1 6.2 6.3 6.4 7.1 8.1 | 1.0 / 2 1.0 / 15 1.0 / 4 1.0 / 12 1.0 / 9 1.0 / 7 1.0 / 4 1.0 / 13 1.0 / 14 1.0 / 9 1.0 / 14 1.0 / 13 1.0 / 4 1.0 / 4 1.0 / 7 1.0 / 6 1.0 / 6 1.0 / 4 1.0 / 5 | Updated step Log Updated step Frequency Deviations & step Log Updated step Log Updated step Log Updated step Log Added step RMR & updated step Log Updated step Log Updated step Log Updated step Log Updated step Log Updated step Log Updated step Log Updated step Log Updated step Log Updated step Log Updated step Log Updated note and step Log Updated step Log Added & updated step Log All procedures in this manual have been reviewed | December 13, 2013 |
| 2.6 3.3 5.1 | 1.0 / 11 1.0 / 13 1.0 / 15 | Updated for NPRR542 Updated for NPRR542 Updated for NPRR542, deleted West to North GTL and updated procedure for North to Houston to a new GTL | January 1, 2014 |
| 2.6 3.1 3.3 3.5 3.6 4.1 5.3 5.4 6.4 8.1 | 1.0 / 12 1.0 / 16 1.0 / 14 1.0 / 8 1.0 / 5 1.0 / 14 1.0 / 15 1.0 / 14 1.0 / 7 1.0 / 6 | Updated Site Failover Complete Updated VDI information, step Monitor/Deploy & step 10 Minutes in Response to Low Frequency Updated VDI information Updated VDI information Updated step Terminating Time Error Correction Updated VDI information Updated ERS, Media appeal, TCEQ and VDI information Updated steps Reserves and 1 in Restore firm load and step 2 in Move From EEA Level 2 to EEA Level 1 Updated Note Updated Requests to Decommit Self-committed Resource in Operating Period | April 4, 2014 |
| 2.2 3.1 3.3 4.1 5.1 5.2 6.2 6.3 | 1.0 / 2 1.0 / 17 1.0 / 15 1.0 / 15 1.0 / 16 1.0 / 10 1.0 / 8 1.0 / 7 | Added VDIs to Master QSEs Updated step BAAL Updated SCED Failure & SCED Data Input Failure steps Updated QSGR in Quick Start Generation Resource Added Note, updated Market Notices Advisory & Watch Updated Watch steps Updated Emergency Notice step Updated Emergency Notice step | June 1, 2014 |
| 3.5 5.3 | 1.0 /9 1.0 / 16 | Updated Deploying Non-Spin, added HASL Release & Recall Added Media Appeal | August 1, 2014 |
| 4.1 5.1 5.3 | 1.0 / 16 1.0 / 17 1.0 / 17 | Updated Reference section step 2 Updated Generic Script Added HASL Release step | October 1, 2014 |
| 2.3 2.4 2.6 3.3 3.5 5.1 5.3 | 1.0 / 1 1.0 / 3 1.0 / 13 1.0 / 16 1.0 / 10 1.0 / 18 1.0 / 18 | Updated all steps Updated step Send E-mail Deleted Site Failover with W-N Active & updated step If EBPs are Needed Updated 1st note & updated scripts Added new procedure, “Valley Generation” Updated GMD scripts Updated scripts to consolidate All procedures in this manual have been reviewed | December 15, 2014 |
| 6.2 | 1.0 / 9 | Updated Note and scripts | December 22, 2014 |
| 2.2 3.1 3.2 3.5 3.9 6.2 | 1.0 / 3 1.0 / 181.0 / 5 1.0 / 11 1.0 / 0 1.0 / 10 | Added Dispatch and VDI definitions Updated Objective and BAAL Updated procedure Updated step 1 and added Log on Valley Generation Added new procedure for NOGRR136 Updated scripts | March 1, 2015 |
| 3.1 3.3 3.5 3.10 4.1 5.1 | 1.0 / 19 1.0 / 17 1.0 / 12 1.0 / 0 1.0 / 17 1.0 / 19 | Clarification to step Frequency Deviation & Hydro Operating in Synch. Condenser Mode Updated Dispatch Instruction scripts Clarification to step HASL Release Manually Deploy RRS New GMD procedure Updated Dispatch Instruction scripts Deleted script for GMD | March 30, 2015 |
| 2.6 2.7 3.2 3.3 3.4 3.63.7 3.10 5.1 5.2 5.3 5.4 5.5 6.1 6.2 6.3 6.4 | 1.0 / 14 1.0 / 3 1.0 / 6 1.0 / 18 1.0 / 10 1.0 / 6 1.0 / 5 1.0 / 1 1.0 / 20 1.0 / 11 1.0 / 19 1.0 / 15 1.0 / 5 1.0 / 5 1.0 / 11 1.0 / 8 1.0 / 8 | Moved scripts to new script procedure Moved scripts to new script procedure Updated 1st note and moved scripts to new script procedure Updated step 2 on SCED Data Input Failure & moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Updated 4th bullet on Emergency Notice & moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure | May 1, 2015 |
| All Sections 2.6 3.5 3.9 3.10 5.1 5.2 6.3 | 1.0 / 1 1.0 / 15 1.0 / 13 1.0 / 1 1.0 / 2 1.0 / 21 1.0 / 12 1.0 / 9 | Added a “Q” for numbered QSE scripts Renamed section to Site Failovers and Database Loads Updated link for Monitor in the Valley Generation Updated 1st Note Updated Procedure Purpose and removed script Updated Specific Scripts, New GTC Updated Q#1, Q#2, Q#3, & Q#4 Script titles Removed Watch script | July 15, 2015 |
| 2.6 3.2 3.3 3.4 3.6 3.7 3.9 3.10 5.1 5.2 5.3 5.4 5.5 6.1 6.2 6.3 6.4 | 1.0 / 16 1.0 / 7 1.0 / 19 1.0 / 11 1.0 / 7 1.0 / 6 1.0 /2 1.0 / 3 1.0 / 21 1.0 / 13 1.0 / 20 1.0 / 16 1.0 / 6 1.0 / 6 1.0 / 12 1.0 / 10 1.0 / 9 | Updated step MMS Changes Typical Script Q#19 Updated step Site Failover Q#20 Updated step Site Failover Complete Q#21 Updated Step If EBP’s are needed Q#22 Updated step Site Failover Complete If EBP’s were needed Q#23 Updated step 2 Q#26 Updated SCED Failure step 2 Q#27 & step 4 Q#28 Updated SCED Data Input Failure step 1 Q#29 Updated RLC Failure step 2 Q#30 & step 4 Q#31 Updated LFC (AGC) Failure step 1 Typical Script step 2 Q#32, step 4 Typical script & Q#33 Updated EMMS (LFC and RLC/SCED) Failure step 1 Typical Script, step 2 Q#34, step 5 Typical Script & Q#35 Updated step 3 Q#36 Updated step Initiating Time Error Correction Q#37 Updated step Terminating Time Error Correction Q#38 Updated step Issue Watch and Deploy Non-Spin Q#39 Updated step Issue Emergency Notice & Deploy Load Resources Q#40 Updated step Recall Load Resources Q#41 Updated step Recall Non-Spin Q#42 Updated step Start CFC Test & End CFC Test Typical Scripts Updated step 1 Q#43 Updated step K Level Increases/Decreases Q#44 Updated step Cancel Q#45 Updated Title Operating Condition Script Updated step Hotline Q#46 Updated step Hotline Cancellation Q#47 Updated Title Specific Scripts for Transmission Operator [State Estimator/RTCA/VSAT] Updated step State Estimator/RTCA Not Solved In 30 MIN Q#48 & Q#49 Updated step VSAT Not Solved In 30 MIN Q#50 & Q#51 Updated step Qualifying Facility Directed to Operate Below LSL Q#52 & Q#53 Updated step New GTC Q#54 Updated step Transmission Watch Q#55 & Q#56 Updated Advisory step Issue Advisory Q#1 Updated Advisory step Cancel Advisory Q#2 Updated Watch step Issue Watch Q#3 Updated Watch step Cancel Watch Q#4 First Note, Updated Implement EEA Level 1 step EEA 1 PRC <2300 Q#5 & Q#6 Updated Implement EEA Level 2 step ERS Resources Q#7 Updated Implement EEA Level 2 step Load Resources Q#8 Updated Implement EEA Level 2 step When ERS Business Hours Change Q#9 Updated Implement EEA Level 3 step When ERS Business Hours Change Q#12, and Implement NPRR708 for EEAUpdated Restore Firm Load step 1 Q#13 Updated Move From EEA Level 3 to EEA Level 2 step 1 Q#14 Updated Move From EEA Level 2 to EEA Level 1 step 1 Q#15 Updated Move From EEA Level 1 to EEA Level 0 step 1 Q#16 Updated Cancel Watch step 1 Q#17 Updated step Return to Normal QSE Notification Q#57 Updated step Emergency Notice Q#61 Updated step Emergency Notice Q#65 Updated step Emergency Notice Q#69 Updated step OCN/Advisory/Watch Q#70 All procedures in this manual have been reviewed | December 31, 2015 |
| 1.3 2.1 3.3 5.1 | 1.0 / 2 1.0 / 3 1.0 / 20 1.0 / 22 | Removed Interchange Coordinator Updated System Operator Responsibility and Authority Updated SCED Failure Note Corrected spelling Qualifying Facility Directed to Operate below LSL Q#52 | March 1, 2016 |
| 2.4 3.1 3.2 4.1 | 1.0 / 4 1.0 / 20 1.0 / 8 1.0 / 18 | Added 2nd Send E-Mail Updated Frequency bias and BAAL step Updated Down Ramp Event step 2 Updated QSGR Qualification Test | April 29, 2016 |
| 2.1 2.2 3.1 3.3 3.5 3.9 4.1 5.1 5.5 | 1.0 / 4 1.0 / 4 1.0 / 21 1.0 / 21 1.0 / 14 1.0 / 3 1.0 / 19 1.0 / 23 1.0 / 7 | Updated for COM-002-4 Updated for COM-002-4 Updated for BAL-001-2 and COM-002-4 Updated for COM-002-4 Updated Deploying Non-Spin step Updated for COM-002-4 Updated for COM-002-4 Updated for COM-002-4 Updated for COM-002-4 | June 30, 2016 |
| 5.3 | 1.0 / 21 | Changed Business Hour to Time Period | July 15, 2016 |
| 2.2 3.3 | 1.0 / 5 1.0 / 22 | Added Hotline Call Communication Note Added SCED Failure Frequency Guidelines Updated LFC Failure Step 2 Q#32 Script Title Updated LFC Failure Step 4 Q#33 Script Title Updated EMMS Failure step 2 Q#34 Script Title Updated EMMS Failure step 5 Q#35 Script Title | September 30, 2016 |
| 3.5 5.1 | 1.0 / 15 1.0 / 24 | Updated Valley Generation step 1 Added Specific Scripts for Transmission Operator step Transmission Emergency script Q#71 | November 2, 2016 |
| 4.1 | 1.0 / 20 | Added Real-Time Data Issues known by the QSE All procedures in this manual have been reviewed | December 30, 2016 |
| 1.3 2.1 2.5 2.6 2.7 3.2 3.10 5.1 5.3 5.5 6.1 6.2 6.3 8.1 | 1.0 / 3 1.0 / 5 1.0 / 5 1.0 / 17 1.0 / 4 1.0 / 9 1.0 / 4 1.0 / 25 1.0 / 22 1.0 / 8 1.0 / 7 1.0 / 13 1.0 / 11 1.0 / 7 | Updated Roles/Responsibilities section Updated for IRO-001-4 Updated categories to show RAS Updated procedure purpose Updated procedure purpose Deleted ELRAS and held location open Updated procedure purpose Updated title and all 1st steps Removed step WS ERS Added Implement EEA Level 3 step EEA3 PRC <1000 MW Updated first note Updated procedure purpose Updated procedure purpose Updated procedure purpose Updated procedure purpose | March 31, 2017 |
| 3.1 | 1.0 / 22 | Updated Frequency bias | April 4, 2017 |
| 3.3 5.1 | 1.0 / 23 1.0 / 26 | Added section on ICCP Outages Updated Transmission Watch | April 6, 2017 |
| 3.1 3.5 | 1.0 / 23 1.0 / 16 | Updated Response to Low Frequency step Monitor/Deploy Updated Insufficient Generation step Deploying Non-Spin | June 1, 2017 |
| 3.1 5.3 | 1.0 / 24 1.0 / 23 | Updated Response to Low Frequency step 25 Minutes Updated 1st note, step EEA Level 2 and EEA Level 3 | June 30, 2017 |
| 2.4 3.1 5.3 | 1.0 / 5 1.0 / 25 1.0 / 24 | Updated steps Added note Response to Low Frequency Updated step 20 Minutes and added scripts Added note Implement EEA Level 2 and Level 3 | July 28, 2017 |