- Power Operations Bulletin # 801

ERCOT has posted/revised the Reliability Risk Desk manual.

A copy of the procedure can be found at:

- http://www.ercot.com/mktrules/guides/procedures/index.html

- 7.2	Implement EEA Levels

Procedure Purpose:  To provide for maximum possible continuity of service while maintaining the integrity of the ERCOT system to reduce the chance of cascading outages. If required to assist other Desk during an EEA event refer to appropriate Operating Procedures.

| Protocol Reference | 6.5.7.6.2.2(1)(b) & (13) | 6.5.9.4 | 6.5.9.4.2 |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.5.3 | 4.5.3.1 | 4.5.3.2 | 4.5.3.3 |
|  | 4.5.3.4 |  |  |  |
| NERC Standard | EOP-011-1 R2.1, R2.2.3, R2.2.3.1, R2.2.3.4 |  |  |  |

| Version: 1 | Revision: 3 | Effective Date: July 28, 2017 |
| --- | --- | --- |

|  | Step |  | Action |  |
| --- | --- | --- | --- | --- |
|  | NOTE |  | - IF steady state system frequency falls below 59.91 Hz, ERCOT CAN immediately implement EEA 3. - IF steady state system frequency falls below 59.5 Hz, ERCOT SHALL immediately implement EEA 3. |  |
|  | TCEQ |  | When increased generation is requested during EEA events, Texas Commission on Environmental Quality (TCEQ) will exercise enforcement discretion for exceedances of emission limits as well as operational limits for power generating plants for Generators who exceed air permit limits in order to maximize generation for the duration of the EEA event. ERCOT General Council will send out a Market Notice each time ERCOT enters into an EEA with this reminder. |  |
| ### Implement EEA Level 1 |  |  |  |  |
| 1 |  | IF: - PRC < 2300 MW; |  |  |
| 2 |  | Assist Control Room as needed and monitor Intermittent Renewable Resources (IRR). |  |  |
| LOG |  | Log all actions. |  |  |
| ### Implement EEA Level 2 |  |  |  |  |
|  | Note |  | ERCOT may declare an EEA Level 2 when the clock-minute average system frequency falls below 59.91 Hz for 15 consecutive minutes. |  |
|  | 1 |  | IF: - PRC < 1750 MW or unable to maintain system frequency at 59.91 Hz and is not projected to be recovered above 1750 MW within 30 minutes without the use of EEA Level 2; |  |
|  | 2 |  | Assist Control Room as needed and monitor Intermittent Renewable Resources (IRR). |  |
|  | LOG |  | Log all actions. |  |
| ### Implement EEA Level 3 |  |  |  |  |
|  | Note |  | ERCOT may declare an EEA Level 3 when the clock-minute average system frequency falls below 59.91 Hz for 20 consecutive minutes. |  |
|  | EEA3 PRC <1375 MW |  | ERCOT will declare an EEA Level 3 when PRC cannot be maintained above 1,375 MW. |  |
|  | EEA3 Unable to Maintain 59.91 Hz or PRC <1000 MW |  | IF: - PRC <1000 MW or Unable to maintain system frequency at 59.91 Hz and is not projected to be recovered above 1000 MW or 59.91 Hz within 25 minutes without the use of EEA Level 3; THEN: - Assist Control Room as needed and monitor wind generation. |  |
|  | LOG |  | Log all actions. |  |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Hartmann, Gaddy, Self, and Frosch | Preparers | January 24, 2017 |
| Hartmann, Gaddy and Frosch | Procedure writers and editors | March 27, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | May 26, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | June 23, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | July 24, 2017 |

Manual Change History

| Procedure | Ver/Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All | 1.0 / 0 | New procedures | January 30, 2017 |
| 2.1 3.1 4.4 5.1 7.1 7.2 9.1 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Updated System Operator Responsibility and Authority Updated Up Ramp Event step 2 Updated Panhandle Region Updated Reliability Risk Desk performs STNET Study Updated title and all 1st steps Updated Implement EEA Level 3 steps Updated Title | March 31, 2017 |
| 3.1 | 1.0 / 2 | Updated Down Ramp Event step 1, 2 & 3 Updated Up Ramp Event step 1 & 2 | June 1, 2017 |
| 3.1 7.2 | 1.0 / 3 1.0 / 2 | Updated Down Ramp Event step 2 Updated 1st note, step 1 changed to EEA Level 3 | June 30, 2017 |
| 7.2 | 1.0 / 3 | Added note Implement EEA Level 2 and Level 3 | July 28, 2017 |