- Power Operations Bulletin # 827

ERCOT has posted/revised the Reliability Unit Commitment manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

- http://www.ercot.com/mktrules/guides/procedures/index.html

## 3.7	Manual Dispatch of Resources

Procedure Purpose:  Manually Dispatch Resources as necessary to ensure system security when HRUC cannot be used.

| Protocol Reference | 5.1(12) | 5.5.2 | 5.5.3(3) | 6.5.9 (3) |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | EOP-011-1 R1.2.4 | IRO-006-TRE-1 R1, R2 |  |  |

| Version: 1 | Revision: 12 | Effective Date: February 28, 2018 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - ERCOT shall honor all Resource operating parameters in Dispatch Instruction / Operating Instructions under normal conditions and Emergency Condition. During Emergency Conditions, ERCOT may verbally request QSE’s to operate its Resources outside normal operating parameters. If such request is received by a QSE, the QSE shall discuss the request with ERCOT in good faith and may choose to comply with the request - A QSE can self-commit by setting the telemetered Resource Status to ONOPTOUT for the first SCED run that the Resource is On-Line and available for SCED dispatch during the first hour of a contiguous block of RUC-Committed Hours - If a QSE-committed Resource experiences a Forced Outage or Startup Loading Failure in an hour for which another Resource under the control of the same QSE is committed by a RUC instruction, the QSE may opt out of the RUC instruction by self-committing the Resource as described above |
| ### Manual Commit of a Resource |  |
| 1 | IF: - It has been determined that a Resource is needed in real-time for a transmission condition or critical inertia level after the close of the Adjustment Period (Typically will be short start, Quick Start resources available or resources scheduled to come off within the operating hour); THEN: - Notify QSE an electronic Dispatch Instruction will be issued - Verify lead time with QSE - Issue an electronic Dispatch Instruction to commit the Resource, - Choose “COMMIT” as the Instruction Type from Resource level - Enter reason, such as contingency name, capacity or critical inertia level in “other information” - Confirm with QSE that the electronic Dispatch Instruction was received - The same Resource attributes communicated programmatically must be communicated when giving a VDI. When issuing a VDI or confirmation, ensure the use of three-part communication: - Issue the Operating Instruction - Receive a correct repeat back - Give an acknowledgement See Desktop Guide Common to Multiple Desks Section 2.3 for additional information to submit a correct electronic Dispatch Instruction. |
| LOG | Log all actions. |
| ### Manual Dispatch of an OFFQS Resource |  |
| 1 | IF: - It has been determined that a OFFQS Resource is needed in real-time for a transmission condition; THEN: - Notify QSE an electronic Dispatch Instruction will be issued - Verify LSL when resource is generating to the grid - Issue an electronic Dispatch Instruction to commit the Resource, - Verbal Dispatch Instructions [Transmission Desk] - Notification Time: This is the time the QSE was first notified. - Initiation Time: This is the hour ending start time of the VDI - Completion Time: This is the hour ending end time of the VDI (if known) - Current Operating Level: “0” - Final Operating Level: LSL minimum - Current State: “OFFQS” - Final State: “ON” - Instruction Type: Choose “OTHER FOR RESOURCE” - Reason: Voltage Stability or critical inertia level - Enter reason, such as contingency name in “other information” - Confirm with QSE that the electronic Dispatch Instruction was received - The same Resource attributes communicated programmatically must be communicated when giving a VDI. When issuing a VDI or confirmation, ensure the use of three-part communication: - Issue the Operating Instruction - Receive a correct repeat back - Give an acknowledgement See Desktop Guide Common to Multiple Desks Section 2.3 for additional information to submit a correct electronic Dispatch Instruction. |
| LOG | Log all actions. |
| ### Manual Dispatch to take a Unit Off-Line |  |
| 1 | IF: - A manual dispatch instruction / Operating Instruction will result in the unit being dispatched off-line (i.e., less than the minimum operating limit for that Resource); THEN: - Issue an electronic Dispatch Instruction taking the Resource to zero until it can be released, - Choose “DECOMMIT” as the Instruction Type from Resource level - Enter contingency name in “other information” When issuing a VDI or confirmation, ensure the use of three-part communication: - Issue the Operating Instruction - Receive a correct repeat back - Give an acknowledgement - Ensure QSE updates telemetry. |
| ### Manual Dispatch to take a Unit of a Combined Cycle Off-line |  |
| 1 | IF: - System conditions require one unit of a Combined Cycle Plant to be manually dispatched off-line; THEN: - Contact the QSE and request which unit the QSE would like to shutdown, - Request the planned/current CC configuration and then the CC configuration that the Resource will need to be operating, - Issue an electronic Dispatch Instruction confirmation to “COMMIT” the QSE to their CC configuration. All data must be entered but pay attention to the following details. - Choose the proper QSE from the Participant name - Select the CC configuration that you are instructing the Resource to operate in from the Resource name - Choose “COMMIT” as the Instruction Type from Resource level - Enter contingency name in “other information” When issuing a VDI or confirmation, ensure the use of three-part communication: - Issue the Operating Instruction - Receive a correct repeat back - Give an acknowledgement - Log the above information. |
| ### Manual Dispatch to bring a Unit of a Combined Cycle On-line |  |
| 1 | IF: - System conditions require a unit of a Combined Cycle Plant to be manually dispatched on-line; THEN: - Contact the QSE and notify which unit will be committed, - Request the planned/current CC configuration and then the CC configuration that the Resource will need to be operating, - Determine the temporal constraints for the CC configuration. - Issue an electronic Dispatch Instruction to “COMMIT” the QSE to their CC configuration. All data must be entered but pay attention to the following details. - Choose the proper QSE from the Participant name - Select the CC configuration that you are instructing the Resource to operate in from the Resource name - Choose “COMMIT” as the Instruction Type from Resource level - Enter contingency name or critical inertia level in “other information” When issuing a VDI or confirmation, ensure the use of three-part communication: - Issue the Operating Instruction - Receive a correct repeat back - Give an acknowledgement - Log the above information. |
| ### Canceling RUC Commitments |  |
| 1 | IF: - A Resource is RUC committed that needs to be canceled; - Only cancel RUC commits if the ERCOT Operator Resource commitment was unintended. THEN: - Issue an electronic Dispatch Instruction to cancel the RUC instruction - Choose “CANCEL RUC COMMIT” as the Instruction Type - Enter “unintended commitment” in other information |
| LOG | Log all actions. |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Frosch, Hartmann, Barcalow, Lowrie, and Stone | Preparers | November 10, 2010 |
| Frosch and Hartmann | Procedure writers and editors | November 29, 2010 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2010 |
| Frosch and Hartmann | Procedure writers and editors | January 26, 2011 |
| Frosch and Hartmann | Procedure writers and editors | March 23, 2011 |
| Frosch and Hartmann | Procedure writers and editors | April 20, 2011 |
| Frosch and Hartmann | Procedure writers and editors | June 6, 2011 |
| Frosch and Hartmann | Procedure writers and editors | July 18, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 22, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 30, 2011 |
| Frosch and Hartmann | Procedure writers and editors | October 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 16, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | April 25, 2012 |
| Frosch and Hartmann | Procedure writers and editors | July 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | October 26, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 26, 2013 |
| Frosch and Hartmann | Procedure writers and editors | May 28, 2013 |
| Frosch and Hartmann | Procedure writers and editors | July 8, 2013 |
| Cheng, Frosch and Hartmann | Procedure writers and editors | August 7, 2013 |
| Frosch and Hartmann | Procedure writers and editors | December 11, 2013 |
| Frosch and Hartmann | Procedure writers and editors | December 20, 2013 |
| Frosch, Gaddy and Hartmann | Procedure writers and editors | April 1, 2014 |
| Frosch, Gaddy and Hartmann | Procedure writers and editors | May 27, 2014 |
| Frosch and Hartmann | Procedure writers and editors | September 29, 2014 |
| Frosch and Hartmann | Procedure writers and editors | December 10, 2014 |
| Frosch and Hartmann | Procedure writers and editors | February 25, 2015 |
| Frosch and Hartmann | Procedure writers and editors | April 29, 2015 |
| Hartmann and Gaddy | Procedure writers and editors | July 13, 2015 |
| Hartmann and Gaddy | Procedure writers and editors | September 25, 2015 |
| Hartmann and Gaddy | Procedure writers and editors | December 22, 2015 |
| Frosch, Hartmann and Gaddy | Procedure writers and editors | January 22, 2016 |
| Hartmann and Gaddy | Procedure writers and editors | February 23, 2016 |
| Frosch, Hartmann and Gaddy | Procedure writers and editors | June 24, 2016 |
| Hartmann and Gaddy | Procedure writers and editors | September 26, 2016 |
| Hartmann and Gaddy | Procedure writers and editors | October 31, 2016 |
| Hartmann and Gaddy | Procedure writers and editors | December 23, 2016 |
| Hartmann, Gaddy and Frosch | Procedure writers and editors | March 27, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | May 26, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | June 23, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | September 27, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | December 22, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | February 22, 2018 |

Manual Change History

| Procedure | Ver/Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All Sections | 1.0 / 0 | New procedures for all sections for Nodal implementation | November 28, 2010 |
| 2.3 2.4 3.2 3.3 4.3 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Added new procedure “Phase Shifter Tap Settings” Updated Note Updated step “Monitor” Updated steps “Commit/De-Commit”, “Violated Constraints” and “HRUC Committed” Updated step “Review”, “A/S Insufficiency from DAM” and “DRUC Committed” | December 1, 2010 |
| 2.3 4.2 4.3 4.4 | 1.0 / 2 1.0 / 1 1.0 / 2 1.0 / 1 | Updated “Review Weather Data Information” step 2 Added steps “DRUC Committed for Capacity Shortage” and “Projected Reserve Capacity Shortage” Updated steps “DAM Timeline Deviation, DAM Failure, DRUC Delay & Software Failure” change to step 1 | December 15, 2010 |
| 3.2 4.3 4.1 4.4 6.1 | 1.0 / 2 1.0 / 3 1.0 / 2 - / 2 1.0 / 1 | Updated step “HRUC Committed Units”, “Manual Commitment”, added steps “Excess Generation” and “Canceling RUC commitments” Updated step DRUC Committed Units”, “Manual Commitment, added steps “Excess Generation” and “Canceling RUC commitments” Updated step “DAM Timeline Deviation”, DAM Failure”, DRUC Delay” Updated scripts Updated script | January 31, 2011 |
| 3.2 3.3 3.5 4.3 4.4 6.1 | 1.0 / 3 1.0 / 2 - / 0 - /4 - / 3 1.0 / 2 | Updated step Canceling RUC Commitments Deleted HRUC Timeline Deviation and updated HRUC Failure/Timeline Deviation Added new section Updated step Canceling RUC Commitments Updated step DAM Timeline Deviation in DAM Timeline Deviation/Failure Timeline not Met in section DRUC Timeline Deviation/Failure Updated Watch and Emergency Notice | March 25, 2011 |
| 2.5 3.2 3.3 4.3 6.1 6.2 | 1.0 / 1 1.0 / 4 1.0 / 3 1.0 / 5 1.0 / 3 1.0 / 1 | Updated Monthly MIS Posting Updated step Canceling RUC Commitments Updated step Failure Updated step Canceling RUC Commitments Updated step 1 in Watch and Emergency Notice Updated step & removed step Market Notification | April 22, 2011 |
| 3.2 3.5 4.3 4.4 5.2 6.1 | 1.0 / 5 1.0 / 1 1.0 / 6 1.0 / 4 1.0 / 1 1.0 / 4 | Updated steps HRUC Committed Units and Approval Updated all steps Updated step Approval Updated step DAM Timeline Deviation Updated step Long Lead Times Updated all steps | June 8, 2011 |
| 2.3 3.1 3.2 3.5 4.2 4.3 4.4 4.5 | 1.0 / 3 1.0 / 1 1.0 / 6 1.0 / 2 1.0 / 2 1.0 / 7 1.0 / 5 1.0 / 1 | Added steps for Publish A/S Requirements Updated Load Forecast step Updated steps Excess Generation, A/S Insufficiency from SASM, Violated Constraints and Approval Corrected title to match TOC and updated 1st note Updated Load Forecast step Updated Approval step Added subtitles, step DRUC Delay & step 1 Moved section 2.6 to 4.5 | July 20, 2011 |
| 2.3 2.4 3.2 3.3 4.3 6.1 7.1 | 1.0 / 4 - / 1 1.0 / 7 1.0 / 4 1.0 / 8 1.0 / 5 1.0 / 1 | Added Note to Increasing A/S Requirements before A/S Obligations Publish Added information on RMR Resource Commitment Updated step Excess Generation, added RMR Resources, RMR Commitment and Canceling RUC Commitments Updated step Commit/Decommit Resources by VDI Updated step Canceling RUC Commitments Added Projected Reserve Capacity Shortage to Watch Updated 4th note | August 24, 2011 |
| 3.2 4.2 4.3 6.1 7.1 | 1.0 / 8 1.0 / 3 1.0 / 9 1.0 / 6 1.0 / 2 | Added Note, updated step Hotline, Post and added step Cancel Deleted step RMR, updated Manual Commitment, deleted Note Updated Note Added Extreme Hot Weather in Watch Updated 3rd note and step 1 | September 1, 2011 |
| 2.3 2.4 3.1 3.2 4.3 4.4 4.5 4.6 4.5 Original | 1.0 / 5 1.0 / 2 1.0 / 2 1.0 / 9 1.0 / 10 1.0 / 6 1.0/ 0 1.0 / 0 1.0 / 2 | Deleted Phase Shifter Tap Settings Deleted step Resources Updated step Manual Commitment in Tasks prior to execution of HRUC Updated step RMR Resources and Canceling RUC Commitments Updated step for Canceling RUC Commitments Moved A/S Insufficiency in DAM to section 4.5 & DAM Failure to section 4.6 Moved A/S Insufficiency in DAM to section 4.5 & deleted Increase A/S Capacity needs about Day-Ahead Requirements Moved from section 4.5 Deleted procedure (was section 4.5), duplicate | November 1, 2011 |
| 2.3 6.1 | - / 6 1.0 / 7 | Removed Invalid SPS/RAP due to Outage Updated Post in “Notifications” All procedures in this manual have been reviewed. | December 15, 2011 |
| 1.2 3.5 4.3 4.6 | 1.0 / 1 1.0 / 3 1.0 / 11 1.0 / 3 | Updated Scope Updated all steps Updated A/S Insufficiency from DAM Updated desktop guide section | January 19, 2012 |
| 2.1 2.3 2.5 3.1 3.2 3.3 3.7 4.2 4.3 4.4 4.5 4.6 5.2 6.1 7.1 | 1.0 / 1 1.0 / 7 1.0 / 2 1.0 / 3 1.0 / 10 1.0 / 5 1.0 / 0 1.0 / 4 1.0 / 12 - / 7 1.0 / 3 1.0 / 4 1.0 / 2 1.0 / 8 1.0 / 3 | Updated 4th Paragraph Updated Desktop Guide reference Updated Monthly MIS Posting Updated Desktop Guide reference Updated Desktop Guide references and step After Approval Added step Create Save Case Added new procedure Projected Capacity Reserve Shortage with no Market Solution Updated Desktop Guide references Updated Desktop Guide references and added step After Approval Added step 2 Updated Desktop Guide reference Updated Desktop Guide reference Added step Create Save Case Updated step 1 of Watch Updated Desktop Guide references | March 1, 2012 |
| 1.1 2.1 3.1 3.2 3.3 4.2 4.3 5.1 5.2 6.1 8.1 | 1.0 / 1 1.0 / 2 1.0 / 4 1.0 / 11 1.0 / 6 1.0 / 5 1.0 / 13 1.0 / 1 1.0 / 3 1.0 / 9 1.0 / 1 | Changed Shift Engineer to Operations Support Engineer Changed TSP,DSP to TO Changed Shift Engineer to Operations Support Engineer Changed Shift Engineer to Operations Support Engineer Changed Shift Engineer to Operations Support Engineer Changed Shift Engineer to Operations Support Engineer and added WRUC Changed Shift Engineer to Operations Support Engineer and Manual Commitment Changed Shift Engineer to Operations Support Engineer Changed Shift Engineer to Operations Support Engineer and updated step Long Lead Times for NPRR402 Updated OCN, Advisory, Watch, Emergency Notice sections Changed Shift Engineer to Operations Support Engineer | May 1, 2012 |
| 1.1 1.3 2.3 3.1 3.2 3.3 4.2 4.3 4.4 5.2 6.1 7.1 | 1.0 / 2 1.0 / 1 1.0 / 8 1.0 / 5 - / 12 - / 7 - / 6 - / 14 - / 8 1.0 / 4 1.0 / 10 1.0 / 4 | Updated last paragraph, HRUC Removed ERCOT Shift Supervisor paragraph Updated step 3, added Fuel Switching and Optimize Fuel Supply & 2nd note Changed Shift Engineer to Operations Support Engineer Updated HRUC Committed Units Updated Create Save Case Updated Manual Commitment on 14:30 each day Updated DRUC Committed Units Updated step 2 in Delay of DRUC Updated Create Save Case Updated all step 1’s Updated 4th note | July 16, 2012 |
| 2.2 3.2 4.3 | 1.0 / 1 1.0 / 13 1.0 / 15 | Added Hotline Call Communication Updated Manual Commitment and Validate Updated Manual Commitment and Validate All procedures in this manual have been reviewed. | November 1, 2012 |
| 2.3 4.3 4.6 | 1.0 / 9 1.0 / 16 1.0 / 5 | Added Blackstart Availability Updated Review Updated steps SASM not able to Procure all A/S Requested & Cancel Emergency Notice | March 1, 2013 |
| 3.1 3.2 3.3 3.5 3.7 4.3 4.4 4.5 4.6 5.2 6.1 | 1.0 / 6 1.0 / 14 1.0 / 8 1.0 / 4 1.0 / 1 1.0 / 17 1.0 / 9 1.0 / 4 1.0 / 6 1.0 / 5 1.0 / 11 | Updated step Deselect Contingencies Updated step Monitor, Excess Generation, Hotline, & Cancel Updated step Failure & Create Save Case Updated step REG/RRS Updated all steps Updated 1st Note, A/S Insufficiency from DAM, Excess Generation &DRUC Committed from Capacity Shortage Updated all steps Updated all steps Updated all steps Updated step Create Save Case Updated Notifications | June 1, 2013 |
| 3.5 4.3 4.4 4.6 6.1 | 1.0 / 5 1.0 / 18 1.0 / 10 1.0 / 7 1.0 / 12 | Correct typo in script Correct typo’s in scripts Updated Delay of DRUC steps Corrected reference in desktop guide Updated step 1 in Watch & Emergency Notice | July 15, 2013 |
| 3.2 3.3 | 1.0 / 15 1.0 / 9 | Updated step HRUC Committed Units, Manual Commitment, HRUC Decommitted Resources & Approval Updated step Create Save Case | August 9, 2013 |
| 3.2 4.3 5.1 5.2 | 1.0 / 16 1.0 / 19 1.0 / 2 1.0 / 6 | Updated steps Violated Constraints, HRUC Committed Units, RMR Commitment & Manual Commitment Updated steps Violated Constraints, DRUC Committed Units & Manual Commitment Updated titles Updated Violated Constraints, Disapprove & Log. Deleted Long Lead Times, All procedures in this manual have been reviewed. | December 13, 2013 |
| 3.3 4.4 4.6 6.1 | 1.0 / 10 1.0 / 11 1.0 / 8 1.0 / 13 | Updated for NPRR542 Updated for NPRR542 Updated for NPRR542 Updated for NPRR542 and 529 | January 1, 2014 |
| 2.3 3.2 3.3 3.6 4.3 6.2 6.3 | 1.0 / 10 1.0 / 17 - / 11 1.0 / 1 1.0 / 20 1.0 / 0 1.0 / 2 | Updated Review and Select Load Forecast Updated step System Summary, HRUC Committed Units & VDI information Updated VDI information Added Manual Commit of a Resource & Canceling RUC Commitments Updated VDI information Updated DRUC Committed Units & VDI information Added new EEA procedure Change section number from 6.2 to 6.3 | April 4, 2014 |
| 2.2 2.3 2.4 2.5 3.2 3.6 4.5 4.6 5.2 6.1 | 1.0 / 2 1.0 / 11 1.0 / 3 1.0 / 3 1.0 / 18 1.0 / 2 1.0 / 5 1.0 / 9 1.0 / 7 1.0 / 14 | Added VDIs to Master QSEs Added Note to Increasing A/S before Publishing Added Note Updated Monthly MIS Posting step Updated step A/S Infeasibility Updated step 1 Updated step A/S Insufficiency Offers Updated DAM Failure Updated step Disapprove Added Note, updated Advisory & Watch | June 1, 2014 |
| 3.2 6.1 | 1.0 / 19 1.0 / 15 | Updated Undeliverable A/S Capacity, added STNET Study and title change on VSAT and RUC perform AC Analysis Updated Generic Script | October 1, 2014 |
| 3.2 3.2 4.3 6.2 | 1.0 / 20 1.0 / 20 1.0 / 21 1.0 / 1 | Updated step STNET Study, HRUC Committed Units & Manual Commitment Updated STNET Study, HRUC Committed Units & Manual Commitment Updated step DRUC Committed Units & Manual Commitment Added step All procedures in this manual have been reviewed | December 15, 2014 |
| 2.2 2.3 3.2 3.3 3.6 4.3 4.4 6.2 | 1.0 / 3 1.0 / 12 1.0 / 21 1.0 / 12 1.0 / 3 1.0 / 22 1.0 / 12 1.0 / 2 | Added Dispatch & Verbal Dispatch Instruction Deleted Meterlogix number. Updated Priority Outages Corrected VDI vs. Dispatch Instruction and Manual Commitment Corrected VDI vs. Dispatch Instruction Corrected VDI vs. Dispatch Instruction Updated step Manual Commitment & corrected VDI vs. Dispatch Instruction Updated DAM Timeline Deviation Corrected VDI vs. Dispatch Instruction | March 1, 2015 |
| 3.2 3.3 3.5 3.6 3.7 4.3 4.4 4.5 4.6 6.1 | 1.0 / 22 1.0 / 13 1.0 / 6 1.0 / 4 1.0 / 2 1.0 / 23 1.0 / 13 1.0 / 6 1.0 / 10 1.0 / 16 | Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Updated to implement NPRR679 Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure | May 1, 2015 |
| All Sections 5.2 | 1.0 / 1 1.0 / 8 | Added a “Q” for QSE scripts Updated Disapprove with email notification | July 15, 2015 |
| 3.6 | 1.0 / 5 | Updated 1st note | October 1, 2015 |
| 2.5 3.3 3.5 3.7 4.3 4.4 4.5 4.6 6.1 | 1.0 / 4 1.0 / 14 1.0 / 7 1.0 / 3 1.0 / 24 1.0 / 14 1.0 / 7 1.0 / 11 1.0 / 17 | Updated Monthly MIS Posting Added step After 20th of the month Updated step Last Day of the Month Updated HRUC Failure/Timeline Deviation step Failure Q#79 & Q#80 Updated step REG/RRS – RUC Committed Shortages Q#81& Q#82 Updated step Hotline Q#83 Updated step Cancel Q#84 Updated step A/S Insufficiency from DAM Q#86 Updated step Excess Generation Typical Script Q#87 & Q#88 Updated DAM Timeline Deviation step DAM Timeline Deviation Q#92 Updated Title DRUC Delay Updated DRUC Delay step DRUC Completes By 18:00 Q#94 Updated DRUC Delay step 2 Typical Script Q#96 Updated step A/S Insufficiency Offers Q#97 Updated step DAM Complete with A/S Q#98 Updated step Cancel Watch Q#99 Updated step DAM Failure Q#100 Updated step Cancel Watch Q#101 Updated Title Operating Condition Script Updated Operating Condition Script step Hotline Q#46 Updated Operating Condition Script step Hotline Cancellation Q#47 All procedures in this manual have been reviewed | December 31, 2015 |
| 2.1 3.6 3.6 3.7 | 1.0 / 3 1.0 / 0 1.0 / 6 1.0 / 4 | Updated System Operator Responsibility and Authority Added new Assigning Ancillary Services procedure Change section number from 3.6 to 3.7 Change section number from 3.7 to 3.8 Updated Hotline Q#83 Updated Cancel Q#84 | February 10, 2016 |
| 1.3 5.2 | 1.0 / 2 1.0 / 9 | Removed Interchange Coordinator Added step EDI step | March 1, 2016 |
| 2.1 2.2 2.4 3.1 3.2 3.3 3.6 3.74.3 5.2 6.1 6.2 | 1.0 / 4 1.0 / 4 1.0 / 4 1.0 / 7 1.0 / 23 1.0 / 15 1.0 / 1 1.0 / 71.0 / 25 1.0 / 10 1.0 / 18 1.0 / 3 | Updated for COM-002-4 Updated for COM-002-4 Added steps Note, Resources, 1, 2, & 3 Updated RMR Consideration &Manual Commitment steps Updated for COM-002-4 Updated for COM-002-4 Updated for COM-002-4 Updated for COM-002-4 & noteUpdated for COM-002-4 Updated for COM-002-4 Updated for COM-002-4 Updated for COM-002-4 | June 30, 2016 |
| 3.4 | 1.0 / 1 | Added Resources Startup Time Less Than One Hour | September 30, 2016 |
| 6.2 | 1.0 / 5 | Deleted step 2 | November 2, 2016 |
|  |  | All procedures in this manual have been reviewed | December 30, 2016 |
| 1.3 2.1 2.5 3.7 5.2 6.1 6.3 8.1 | 1.0 / 3 1.0 / 5 1.0 / 5 1.0 / 8 1.0 / 11 1.0 / 19 1.0 / 3 1.0 / 2 | Deleted section 1.3 Updated for IRO-001-4 Updated procedure purpose Updated Monthly MIS Posting Updated note Updated Manual Dispatch to take a Unit Off-Line step 1 Updated note Updated Title and all 1st steps Updated Market Notifications steps Updated Note Updated Title and QSE Issues step 1 and step 3 | March 31, 2017 |
| 3.2 3.6 3.7 3.8 4.3 | 1.0 / 24 1.0 / 2 1.0 / 9 1.0 / 5 1.0 / 26 | Updated step Excess Generation Updated step OpsMon Display to Splunk Display Updated Manual Commit of a Resource step 1 Updated step Monitor Updated step Excess Generation | June 1, 2017 |
| 3.2 3.7 | 1.0 / 25 1.0 / 10 | Added Manual Commitment to bring a Combined Cycle On Line Updated 1st Note and Manual Dispatch to bring a Unit of a Combined Cycle On-line | June 30, 2017 |
| 3.7 | 1.0 / 11 | Added Manual Dispatch of an OFFQS Resource | September 29, 2017 |
| 2.4 7.1 | 1.0 / 5 1.0 / 5 | All procedures in this manual have been reviewed Removed Greens Bayou Unit 5 Updated Primary Control Center 4th note | December 28, 2017 |
| 3.7 | 1.0 / 12 | Updated Manual Commit of a Resource, Manual Dispatch of an OFFQS Resource and Manual Dispatch to bring a Unit of a Combined Cycle On-line | February 28, 2018 |