- Power Operations Bulletin # 855

ERCOT has posted/revised the Reliability Risk Desk manual.

A copy of the procedure can be found at:

- http://www.ercot.com/mktrules/guides/procedures/index.html

## 5.1	STNET Study

Procedure Purpose: To review and analyze future voltage violations.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standand | IRO-001-4 R1 | TOP-001-4 R2 | VAR-001-4.2 R2 |  |

| Version: 1 | Revision: 3 | Effective Date: August 31, 2018 |
| --- | --- | --- |

| Step | Action |  |
| --- | --- | --- |
| ### Reliability Risk Desk performs STNET Study |  |  |
| NOTE | Each hour run a STNET study for four hours out (example it is 0100, run study for 0500) to review voltage violations. |  |
| Voltage Contingencies | IF: - Voltage contingencies exist; THEN: - Check “Voltage Tracking Issues spreadsheet” on Sharepoint to ensure the contingency is not listed. - If not listed, convey the voltage violations to the Transmission and Security Operator - Create a savecase, use naming convention “SC_RRD(HE)_(DATE) - Make at least one detailed log entry per shift that the studies are being executed. If any new voltage violations are identified that do not have a solution, log the information and notify the Transmission and Security Operator of the new violation(s). IF: - Unsolved contingencies exists; THEN: - Communicate any unsolved contingency to the Shift Engineer and Transmission Security Desk Operator for potential solutions. - Some potential solutions could be transmission switching, creation of a manual constraint, bringing on an additional Resource, returning a planned outage, or development of a CMP. |  |
| Violated Constraints | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP Binding Constraint Summary Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP Constraint Summary REVIEW: - Violated constraints. If needed, notify Operations Support Engineer to determine the validity; IF: - Invalid, no further action is required; IF: - Valid; AND - Related to a phase shifter tap settings, THEN: - Notify Operations Support Engineer to determine and determine if adjusting a Phase Shifter would reduce the flow, - Create Suggestion Plan for Constraint, - Manually commit resources as needed - Refer to Desktop Guide Reliability Risk Desk Section 2.5 and 2.6. |  |
| Phase Angles | Monitor phase angles during the 4 hour ahead voltage studies IF: - Phase angle exceedances exists; THEN: - Communicate any phase angle exceedances to the Shift Engineer and Transmission Security Desk Operator for potential solutions. - Some potential solutions could be transmission switching, creation of a manual constraint, bringing on an additional Resource, returning a planned outage, or development of a CMP. |  |
| LOG | Log actions taken. |  |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Hartmann, Gaddy, Self, and Frosch | Preparers | January 24, 2017 |
| Hartmann, Gaddy and Frosch | Procedure writers and editors | March 27, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | May 26, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | June 23, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | July 24, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | September 27, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | December 22, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | February 22, 2018 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | March 26, 2018 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | April 27, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | May 25, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | August 24, 2018 |

Manual Change History

| Procedure | Ver/Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All | 1.0 / 0 | New procedures | January 30, 2017 |
| 2.1 3.1 4.4 5.1 7.1 7.2 9.1 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Updated System Operator Responsibility and Authority Updated Up Ramp Event step 2 Updated Panhandle Region Updated Reliability Risk Desk performs STNET Study Updated title and all 1st steps Updated Implement EEA Level 3 steps Updated Title | March 31, 2017 |
| 3.1 | 1.0 / 2 | Updated Down Ramp Event step 1, 2 & 3 Updated Up Ramp Event step 1 & 2 | June 1, 2017 |
| 3.1 7.2 | 1.0 / 3 1.0 / 2 | Updated Down Ramp Event step 2 Updated 1st note, step 1 changed to EEA Level 3 | June 30, 2017 |
| 7.2 | 1.0 / 3 | Added note Implement EEA Level 2 and Level 3 | July 28, 2017 |
| 7.2 | 1.0 / 4 | Updated Implement EEA Level 3 | September 29, 2017 |
| 8.1 | 1.0 / 1 | All procedures in this manual have been reviewed Updated Primary Control Center 4th note | December 28, 2017 |
| 3.3 | 1.0 / 1 | Updated Day Ahead RRS Sufficiency Monitoring, moved Real-time RRS Sufficiency Monitoring down, added Look Ahead Critical Inertia Level Sufficiency Monitoring and Real-time Critical Inertia Level Sufficiency Monitoring | February 28, 2018 |
| 9.1 | 1.0 / 2 | Updated Note | March 30, 2018 |
| 2.2 | 1.0 / 1 | Updated procedure purpose | May 1, 2018 |
| 5.1 | 1.0 / 2 | Added Phase Angles steps | May 31, 2018 |
| 5.1 | 1.0 / 3 | Updated and named step to Voltage contingencies | August 31, 2018 |