- Power Operations Bulletin # 868

ERCOT has posted/revised the Shift Supervisor Desk manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

## http://www.ercot.com/mktrules/guides/procedures/index.html

## 6.1	Reports

Procedure Purpose: Provide reporting criteria and instructions for the daily reports sent to the PUC, the process to report certain events to the Texas Reliability Entity, posting EEA notices to RCIS and the process for reporting system disturbances to NERC and DOE.

| Protocol Reference | 22 (B) | 6.5.1.2 (4) |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 3.2.3 | 4.7 |  |  |
| NERC Standard | EOP-004-3 R1, R2 | EOP-010-1 R1, R2 | EOP-011-1 R2, R2.1, R2.2, R2.2.2, R2.2.3, R2.2.3.2, R2.2.3.3, R2.2.5 |  |

| Version: 1 | Revision: 36 | Effective Date: November 1, 2018 |
| --- | --- | --- |

| Step | Action |  |
| --- | --- | --- |
| ### PUCT Daily Report |  |  |
| Initial Report | Complete the PUCT Daily Report template between 0300 – 0400 and again between 1400 – 1500 each day. |  |
| E-Mail Report | E-mail the report to the distribution list entitled “PUC-Available Generating Resources.” |  |
| Update Report | Update and resend report when system conditions change that cause concern. Some examples are below: - The probability of an EEA event increases. Give reason(s) for concerns - When Off-Line Non-Spin is deployed for capacity (provide times) - A special update is not needed; provide information next time report is updated. - Conditions change that required new notices to be issued or cancelled - OCN, Advisory, Watch, or Emergency Notice (excluding GMD Advisory’s) - Clarify whether Transmission Watch/Emergency is due to a planned or forced outage (state the area of the state) noting the date and time - Do NOT update report for DAM/DRUC delays - Do NOT update report for tool outages. - The Gibbons Creek Bryan East/Green Prairie 138 kV double circuit transmission line trips, or if unplanned outages of generation units cause security problems in the Bryan-College Station area - Localized gas curtailments, not expected to cause reliability issues (be specific, how much is derated) - Deployment of Load Resources - Any Nuclear Resource issues (including trips, coming off-line, high risk activities, de-ratings, etc.) Do Not use abbreviations, spell words out. Send updated report when conditions have returned to normal. |  |
| Weather Information | The temperatures are automatically pulled from the EMS, however please verify temperatures from a National or Local Weather Service for each city listed and adjust as necessary. |  |
| Guidelines for Determining EEA Potential | Use the following guidelines to determine the potential for EEA when completing the PUCT Daily Report: Potential for EEA Level 1 - Low - Sufficient capacity to cover peak demand - An Advisory is in effect for Physical Responsive Capability. - Medium - A Watch is in effect for Physical Responsive Capability. - Loss or delay of generation availability during peak demand that may diminish Physical Responsive Capabilities - Excel MAI shows multiple hours of insufficient reserves and there is belief it is a significant threat - High - A Watch is in effect for Physical Responsive Capability and trending downward after procuring quick-start capacity - Excel MAI shows multiple hours of insufficient reserves AND ERCOT has been unable to correct the capacity insufficiency over several hours AND ERCOT believes it is a significant threat - Critical - EEA Level 1 in effect Potential for EEA Level 2 - Low - Sufficient capacity to cover peak demand - An Advisory is in effect for Physical Responsive Capability - Medium - EEA Level 1 in effect - High - Physical Responsive Capability ≤ 1750 MW and trending downward - Critical - Physical Responsive Capability ≤ 1375 MW and trending downward Potential for EEA Level 3 - Low - Sufficient capacity to cover peak demand - High - EEA Level 2 in effect - Physical Responsive Capability < 1000 MW and trending downward, OR - Unable to maintain frequency ≥ 59.8 Hz - Critical - EEA Level 3 in effect |  |
| ### Unit Trip Posting |  |  |
| Report | Complete the Unit Trip posting for the previous day between 0000 – 0800 each day of the week. |  |
| Analyze | Review: - Any unit trips from the previous day, - Post an Operational Information message, low priority, on MIS Public |  |
| <450 MW | IF: - No trips are greater than 450 MW, - Post the following message example on MIS Public |  |
| Post | No sudden loss of generation greater than 450 MW occurred on <Date>. |  |
| ≥450 MW | IF: - A trip was 450 MW or more, - Post the following message example on MIS Public |  |
| Post | On <Date>, a sudden loss of generation occurred at <Time> totaling *** MW. Frequency declined to **.*** Hz, ERCOT load was **,*** MW. |  |
| Multiple Trip Example | On <Date>, a sudden loss of generation occurred at <Time> totaling *** MW. Frequency declined to **.*** Hz, ERCOT load was **,*** MW. Another sudden loss of generation occurred at <Time> totaling *** MW. Frequency declined to **.*** Hz, ERCOT load was **,*** MW. |  |
| ### Event Analysis Reporting |  |  |
| 1 | WHEN an event occurs that is listed on the “event list” below, before shift is over: - E-mail information to Manager, System Operations and Designee - The subject line of the e-mail should read “TRE Event.” |  |
| Event List | For purposes of the event analysis program, brief reports must be completed with 5 days. Most events listed are either OE-417 or EOP-004 reportable, those timelines and forms will be used in place of the EA brief report. Category 1 Events: - An unexpected outage, contrary to design, of three or more BES Facilities caused by a common disturbance: - The sustained outage of a combination of three or more BES Facilities - The outage of an entire generation station of three or more generators (aggregate generation of 500 MW to 1,999 MW); each combined cycle unit is counted as one generator - Intended and controlled system separation by the proper operation of a RAS - Failure or misoperation of BES RAS - System-wide voltage reduction of 3% or more that lasts more than 15 continuous minutes due to a BES emergency - Unintended BES system separation that results in an island of 100 MW to 999 MW. This excludes BES radial connections, and non-BES (distribution) level islanding - The loss of generation of 1,000 MW to 1,999 MW - Loss of monitoring or control, at a control center, such that it significantly affects the entity’s ability to make operating decisions for 30 continuous minutes or more Examples include, but are not limited to the following: - Loss of operator ability to remotely monitor or control BES elements - Loss of communications from SCADA RTU - Unavailability of ICCP links reducing BES visibility - Loss of the ability to remotely monitor and control generating units via AGC - Unacceptable state estimator or contingency analysis solutions Category 2 Events: - Complete loss of Interpersonal Communication and Alternative Interpersonal Communication capability affecting its staffed BES control center for 30 continuous minutes or more - Voltage excursions within a Transmission Operator’s footprint equal to or greater than 10% lasting more than 15 continuous minutes - Complete loss of off-site power (LOOP) to a nuclear generating station per the Nuclear Plant Interface Requirement - Unintended system separation that results in an island of 1,000 MW to 4,999 MW - Unintended loss of 300 MW or more of firm load for more than 15 minutes - IROL Violation for time greater than Tv. Category 3 Events: - Unintended loss of load or generation of 2,000 MW or more - Unintended system separation that results in an island of 5,000 MW to 10,000 MW Category 4 Events: - Unintended loss of load or generation from 5,001 MW to 9,999 MW - Unintended system separation that results in an island of more than 10,000 MW Category 5 Events: - Unintended loss of load of 10,000 MW or more - Loss of generation of 10,000 MW or more |  |
| ### NERC and DOE Reporting |  |  |
| NOTE | - Contact the Manager, System Operations and/or Designee when a NERC or DOE reporting event occurs. If available, they will be responsible to complete the required form - In the body of the e-mail, type the following: - "Contains Privileged Information and/or Critical Energy Infrastructure Information - Do Not Release.". - NERC 24-hour Emergency Hotline (404) 446-9780), |  |
| OE-417 Reporting Events | DOE OE-417 forms can be downloaded at: http://www.eia.gov/survey/form/oe_417/form.pdf. The items in bold/grey must be reported within 1 hour of the incident. The others must be reported within 6 hours. All final reports must be submitted within 72 hours. OE-417 reports are required for the following events: - Physical attack that causes major interruptions or impacts to critical infrastructure facilities or to operations - Cyber event that causes interruptions of electrical system operations - Complete operational failure or shut-down of the transmission and/or distribution electrical system - Electrical System separation (Islanding) where part or parts of a power grid remain(s) operational in an otherwise blacked out area or within the partial failure of an integrated electrical system - Uncontrolled loss of 300 MW or more of firm system loads for more than 15 minutes from a single incident - Load shedding of 100 MW or more implemented under emergency operational policy - System-wide voltage reduction of 3% or more - Public appeal to reduce the use of electricity for purpose of maintaining the continuity of the electric power system (ERCOT process each EEA) - Physical attack that could potentially impact electric power system adequacy or reliability; or vandalism which target components of any security systems - Cyber event that could potentially impact electric power system adequacy or reliability - Loss of electric service to more than 50,000 customers for 1 hour or more - Fuel supply emergencies that could impact electric power system adequacy or reliability |  |
| Event Reporting EOP-004-3 | NERC Preliminary Disturbance reports are to be completed within 24 hours of recognition of meeting an event type threshold for reporting or by the end of the next business day if the event occurs on a weekend (which is recognized to be 4 PM local time on Friday to 8 AM Monday local time). Events that are also DOE reportable, the OE-417 form should be used. For the other events, use the EOP-004 – Attachment 2 Event Reporting Form: - Damage or destruction of a Facility that results in actions to avoid a BES Emergency - Damage or destruction of a Facility that results from actual or suspected intentional human action - Physical threats to a Facility excluding weather or natural disaster related threats, which has the potential to degrade the normal operation of the Facility or suspicious device or activity at a Facility. Do not report theft unless it degrades normal operation of a Facility - Physical threats to its BES control center, excluding weather or natural disaster, which has the potential to degrade the normal operation or suspicious device or activity at its BES control center - Public appeal for load reduction event - System wide voltage reduction of 3% or more - Manual firm load shedding 100 MW or more - Automatic firm load shedding 100 MW or more (via automatic undervoltage or underfrequency load shedding schemes or RAS - Voltage deviation of 10% or more of nominal voltage sustained for 15 or more continuous minutes - Operate outside the IROL for time greater than IROL Tv (30 minutes) - Loss of firm load for 15 minutes or more: - 300 MW or more for entities with a previous year’s demand of 3,000 MW or more - 200 MW or more for all other entities - Each system separation resulting in an island 100 MW or more - Loss of generation of 1,000 MW or more - Complete loss of off-site power affecting a nuclear generating station per the Nuclear Plant Interface Requirement - Unexpected loss within its area, contrary to design, of three or more BES Elements caused by a common disturbance (excluding successful automatic reclosing - Unplanned evacuation from BES control center facility for 30 continuous minutes or more - Complete loss of voice communication capability affecting a BES control center for 30 continuous minutes or more - Complete loss of monitoring capability affecting a BES control center for 30 continuous minutes or more such that analysis capability (i.e., State Estimator or Contingency Analysis) is rendered inoperable |  |
| 1 | When required to file or forward a report, the Manager, of System Operations or the Designee will be responsible. File or forward disturbance report to entities that have not received: - NERC System Awareness (systemawareness@nerc.net) - NERC (operations@eisac.com), requirement for cyber and courtesy copy for all other reports - Fax (404) 446-9770, if internet down - Phone (404) 446-9780 - DOE when required above (doehqeoc@oem.doe.gov) - Fax (202) 586-8485, if internet down - Phone (202) 586-8100 - NERC and DOE Disturbance Reporting e-mail list |  |
| NOTE | Please be aware that for phone calls to NERC, you will be prompted by a computerized auto-attendant to press 1 for operational issues or 2 for cyber-security issues. |  |
| ### RCIS Reporting |  |  |
| EEA Postings | There are four levels of Emergency Energy Alert (EEA). As ERCOT enters each level, postings must be made on the RCIS under “Energy Emergency Alert”: - “ERCOT is declaring EEA 1” - “ERCOT is declaring EEA 2” - “ERCOT is declaring EEA 3” - “ERCOT is in EEA 0 and back to normal operations.” |  |
| ### NXT Notification Requirements |  |  |
| Beginning of each Shift |  | Log into the NXT Communicator at the beginning of each shift in order to make the required notification quickly. - If issues arise and you are unable to log into the NXT Communicator with your user name, notify the helpdesk and request immediate assistance. |
| NOTE |  | NXT notification should be coordinated with the Shift Engineer. |
| Watch |  | IF: - A Watch for Physical Responsive Capability is initiated, THEN: - Select the “SO Watch PRC below 2500” Scenario and activate notification, WHEN: - A Watch for Physical Responsive Capability has been cancelled, THEN: - Select the “SO Watch for PRC Cancelled” Scenario and activate notification. |
| EEA Implementation Levels |  | IF: - ERCOT initiates EEA Level 1, THEN: - Select the “SO EEA Level 1” Scenario and activate notification, IF: - ERCOT initiates EEA Level 2, THEN: - Select the “SO EEA Level 2” Scenario and activate notification, IF: - ERCOT initiates EEA Level 3 without Load Shed, THEN: - Select the “SO EEA Level 3, NO Load Shed” Scenario and activate notification. IF: - ERCOT initiates EEA Level 3 with Load Shed, THEN: - Select the “SO EEA Level 3, WITH Load Shed” Scenario and activate notification. |
| EEA Termination Levels |  | WHEN: - EEA Level 3 is terminated, THEN: - Select the “SO EEA Level 3 to EEA Level 2” Scenario and activate notification, WHEN: - EEA Level 2 is terminated, THEN: - Select the “SO EEA Level 2 to EEA Level 1” Scenario and activate notification, WHEN: - EEA Level 1 is terminated, THEN: - Select the “SO EEA Level 1 Cancellation” Scenario and activate notification. |
| Loss of Firm Load |  | IF: - An Operator (ERCOT or TO) has issued a request for firm load shed of ≤ 100 MW, THEN: - Notify the Manager, System Operations and/or Designee immediately. WHEN: - An Operator (ERCOT or TO) has issued a request for firm load shed of ≥ 100 MW, THEN: - Notify the Manager, System Operations and/or Designee immediately, - Select the “SO Request Firm Load Shed” Scenario and activate notification. |
| NXT Testing |  | WHEN: - Performing Shift Supervisor Procedure 9.2 Monthly Testing of Non-Routinely used Telecommunications Facilities, THEN: - Select the “SO ENS Test” Scenario and activate notification. |
| ### ERCOT Morning Report |  |  |
| NOTE | - This report is currently only required Monday – Friday. - The Morning Report form is located on the _Operations Official Spreadsheets folder |  |
| 1 | Weather Information: - The temperatures are automatically pulled from the EMS, however please verify temperatures from a National or Local Weather Service for each city listed and adjust as necessary.. - Enter the current day forecast conditions for each city listed. |  |
| 2 | Load Data: - The All-Time Peak MW and Seasonal Peak MW will be provided as needed. - Verify the Projected Peak MW and peak hour for the current day. Use the most reasonable forecast, which may not be the highest. - Verify the Previous Day Actual MW. |  |
| 3 | Interchange: - Verify the net flow across the DC-Ties for the peak hour. This can be obtained from the MOI under “DC Tie Scheduling” or from the Excel MAI. |  |
| 4 | Transmission Line Outages: - Verify the number of 345 kV line segment outages for the peak hour. |  |
| 5 | Generation MW Totals: - Verify the Generation scheduled outage MW total. - Verify the Generation forced outage MW total. |  |
| 6 | Projected MW Reserves: - Verify the Responsive Reserve requirement at the Project Peak. - Verify the anticipated operating reserves available at time of peak. - The anticipated operating reserves can be found by adding the “Max Cap. Room” and Responsive Reserve requirement. |  |
| 7 | Recent ERCOT Congestion Activity: - No action needed |  |
| 8 | Comments: - List any active OCNs, Advisories, Watches or Emergency notices. |  |
| 9 | Select: Create Report |  |
| EMAIL | The file is transferred to P:\SYSTEM OPERATIONS drive in the NERC Morning Report Folder. This report should be sent as an attachment by 0700 using the e-mail distribution list entitled “ERCOT Morning Report.” The subject line of the e-mail should read “ERCOT Morning Report for <date>” |  |
| ### RMR Unexcused Misconduct Events |  |  |
| NOTE | - For a RMR unit, a “Misconduct Event” means any hour or hours during which Participant is requested to, but does not; deliver the energy at a level of at least 98% on each hour of the level shown in the Availability Plan. - For a Synchronous Condenser Unit, a “Misconduct Event” means any hour or hours during which Participant is requested to, but does not, synchronize the Unit to the ERCOT Transmission Grid during any hour in which the Unit is shown in the Availability Plan |  |
| 1 | IF: - An RMR or Synchronous Condenser fail to deliver the energy when requested to; THEN: - Notify the Manager of System Operations and/or Designee. - The manager will gather the detailed information and send an e-mail to “Nodal Settlements and Billing” with the subject line “Action Required – RMR Unexcused Misconduct Event”. |  |
| ### Shift Schedule |  |  |
| NOTE | - Shift Schedules will be posted to the MIS under GRID on the Transmission Page in the Transmission Supporting Information section. - The posting of the schedule will be current at all time to be compliant with the Protocols. |  |
| ### GEO-Magnetic Disturbance (GMD) |  |  |
| NOTE | Solar storms or Geo magnetic disturbances (GMDs) are caused by the interaction of coronal mass ejections (solar flares) with the Earth’s Ionosphere. This interaction produces ionospheric currents in the magnitude of millions of amperes which disturb Earth’s magnetic field. This disturbance induces voltage potential at Earth’s surface which results in geomagnetically induced currents (GICs) in conducting paths such as long transmission lines, pipelines, cables etc. GICs are low frequency or quasi-DC currents which enter and exit the power system at transformer groundings and grounded transmission lines. GICs of 100’s of amperes in magnitude have been recorded. Hence the GICs have the potential to disrupt the normal operation of power system and may damage transformers. GICs may also lead to the loss of reactive power support and hence may cause voltage instabilities. |  |
| Monitor | Monitor forecasted and current space weather: - Reliability Coordinator Information System (RCIS) at https://rcis.nerc.net - NOAA’s Space Weather Prediction Center http://www.swpc.noaa.gov/ |  |
| Warning (Forecasted) | WHEN: - A forecasted GMD Warning is issued for K-7 and greater or G3 and greater; THEN: - Post message on MIS Public - Notice Type: Operational Information - Notice Priority: Low Typical MIS Posting: The Space Weather Prediction Center has issued a GMD Warning of [state level] until [date and time]. Notify Operations Support to run power flow studies to identify 345kV transformers loaded above 70% and develop a mitigation plan if needed. |  |
| Extend | IF: - The Warning is extended or K level increases/decreases; THEN: - Post new message on MIS Public and - Cancel the older message Typical MIS Posting: The Space Weather Prediction Center has extended the GMD Warning of [state level] until [date and time]. |  |
| Cancel | WHEN: - The Warning is no longer valid; THEN: - Cancel the MIS posting. |  |
| Alert (Current) | WHEN: - An Alert for a GMD is issued for K-7 and greater or G3 and greater, or the K level increases/decreases; THEN: - Instruct the Transmission & Security and Real-Time Operators to implement their GMD procedures to make additional postings and Hotline calls. |  |
| Extend | IF: - The Alert is extended or the K level is increased/decreases; THEN: - Instruct the Operators to extend the Alert and/or make notifications regarding storm severity. |  |
| Cancel | WHEN: - K levels drop below K7 or when the Warning is no longer valid; THEN: - Instruct the Operators to cancel the Advisory for the Alert. |  |
| Issues | IF: - Any TO reports an issue due to the GMD event; THEN: - Send e-mail to the following with the details - Operations Analysis - Operations Support - Shiftsupv |  |
| ### Gas Restrictions |  |  |
| 1 | Once notified by a QSE of gas restrictions - Send an e-mail to “Gas Company Notifications”. This will notify all appropriate ERCOT staff. |  |
| 2 | Determine: - If the gas restriction could impact electric power system adequacy or reliability, THEN: - Proceed to “Reports” procedure for NERC/DOE reporting requirements, AND - Consider fuel switching for the generation that has this capability This data can be viewed at ERCOT SharePoint > System Operations – Control Center > Quick Links > Fuel Oil Capability |  |
| ### Remedial Action Schemes (RAS) |  |  |
|  | IF: - A Monthly RAS report is received by e-mail; THEN: - Forward reports to: - OPS Support Engineering - Shift Supervisors |  |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Frosch, Hartmann, Stone, and Barcalow | Preparers | November 10, 2010 |
| Frosch and Hartmann | Procedure writers and editors | November 29, 2010 |
| Frosch, Hartmann, and Moore | Procedure writers and editors | January 26, 2011 |
| Frosch and Hartmann | Procedure writers and editors | March 23, 2011 |
| Frosch and Hartmann | Procedure writers and editors | April 20, 2011 |
| Frosch and Hartmann | Procedure writers and editors | June 6, 2011 |
| Frosch and Hartmann | Procedure writers and editors | July 18, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 30, 2011 |
| Frosch and Hartmann | Procedure writers and editors | September 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | October 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 16, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | April 25, 2012 |
| Frosch and Hartmann | Procedure writers and editors | May 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | May 30, 2012 |
| Frosch and Hartmann | Procedure writers and editors | July 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | August 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | October 26, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 26, 2013 |
| Frosch and Hartmann | Procedure writers and editors | May 28, 2013 |
| Frosch and Hartmann | Procedure writers and editors | July 10, 2013 |
| Frosch and Hartmann | Procedure writers and editors | August 7, 2013 |
| Frosch and Hartmann | Procedure writers and editors | August 28, 2013 |
| Frosch and Hartmann | Procedure writers and editors | December 11, 2013 |
| Frosch and Hartmann | Procedure writers and editors | January 27, 2014 |
| Frosch, Gaddy, and Hartmann | Procedure writers and editors | April 1, 2014 |
| Frosch and Hartmann | Procedure writers and editors | May 27, 2014 |
| Frosch and Hartmann | Procedure writers and editors | July 29, 2014 |
| Frosch and Hartmann | Procedure writers and editors | September 29, 2014 |
| Frosch and Hartmann | Procedure writers and editors | December 10, 2014 |
| Frosch and Hartmann | Procedure writers and editors | February 25, 2015 |
| Frosch and Hartmann | Procedure writers and editors | March 25, 2015 |
| Frosch and Hartmann | Procedure writers and editors | April 29, 2015 |
| Frosch and Hartmann | Procedure writers and editors | July 13, 2015 |
| Frosch, Hartmann and Gaddy | Procedure writers and editors | September 25, 2015 |
| Frosch, Hartmann and Gaddy | Procedure writers and editors | December 22, 2015 |
| Frosch, Hartmann and Gaddy | Procedure writers and editors | February 23, 2016 |
| Hartmann and Gaddy | Procedure writers and editors | April 22, 2016 |
| Frosch, Hartmann and Gaddy | Procedure writers and editors | June 24, 2016 |
| Frosch, Hartmann and Gaddy | Procedure writers and editors | September 26, 2016 |
| Hartmann, Gaddy and Frosch | Procedure writers and editors | December 23, 2016 |
| Hartmann, Gaddy and Frosch | Procedure writers and editors | March 27, 2017 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | May 26, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | June 23, 2017 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | September 27, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | October 27, 2017 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | December 22, 2017 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | February 22, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | March 26, 2018 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | April 27, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | May 25, 2018 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | August 28, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | September 26, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | October 29, 2018 |

Manual Change History

| Procedure | Ver/Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All Sections | 1.0 / 0 | New procedures for all sections for Nodal implementation | November 28, 2010 |
| 3.1 4.2 6.1 10.2 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Updated steps 1 and 5, deleted steps 6, 7 and 8 Updated VDI, Testing Rules and Retest Updated PUCT Daily Report step “Update Report”. Updated all steps of Texas RE Event Reporting. Updated Title (Dynamic Rating, SCED Status, EMBP, SE, RTCA or RLC Alarms), 1st Note and Monitor | December 1, 2010 |
| 3.2 3.3 3.7 4.2 6.1 10.2 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 2 1.0 / 2 - / 2 | Updated step 1,3 and added step 4 in “Capacity Monitoring” Updated step 4 Updated step No SCED Solution Updated VDI, Retest, and Notify, added Completion Updated step OE-417 Reporting Events in NERC, DOE Reporting and step 2 on GEO-Magnetic Disturbance (GMD) Updated step Monitor on “Dynamic Rating, SCED Status, EMBP, SE, RTCA or RLC Alarms” | January 31, 2011 |
| 3.2 5.3 5.5 6.1 7.2 7.3 9.2 | 1.0 / 2 1.0 / 1 1.0 / 1 1.0 / 3 1.0 / 1 1.0 / 1 1.0 / 1 | Updated step 3 “Capacity Monitoring” Updated step 1 & 3 Updated 1st note & step 2 Updated PUCT Daily Report, Texas RE Event Reporting & NXT Notification Updated EEA Checklist Updated EEA Restoration Checklist Added new steps “SAT modem testing” & updated NXT Tests | March 25, 2011 |
| 4.2 5.1 7.1 7.3 | 1.0 / 3 1.0 / 1 1.0 / 1 1.0 / 1 | Updated “Unannounced Resource Testing” 1st note Updated 2nd & 6th paragraphs Updated “System Disturbance” NERC, step 2 and “Degraded Weather” step 3 Updated Table | April 22, 2011 |
| 5.3 5.7 6.1 7.1 7.4 7.5 7.6 8.3 | 1.0 / 2 1.0 / 1 1.0 / 4 1.0 / 2 1.0 / 1 1.0 / 0 1.0 / 1 1.0 / 1 | Updated step 2 Updated all steps Updated all steps in Texas RE Event Reporting and NERC and DOE Reporting Updated steps in Degraded Weather Updated all steps Added new procedure Updated all steps Updated step 2 and deleted step 3 | June 8, 2011 |
| 3.6 4.1 4.2 6.1 7.2 7.3 9.2 | 1.0 / 1 1.0 / 1 1.0 / 4 1.0 / 5 1.0 / 1 1.0 / 1 1.0 / 2 | Updated step 3 Removed Initial Synchronization of New Resource Updated Testing Rules Updated step Event List Updated EEA Implementation Checklist Updated EEA Restoration Checklist Added Notice Builder test in Primary Control Center section | July 20, 2011 |
| 4.2 5.5 6.1 7.2 7.3 7.7 9.2 10.1 | 1.0 / 5 1.0 / 2 1.0 / 6 1.0 / 2 1.0 / 3 1.0 / 0 1.0 / 3 1.0 / 1 | Updated step Caution Updated 1st Note Updated step 1 in Texas RE Event Reporting and NXT Testing in NXT Notification Requirements Updated EEA Implementation checklist Updated EEA Restoration checklist Added Extreme Hot Weather Updated NXT Test in Alternate Control Center Updated step 3 | September 1, 2011 |
| 3.4 6.1 7.2 7.3 9.2 | 1.0 / 1 1.0 / 7 1.0 / 2 1.0 / 3 1.0 / 4 | Grammar changes Combined EEA 2A & B per NPRR 379 Updated to implement NPRR 379 Updated to implement NPRR 379 Updated Phone Test in Alternate Control Center | October 1, 2011 |
| 3.7 7.2 10.2 | 1.0 / 2 1.0 / 3 1.0 / 3 | Changed title & all steps Updated EEA checklist Updated 1st Note | November 1, 2011 |
| 3.3 6.2 6.3 | 1.0 / 2 1.0 / 1 1.0 / 1 | Updated all steps Updated step 2 Updated step 1 & 2 All procedures in this manual have been reviewed. | December 15, 2011 |
| 1.2 4.2 5.7 | - / 1 - / 6 - / 2 | Updated Scope Updated all steps of procedure Updated Market Participant Backup Control Center Transfer | January 19, 2012 |
| 2.1 3.3 3.4 3.7 3.8 4.1 4.2 5.3 5.6 5.8 6.1 7.1 9.1 9.2 10.2 | 1.0 / 1 1.0 / 3 1.0 / 2 1.0 / 3 1.0 / 1 1.0 / 2 1.0 / 7 1.0 / 3 1.0 / 1 1.0 / 1 1.0 / 8 1.0 / 3 1.0 / 1 1.0 / 5 1.0 / 4 | Updated paragraph 4 Updated Step 3 Updated Threat & Emergency Classifications & Desktop Guide reference Changed Shift Engineer to Operations Support Corrected grammar on step 1 Changed Shift Engineer to Operations Support Updated procedure Changed Shift Engineer to Operations Support Corrected grammar on step 2 Updated step 2 Updated Texas RE Event Reporting, OE-417 reporting & Desktop Guide reference Updated Desktop Guide reference Updated Desktop Guide reference Updated Desktop Guide reference Changed Shift Engineer to Operations Support and updated Desktop Guide reference | March 1, 2012 |
| 2.1 3.3 3.6 5.6 6.1 7.1 7.4 7.5 7.6 | 1.0 / 2 1.0 / 4 1.0 / 2 1.0 / 2 1.0 / 9 1.0 / 4 1.0 / 2 1.0 / 2 1.0 / 2 | Changed TSP/DSP to TO Updated 3rd Note Updated purpose Changed TSP to TO and Transmission Facility Updated step Update Report & changed ARR to PRC and ERCOT Morning Report Updated step NERC and Degraded Weather Updated OCN, Advisory, & Watch steps Deleted Cold Weather, not Extreme Cold Weather Section number changed, Added OCN, Advisory and Emergency Notice | May 1, 2012 |
| 3.2 | 1.0 / 3 | Updated to reflect changes in the TAC approved Non-Spin document | May 14, 2012 |
| 7.2 7.3 | 1.0 / 3 1.0 / 4 | Updated EILS to ERS per NPRR 451 & added TO load management program Updated EILS to ERS per NPRR 451 & added TO load management program | June 1, 2012 |
| 3.3 4.2 6.1 | 1.0 / 5 1.0 / 8 1.0 / 10 | Updated step 3 Added Desktop Guide to VDI reference Updated PUCT Daily Report, NERC and DOE Reporting and RCIS Posting | July 16, 2012 |
| 3.4 4.2 5.9 6.1 7.2 | 1.0 / 3 1.0 / 9 1.0 / 1 1.0 / 11 1.0 / 4 | Added CPT to procedure and Typical Subject line for e-mail Added Log to procedure Deleted Procedure Updated NERC and DOE Reporting Added 30 MIN ERS deployed to EEA 1 | August 29, 2012 |
| 2.2 3.1 5.3 6.1 7.6 9.1 | 1.0 / 1 1.0 / 2 1.0 / 4 1.0 / 12 1.0 / 3 1.0 / 2 | Added Hotline Call Communication Updated step 5 Updated and added Planned and Forced Outage sections. Added Weather Information section to PUCT Daily Report. Updated step 1 in NERC and DOE Reporting and ERCOT Morning Report section. Updated OCN, Advisory, & Watch Updated step E-mail All procedures in this manual have been reviewed. | November 1, 2012 |
| 3.2 3.3 3.4 3.5 3.6 3.7 3.8 4.1 5.2 5.3 5.5 5.6 5.8 6.1 6.2 6.3 7.4 7.5 7.6 8.3 8.6 9.2 10.1 10.2 11.0 | 1.0 / 4 1.0 / 6 1.0 / 4 1.0 / 1 1.0 / 3 1.0 / 4 1.0 / 2 1.0 / 3 1.0 / 1 1.0 / 5 1.0 / 3 1.0 / 3 1.0 / 2 1.0 / 13 1.0 / 2 1.0 / 2 1.0 / 3 1.0 / 3 1.0 / 4 1.0 / 2 1.0 / 1 1.0 / 6 1.0 / 2 1.0 / 5 1.0 / 1 | Updated step 1, Capacity Monitoring and deleted Reserve Monitoring Updated step 3 Updated notes and Management Notifications Updated purpose and step 1 Updated step 2 Updated step TCM & renamed LMP Map Delete procedure for large wind ramp events Updated step 1 Grammatical correction Updated step 3 Protective Relay or Equipment Failure Added MISO Reliability Coordinator Updated step 2 TO Temporary Equipment Limitation Notifications Updated purpose Updated step 1 Texas RE Event Reporting, Note and step 1 NERC and DOE Reporting, Loss of Firm Load NXT Notification Requirements, step 1 Weather Information section to ERCOT Morning Report, step 1 RMR Unexcused Misconduct Events, GMD, step 2 Gas Restrictions and added Special Protection Systems (SPSs) Deleted procedure Renamed to 6.2 and updated procedure Updated step Reporting Updated step Reporting Updated Log Updated step 2 Updated procedure Deleted Notice Builder Updated step 3 Updated step monitor, step 4 Building Security and Fire Alarms and step 3 Failure of the Emergency Generator Updated procedure Review New Communications from Manager and/or Control Room Operations Manager and step 4 Implement ERCOT Personnel and Company Standards | March 1, 2013 |
| 3.3 3.4 6.1 | 1.0 / 7 1.0 / 5 1.0 / 14 | Updated all steps Added 1st Note, deleted 2nd & 3rd Notes, Management Notification, updated QSE Notification, TO Notification Updated step Update Report | June 1, 2013 |
| 4.1 5.1 6.1 10.2 | 1.0 / 4 1.0 / 2 1.0 / 15 1.0 / 6 | Updated Ancillary Service Testing Coordination and added Coordinated Reactive Tests Added MISO Updated PUCT Daily Report & step 1 on NERC and DOE Reporting and added Note to NXT Notification Requirements Updated 1st Note and step #3 on Building Security and Fire Alarms | July 15, 2013 |
| 3.4 4.1 6.1 7.3 | 1.0 / 6 1.0 / 5 1.0 / 16 1.0 / 5 | Updated QSE Notification, TO Notification & Send E-mail Updated Coordinated Reactive Tests Added 7-Day Outlook, updated Event List on Texas RE Event Reporting & step 2 on GEO-Magnetic Disturbance (GMD) Updated table | August 9, 2013 |
| 3.3 | 1.0 / 8 | Removed HHGT TO reference | August 30, 2013 |
| 3.3 3.4 4.1 4.2 5.3 5.4 5.6 5.7 6.1 7.6 8.1 8.2 8.3 9.1 9.2 10.2 | 1.0 / 9 1.0 / 7 1.0 / 6 1.0 / 10 1.0 / 6 1.0 / 1 1.0 / 4 1.0 / 3 1.0 / 17 1.0 / 5 1.0 / 1 1.0 / 1 1.0 / 3 1.0 / 3 1.0 / 7 1.0 / 7 | Updated step 1 and Log Updated step Log Updated step Log Updated step Log Updated step 4, Planned Outage, Forced Outage and added Log Updated step Log Updated step Log Updated step 1 and added Log Updated step Update Report, TRE Event Reporting changed to Event Analysis Report and event list updated, and NERC and DOE Reporting updated Added step Issues and updated Log Updated step 3 and added Log Updated step 3, 5 and added Log Updated step 3 Updated step Log Updated steps Log Added step 4 and updated Log All procedures in this manual have been reviewed. | December 13, 2013 |
| 4.1 6.1 7.2 7.3 | 1.0 / 7 1.0 / 18 1.0 / 5 1.0 / 6 | Updated for NOGRR125 & OK to test on Coordinated Reactive Tests Updated NERC and DOE Reporting Updated EEA Implementation Checklist Updated EEA Restoration Checklist | January 29, 2014 |
| 3.2 4.2 5.5 6.1 6.2 | 1.0 / 5 1.0 / 11 1.0 / 4 1.0 / 19 1.0 / 3 | Updated VDI information Updated VDI information Updated Note Updated Update Report on PUCT Daily Report and step 1 on NERC and DOE Reporting Updated step 1 | April 4, 2014 |
| 2.2 7.1 | 1.0 / 2 1.0 / 5 | Added VDIs to Master QSEs Updated step 1 | June 1, 2014 |
| 4.2 6.1 6.2 7.2 | 1.0 / 12 1.0 / 20 1.0 / 4 1.0 / 6 | Updated 1st Note, Retest and added Demonstration Test Updated step Update Report Updated steps 1 & 4 Updated checklist | August 1, 2014 |
| 3.3 3.4 4.1 4.2 9.2 | 1.0 / 10 1.0 / 8 1.0 / 8 1.0 / 13 1.0 / 8 | Added step 2 Corrected spelling on Send E-mail Updated script for Unit Testing Added new reference Updated new section on Phone Tests | October 1, 2014 |
| 3.6 3.7 4.2 6.1 | 1.0 / 4 1.0 / 5 1.0 / 14 1.0 / 21 | Changed title and removed references to W-N Added step RTMONI Updated Testing Rules and Scripts Added 2nd note to NERC and DOE Reporting & updated GMD procedure All procedures in this manual have been reviewed | December 15, 2014 |
| 2.2 3.2 3.3 4.2 5.3 5.5 6.1 7.2 7.5 | 1.0 / 3 1.0 / 6 1.0 / 11 1.0 / 14 1.0 / 7 1.0 / 5 1.0 / 22 1.0 / 7 1.0 / 4 | Added Dispatch and VDI definitions Updated step 4 Updated step 1 in Suspected Sabotage or Sabotage Events Moved procedure to Resource desk Updated title and added Protection System Setting Notifications Added Switchable Generation Resource Added Unit Trip Posting Updated checklist Updated Note | March 1, 2015 |
| 5.3 6.1 | 1.0 / 8 1.0 / 23 | Clarification to step 2 Clarifications to GMD procedure | March 30, 2015 |
| 3.3 3.4 3.6 3.7 4.1 5.6 6.1 6.2 7.6 8.3 8.6 10.1 10.2 11 | 1.0 / 12 1.0 / 9 1.0 / 5 1.0 / 6 1.0 / 9 1.0 / 5 1.0 / 24 1.0 / 5 1.0 / 6 1.0 / 4 1.0 / 2 1.0 / 3 1.0 / 8 1.0 / 2 | Updated contact information Updated contact information Updated contact information Updated contact information Updated contact information Updated contact information Updated contact information Updated contact information Updated contact information Updated contact information Updated contact information Updated contact information Updated contact information Updated contact information | May 1, 2015 |
| 6.1 10.2 | 1.0 / 25 1.0 / 9 | Updated GMD procedure Added new Telemetering, Control Equipment and Communication Outages process | July 15, 2015 |
| 9.1 9.2 9.3 9.4 | 1.0 / 0 1.0 / 0 1.0 / 9 1.0 / 4 | New procedure for COM-001-2 New procedure for COM-001-2 Updated procedure for COM-001-2 Updated section number | October 1, 2015 |
| 6.1 7.2 9.3 | 1.0 / 26 1.0 / 8 1.0 / 10 | Updated Event Analysis Reporting step Event List Implement NPRR708 for EEA Added Primary Control Center step Replacement/Alternative Device Examples Added Alternate Control System step Replacement/Alternative Device Examples All procedures in this manual have been reviewed | December 31, 2015 |
| 2.1 6.1 | 1.0 / 3 1.0 / 27 | Updated System Operator Responsibility and Authority Updated Guidelines for Determining EEA Potential | March 1, 2016 |
| 5.3 10.2 | 1.0 / 9 1.0 / 10 | Updated Protective Relay or Equipment Failure step 2 Deleted step 2 and updated step 3 | April 29, 2016 |
| 2.1 2.2 3.2 4.1 5.37.2 7.3 8.2 8.6 10.2 | 1.0 / 4 1.0 / 4 1.0 / 7 1.0 / 10 1.0 / 10 1.0 / 9 1.0 / 7 1.0 / 2 1.0 / 3 1.0 / 11 | Updated steps for COM-002-4 Updated steps for COM-002-4 Updated steps for COM-002-4 Updated steps for COM-002-4 Updated Protection System Setting Notification Updated steps for COM-002-4 Updated steps for COM-002-4 Updated steps for COM-002-4 Updated steps for COM-002-4 Updated steps for COM-002-4 | June 30, 2016 |
| 3.3 6.1 7.2 10.1 | 1.0 / 13 1.0 / 28 1.0 / 9 1.0 / 4 | Updated step Updated Step 1 of NERC and DOE Reporting Updated checklist Updated step 2 | September 30, 2016 |
| 3.3 4.1 5.5 6.1 | 1.0 / 14 1.0 / 11 1.0 / 6 1.0 / 29 | Updated Note Added Unit Testing Note Updated Approved Resources to be ONTEST Step Approval Deleted Turbine Governor Updated Note, renamed SPS to RAS & updated RAS Updated Event Analysis Reporting Step Event List, Event Reporting EOP-004-2 & Step 1 Renamed Special Protection Systems (SPS) to Remedial Action Schemes (RAS) & updated Remedial Action Schemes (RAS) All procedures in this manual have been reviewed | December 30, 2016 |
| 2.1 3.4 4.1 5.1 5.3 5.4 5.5 5.6 5.7 5.9 6.1 7.2 7.6 9.1 9.2 9.3 10.2 | 1.0 / 5 1.0 / 10 1.0 / 12 1.0 / 3 1.0 / 11 1.0 / 2 1.0 / 7 1.0 / 6 1.0 / 4 1.0 / 0 1.0 / 30 1.0 / 10 1.0 / 7 1.0 / 1 1.0 / 1 1.0 / 11 1.0 / 12 | Updated for IRO-001-4 Updated Threat & Emergency Classifications step Updated In Service Approval step 1 Deleted paragraph to create new procedure in 5.9 Updated CFE to CENACE Updated Protective Relay Outages step Updated second note, step 5 & 6 Updated CFE to CENACE Updated TO Temporary Equipment Limitation Notifications step 2 Updated Heading title and step 1 New procedure for IRO-002-4 R2 Updated with Event Analysis v3.1 changes and EOP-004-3 and EOP-011 Updated checklist Updated title Updated step 1 Updated step 2 Updated Satellite Modem Updated TOs, QSEs along with Telemetering, Control Equipment and Communication Outages | March 31, 2017 |
| 1.1 3.2 5.3 7.2 9.1 | 1.0 / 1 1.0 / 8 1.0 / 12 1.0 / 11 1.0 / 2 | Updated Purpose to add Reliability Risk desk Updated Capacity Monitoring step 3 & 4 Updated step 3 and Protective Relay Outages Updated EEA 3 checklist Updated Interpersonal Communication | June 1, 2017 |
| 7.2 | 1.0 / 12 | Updated checklist | June 30, 2017 |
| 9.1 | 1.0 / 3 | Updated steps & deleted Note | September 29, 2017 |
| 9.3 | 1.0 / 12 | Updated 1st Weekend of Every Month | October 31, 2017 |
| 6.1 7.1 8.6 | 1.0 / 31 1.0 / 6 1.0 / 4 | All procedures in this manual have been reviewed Updated PUCT Daily Report step Update Report Updated System Disturbance step NERC Updated Root Cause Analysis step NOTE | December 28, 2017 |
| 6.1 7.2 9.3 10.2 | 1.0 / 32 1.0 / 13 1.0 / 13 1.0 / 13 | Updated NERC and DOE Reporting OE-417 Reporting Events Updated Checklist Added Form an Email steps Updated step 1 & 2 | February 28, 2018 |
| 6.1 10.2 | 1.0 / 33 1.0 / 14 | Updated NERC and DOE Reporting step OE-417 Reporting Events Updated Title & EMS Alarm Heartbeat, Dynamic Rating, SCED Status, EMBP, SE, RTCA or RLC Alarms steps note and Monitor | March 30, 2018 |
| 2.2 7.2 7.3 | 1.0 / 5 1.0 / 14 1.0 / 8 | Updated procedure purpose Updated Checklist Updated Checklist | May 1, 2018 |
| 5.5 | 1.0 / 8 | Update EEA and Switchable Generation Resource | May 31, 2018 |
| 3.2 6.1 7.2 9.3 9.4 | 1.0 / 9 1.0 / 34 1.0 / 15 1.0 / 14 1.0 / 5 | Added step 2 & Log, updated step 3 and renumbered 2, 3 &4 Deleted 7-Day Outlook Report Updated Checklist Multiple changes to clarify the roles and responsibilities Updated forms | August 31, 2018 |
| 5.5 6.1 | 1.0 / 9 1.0 / 35 | Removed Monticello RAS Removed Reportable Balancing Contingency Event from the PUCT Daily Report update and updated step 1 on the ERCOT Morning Report | October 1, 2018 |
| 6.1 | 1.0 / 36 | Updated PUCT Daily Report | November 1, 2018 |