## Power Operations Bulletin # 875

ERCOT has posted/revised the Resource Desk manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

## http://www.ercot.com/mktrules/guides/procedures/index.html

## 7.3	Restore EEA Levels

Procedure Purpose:  To restore the ERCOT grid to normal state as system conditions warrant while recovering from an EEA event.

| Protocol Reference | 6.5.9.4.3 |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.5.3.5 |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 14 | Effective Date: December 28, 2018 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| RESERVES | 1375 MW of PRC must be restored within 90 minutes. |
| Restore Firm Load |
| 1 | IF: Sufficient Regulation Service exist to control to 60 Hz, AND PRC – Regulation Up Responsibility ≥ 1375 MW for the last 15 minutes; THEN: Transmission Operator will restore firm load. |
| Move from EEA Level 3 to EEA Level 2 |
| 1 | IF: Sufficient Regulation Service exist to control to 60 Hz, AND PRC is ≥ 1750 MW, AND All firm load have been instructed to be restored; THEN: When instructed by the Real-Time Operator to recall Load Resources Send XML message to recall Load Resources, (see Desktop Guide Resource Desk Section 2.2.4) Make EEA 3 to EEA 2 posting to MIS Public Use preformatted notice |
| Move from EEA Level 2 to EEA Level 1 |
| 1 | IF: The system can maintain PRC ≥ 2300 MW, AND All Load Resources have been instructed to be restored; THEN: Send XML message to recall 30 MIN then 10 MIN ERS (see Desktop Guide Resource Desk Section 2.3.3) Make EEA 2 to EEA 1 posting to MIS Public Use preformatted notice |
| Move from EEA Level 1 to EEA 0 |
| 1 | IF: The system can maintain PRC ≥ 2300 MW, AND All uncommitted units secured in EEA 1 can be released, AND Emergency energy from the DC Ties is no longer needed; THEN: Terminate EEA 1 by posting to MIS Public Use preformatted notice “EEA 1 to Normal” |
| Recall Non-Spin and Cancel Watch |
| 1 | WHEN: Avail_CAP_30Min ≥ 1000, AND PRC is ≥ 2800 MW; THEN: Coordinate with the Real Time Operator and recall half of the Non-Spin by sending a Zero MW XML message (Refer to Desktop Guide Resource Desk Section 2.1.3). WHEN: Avail_CAP_30Min ≥ 1000, AND PRC is ≥ 3000 MW; THEN: Coordinate with the Real Time Operator and recall all of the Non-Spin by sending a Zero MW XML message (Refer to Desktop Guide Resource Desk Section 2.1.1). |
| Log | Log all actions. |