- Power Operations Bulletin # 902

ERCOT has posted/revised the DC Tie manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

- http://www.ercot.com/mktrules/guides/procedures/index.html

## 4.1	Implement EEA Levels

Procedure Purpose: Steps to perform when ERCOT declares Energy Emergency Alert (EEA).

| Protocol Reference | 4.4.4 | 6.5.9.4.2 | 6.5.9.4.3 |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 2.1(3)(f) | 4.5.3(2) | 4.5.3.3 |  |
| NERC Standard | EOP-011-1 R2, R2.1, R2.2, R2.2.2, R2.2.3, R2.2.3.1, R2.2.7 | INT-006-4 R1, R2, R3 | INT-010-2.1 R2, R3 | IRO-001-4 R1 |
|  | TOP-001-4 R2 |  |  |  |

| Version: 1 | Revision: 28 | Effective Date: August 1, 2019 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Turret Phone | - The DC Tie Operator for the Laredo and Eagle Pass DC Ties can be reached using the Turret phone button labeled (AEP TO), page 4 - The DC Tie Operator for the Railroad DC Tie can be reached using the Turret phone button labeled (ONCOR DC TIE), page 14 - AEP un-regulated QSE is responsible for assets associated with unregulated retail operations (SQ2, SQ3, and SQ4 sub-QSEs). The electronic Dispatch Instruction for emergency energy to and from CENACE will be given to this QSE. They can be reached using the Turret phone button labeled (AEP UNREG QSE), page 4 |
| EEA | When notified by Hotline that ERCOT has implemented EEA 1, proceed with this procedure. See Desktop Guide DC Tie Desk Section 2.8 for flow diagram. |
| ### DC-Ties with Centro Nacional de Control de Energia (CENACE) |  |
| 1 | This applies to the Laredo and Eagle Pass DC Ties: IF: - There are export schedules, OR - Export inadvertent payback flowing; THEN: - Stop the export inadvertent payback - Curtail the export schedules (see Desktop Guide DC Tie Desk Section 2.3 or 2.4) - Anytime an approved E-Tag is curtailed or adjusted by ERCOT a DC Tie Curtailment Notice (DCTCN) must be posted on the MIS Secure area. - Use the canned message CONTACT: - The DC-Tie Operator (AEP TO) Typical script (use what is applicable): This is ERCOT operator [first and last name]. Due to ERCOTs EEA status: - We have curtailed E-Tag(s) [tag number(s)] on the [DC Tie name] and request ramping the Tie(s) accordingly - We request the inadvertent payback on [DC-Tie] be ramped to zero - We request you inquire about the availability of emergency energy from CENACE. Please repeat this back to me. That is correct. Thank you.” |
| 2 | This applies to the Railroad DC-Tie: IF: - There are export schedules, OR - Export inadvertent payback flowing; THEN: - Stop the export inadvertent payback - Curtail the export schedules (see Desktop Guide DC Tie Desk Section 2.3 or 2.4) - Anytime an approved E-Tag is curtailed or adjusted by ERCOT a DC Tie Curtailment Notice (DCTCN) must be posted on the MIS Secure area. - Use the canned message CONTACT: - The DC-Tie Operator (ONCOR DC TIE) Typical script (use what is applicable): This is ERCOT Operator [first and last name]. Due to ERCOTs EEA status: - We have curtailed E-Tag(s) [tag number(s)] and request ramping the Tie accordingly - We request the inadvertent payback be ramped to zero - We request you inquire about the availability of emergency energy from CENACE. Please repeat this back to me. That is correct. Thank you.” |
| Electronic Dispatch Instruction | IF: - AEP TO and/or ONCOR DC Tie notifies ERCOT of available emergency energy; THEN: - Accept all available emergency energy - Notify the Shift Supervisor - Issue the electronic Dispatch Instruction as time permits Verbal Dispatch Instructions [Emergency] MOI display AEP un-regulated QSE (AEP UNREG QSE): - Choose DC Tie tab - Choose QAEPS2 for Participant Name - Choose DC Tie Name - Enter Up-To MW value - Choose PROVIDE EMERGENCY POWER FROM DC TIE – Import for Instruction Type - State “Emergency Energy to ERCOT on [DC Tie(s)] in Other InformationCompletion Time can be left blank, if unknown and inserted when completion time is known.(back office will take care of the rest) - Click “Send” (do not “Commit to Database”) Notify AEP un-regulated QSE (AEP UNREG QSE) that the electronic Dispatch Instruction has been issued. When issuing a VDI or confirmation, ensure the use of three-part communication. |
| 3 | This applies to the Laredo and Eagle Pass DC Ties: WHEN: - EEA has ended; THEN: - Notify the DC-Tie Operator (AEP TO) Typical script (use what is applicable): “This is ERCOT Operator [first and last name]. At [time], ERCOT has ended EEA 1. Thank you.” CONTACT: - The DC-Tie Operator (AEP TO) for the following as appropriate: - End emergency energy - Verify Completion Time from the Verbal Dispatch Instructions [Emergency] MOI display has a Completion Time entered for the appropriate DC Tie. - Reload any E-Tag (see Desktop Guide DC Tie Section 2.5) - Cancel DCTCN MIS Posting message - Re-start inadvertent payback |
| 4 | This applies to the Railroad DC-Tie: WHEN: - EEA has ended; THEN: - Notify the DC-Tie Operator (ONCOR DC TIE) Typical script (use what is applicable): “This is ERCOT Operator [first and last name]. At [time], ERCOT has ended EEA 1. Thank you.” CONTACT: - The DC-Tie Operator (ONCOR DC TIE) for the following as appropriate: - End emergency energy - Verify Completion Time from the Verbal Dispatch Instructions [Emergency] MOI display has a Completion Time entered for the DC-R Tie. - Reload any E-Tag (see Desktop Guide DC Tie Section 2.5) - Cancel DCTCN MIS Posting message - Re-start inadvertent payback |
| LOG | Log all actions taken. |
| ### DC-Ties with Southwest Power Pool (SPP) |  |
| Turret Phone | - SPP Reliability Coordinator can be reached using the Turret phone button labeled (SPP RC), page 2 - AEP regulated QSE is responsible for assets associated with regulated retail operations (Main and SQ1sub-QSE). The electronic Dispatch Instruction for emergency energy from SPP will be given to this QSE. They can be reached using the Turret phone button labeled (AEP REG QSE), page 4 |
| NOTE | For any EEA level, only hourly non-firm transmission service is available for the North and East DC Ties. Keep AEP informed so they can make the proper submittals hour to hour. |
| NOTE | If an e-Tag cannot be timely submitted during an Emergency Condition, and energy is available. The DC Tie Operator may start the flow after approval from the RC’s. An e-Tag must be submitted after the schedule has physically started for tag approval. |
| 1 | NOTIFY: - SPP Reliability Coordinator (SPP RC) of ERCOT’s EEA 1 status: Typical Script to SPP Reliability Coordinator (SPP RC): “This is ERCOT Operator [first and last name]. At [time], ERCOT declared EEA 1”. |
| 2 | IF: - There are export E-tags across the DC Ties (does not apply to DC_N schedules which are identified by “OKLA” in the Physical Path on the tag), OR - Export inadvertent payback flowing, OR - DC_N deadband is active and exporting; CONTACT: - The SPP Tariff Operator (SPP Tariff) Typical script (use what is applicable): This is ERCOT Operator [first and last name]. ERCOT is in EEA [level]: - We are curtailing E-Tag(s) [tag number(s)] and request that you ramp the Tie accordingly - We request the inadvertent payback be ramped to zero - If applicable, request the deadband on the North Tie be turned into ERCOT. Please repeat this back to me. That is correct. Thank you.” IF: - SPP provides a reliability reason for NOT approving the curtailing of the E-Tag(s); THEN: - Do not proceed with curtailments - Notify the Shift Supervisor - Make a log entry IF: - SPP approves; THEN: - Curtail the export schedules (usually done one hour at a time) (see Desktop Guide DC Tie Desk Section 2.3 or 2.4) - During an emergency condition if an approved E-Tag is curtailed or adjusted by ERCOT a DC Tie Curtailment Notice (DCTCN) must be posted on the MIS Secure area. - Use the canned message |
| 3 | IF: - The SPP DC Ties are not at maximum import into ERCOT; THEN: - Notify the AEP regulated QSE (AEP REG QSE) to request emergency energy. Typical Script to AEP (AEP REG QSE): “This is ERCOT Operator [first and last name]. At [time], ERCOT declared EEA [state level]. Can AEP assist ERCOT with transmission service and energy on either available DC Tie?” NOTE: AEP will have to request the transmission service and energy first before they will know if it is available. SPP will approve if both services are available. IF: - Not approved; THEN: - Do NOT proceed and make log entry - Notify Shift Supervisor |
| Electronic Dispatch Instruction | IF: - AEP notifies ERCOT of available emergency energy THEN: - Accept all available emergency energy - Notify the Shift Supervisor - Approve the E-Tag - Issue electronic Dispatch Instruction as time permits Verbal Dispatch Instructions [Emergency] MOI display AEP REG QSE: - Choose DC Tie tab - Choose QAEPSC for Participant Name - Choose DC Tie Name - Enter Up-To MW value - Choose PROVIDE EMERGENCY POWER FROM DC TIE - Import for Instruction Type - State “Emergency into ERCOT” and which DC Tie(s) in Other Information - Completion Time can be left blank, if unknown and inserted when completion time is known (back office will take care of the rest) - Click “Send” (do not “Commit to Database”) Notify AEP regulated QSE (AEP REG QSE) that the electronic Dispatch Instruction has been issued. When issuing a VDI or confirmation, ensure the use of three-part communication. |
| 4 | WHEN: - EEA status changes; THEN: - Notify SPP Reliability Coordinator (SPP RC) Typical Script to SPP Reliability Coordinator (SPP RC): “This is ERCOT Operator [first and last name]. At [time], ERCOT moved from EEA 1 to EEA 2. Thank you”. If moved to EEA 2 or 3 continue process above but with new levels. |
| 5 | WHEN: - EEA has ended; THEN: - Notify SPP Reliability Coordinator (SPP RC) Typical Script to SPP Reliability Coordinator (SPP RC): “This is ERCOT Operator [first and last name]. At [time], ERCOT has ended EEA 1. Thank you.” CONTACT: - The SPP Tariff Operator (SPP Tariff) for the following as appropriate: - End emergency energy - Verify Completion Time from the Verbal Dispatch Instructions [Emergency] MOI display has a Completion Time entered for the appropriate DC Tie - Reload any E-Tag (see Desktop Guide DC Tie Section 2.5) - Cancel DCTCN MIS Posting message - Re-start inadvertent payback - If applicable, have deadband turned back into SPP |
| LOG | Log all actions taken. |

## 4.4	Loss of Primary Control Center Functionality

Procedure Purpose: Provide instructions for responding to conditions that cause the primary control center to become inoperable or uninhabitable and ensuring the safety of control room personnel.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | EOP-008-2 R1, R1.4 R1.6, R1.6.1, R1.6.2, 1.6.3, R4 |  |  |  |

| Version: 1 | Revision: 24 | Effective Date: August 01, 2019 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Contact Security | IF: - Unable to reach any Operator at the PCC (also trying Alternative Interpersonal Communication capability); THEN: - Check the Control Center video camera to determine the status of the PCC and personnel, - Contact Security at the ACC - Notify them of the situation AND - Have them attempt to make contact with Security at PCC. - Have them contact you with information acquired OR IF: - Notified by the PCC that they are evacuating and/or transferring sites OR - Control Center video and Security confirms evacuation; THEN: - Continue with procedure. |
| IROL | The North – Houston VSAT voltage stability limit is an IROL; the actual flow should not be allowed to exceed the limit, and MUST NOT exceed the limit for more than 30 minutes. If necessary, the System Operator has the authority to direct load shedding before this IROL has been exceeded. |
| 3-Part | When issuing an Operating Instruction, follow three-part communication: - Issue the Operating Instruction - Receive a correct repeat back - Give an acknowledgement |
| ### Systems are Functional |  |
| Call in Additional Operators | Activate the NXT scenario to call in additional shift personnel, which includes a Shift Supervisor. SELECT: - SO Loss of Control Room at Taylor, OR; - SO Loss of Control Room at Bastrop. - Operator will receive an email after 10 minutes with a report of who has responded along with their estimated time of arrival. |
| QSE Hotline Call | - Q#106 - Typical Hotline Script Emergency Notice Loss of Primary Control Center (Systems are Functional) |
| TO Hotline Call | - T#91 - Typical Hotline Script Emergency Notice Loss of Primary Control Center (Systems are Functional) |
| Additional Notifications | - The Manager of System Operations and/or Control Room Operations Manager will notify the following: - Help Desk (to notify EMMS Support and Telecommunications) - Engineering Support - These phone numbers are also programmed into the control room cell phone. |
| MIS Posting | - As time permits, post the Emergency Notice in the Public MIS. - Typical Posting Script: - ERCOT has issued an Emergency Notice for the loss of the primary control center. |
| Monitor Critical Facilities | Critical facilities are the ERCOT defined contingencies that show up after running Real Time Contingency Analysis (RTCA) as a post-contingency overload. This list is located in the EMS and an electronic copy is located on the MIS Secure site: Select: Grid>Generation>Reliability Unit Commitment>Standard Contingency List’ - Select “Standard Contingency List” Open the zip file>Open the CIM file>Select the Standard_Contingency_List tab and view the contingencies. - A potential critical facility becomes a critical facility when the contingency appears in RTCA/TCM as a post-contingency overload. |
| Respond to QSEs | Monitor frequency and re-run SCED/use (manual offset) as needed. IF: - QSEs call in with questions about operational timelines or non real-time issues; THEN: - Notify the QSE that timelines and non real-time issues will be addressed when additional staff arrive, - Document QSE calls to pass along to the appropriate Operators as they arrive. |
| Respond to TOs Thermal/ Voltage Limits Reached (SOL) | IF: - Thermal limits have reached their continuous rating; THEN: - Activate associated constraint, OR - Seek a recommendation from the corresponding TO as to what actions will alleviate the situation, - Issue unit specific Operating Instructions as necessary to QSE. (Follow-up with electronic Dispatch Instruction confirmation as time permits), - Continue to monitor to determine the effect of the plan. ERCOT Nominal Voltage Levels are 345kV, 138kV, and 69kV. The general voltage guidelines are as follows (listed in kV): Nominal Voltage; Operating Limits; Ideal Voltage Range. 345; 327.75 – 362.25; 345 – 359. 138; 131.1 – 144.9; 138 – 144. 69; 65.55 – 72.45; 69 – 71.5. WHEN: - Indicated by SCADA alarms, OR - Notified by a TO of voltage concerns; THEN: - Initiate a solution in collaboration with the appropriate TO and QSE in the area. WHEN: - TOs have utilized all Static Reactive Power Resources (capacitors, reactors, change in transformer taps) and a voltage issue still remains; THEN: - Instruct a QSE to raise or lower bus voltage, - The QSE should complete the requested in no more than five minutes. Typical Script: “This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is instructing [QSE] to [raise or lower] voltage at [specify bus] by [+1 or 2kV or -1 or 2kV] for a target of [target kV]. [QSE] please repeat this instruction back to me. That is correct, thank you.” |
| GTCs | IF: - Any of the GTCs is approaching 85%, OR - A TO calls to report a GTC approaching 85%; THEN: - Activate the associated “BASECASE” constraint in TCM - Update RTMONI with new limit each time it changes |
| DC Tie Tags | Make every attempt to handle all DC Tie tags. If the workload makes it impossible to keep up with, the tags will be passively denied. |
| Log | Make log entry of events. |
| ### Systems are not Functional |  |
| Monitor Frequency | The ability to view an adequate Frequency source may be limited during a site-failover, database load, or if AGC is temporarily unavailable. To view the System Frequency during these conditions you may monitor the following sources. - ERCOT Control Room digital wall frequency displays - PI ProcessBook → ERCOT → TrueTime Frequency (Taylor) and/or - PI ProcessBook → ERCOT → TrueTime Frequency (Bastrop) It may be necessary to reload the PI ProcessBook “ERCOT Main Summary” display to show the historical data. |
| Constant Frequency | IF: - The loss of PCC involves the loss of EMS (LFC and RLC); THEN: - Frequency is degrading +/- .10~.15 Hz of 60 Hz - Instruct a QSE to go on Constant Frequency |
| Call in Additional Operators | Activate the NXT scenario to call in additional shift personnel, which includes a Shift Supervisor. SELECT: - SO Loss of Control Room at Taylor, OR; - SO Loss of Control Room at Bastrop. - Operator will receive an email after 10 minutes with a report of who has responded along with their estimated time of arrival. |
| QSE Hotline Call | - Q#107 - Typical Hotline Script Emergency Notice Loss of Primary Control Center (Systems are NOT Functional) |
| TO Hotline Call | - T#92 - Typical Hotline Script Emergency Notice Loss of Primary Control Center (Systems are NOT Functional) |
| MIS Posting | As time permits, post the Emergency Notice in the Public MIS. - Typical Posting Script: ERCOT has issued an Emergency Notice for the loss of the primary control center. |
| Additional Notifications | - The Manager of System Operations and/or Control Room Operations Manager will notify the following: - Help Desk (to notify EMMS Support and Telecommunications) - Engineering Support These phone numbers are also programmed into the control room cell phone. |
| Respond to QSEs | IF: - The QSE that is put on constant frequency is having trouble controlling frequency; THEN: - Issue a unit specific Operating Instruction to another QSE to help with Regulation. (Follow-up with electronic Dispatch Instruction as time permits) OR - Put a different QSE on constant frequency (Remember to take the first QSE off constant frequency). |
| Respond to TOs Thermal/ Voltage Limits Reached (SOL) | IF: - Thermal limits have reached their emergency rating; THEN: - Seek a recommendation from the corresponding TO as to what actions will alleviate the situation, and issue unit specific Operating Instructions to appropriate QSE. - Continue to monitor to determine the effect of the plan. ERCOT Nominal Voltage Levels are 345kV, 138kV, and 69kV. The general voltage guidelines are as follows (listed in kV): Nominal Voltage; Operating Limits; Ideal Voltage Range. 345; 327.75 – 362.25; 345 – 359. 138; 131.1 – 144.9; 138 – 144. 69; 65.55 – 72.45; 69 – 71.5. WHEN: - Notified by a TO of voltage concerns; THEN: - Initiate a solution in collaboration with the appropriate TO and QSE in the area. WHEN: - TOs have utilized all Static Reactive Power Resources (capacitors, reactors, change in transformer taps) and a voltage issue still remains; THEN: - Instruct the appropriate QSE to raise or lower bus voltage, - The QSE should complete the requested in no more than five minutes. Typical Script: “This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is instructing [QSE] to [raise or lower] voltage at [specify bus] by [+1 or 2kV or -1 or 2kV] for a target of [target kV]. [QSE] please repeat this instruction back to me. That is correct, thank you.” |
| GTCs | IF: - A TO calls to report a GTCs approaching 85% and is continuing to trend upward; THEN: - Take action to adjust generation in the appropriate area by issuing unit specific Operating Instructions as necessary to relieve the congestion (Follow-up with electronic Dispatch Instructions as time permits). - Monitor QSE on constant frequency |
| Thermal Limits Reached (SOL) | IF: - Thermal limits have reached their continuous rating and are continuing to trend upward, THEN: - Seek a recommendation from the corresponding TO as to what actions will alleviate the situation, and issue unit specific Operating Instructions as necessary (Follow-up with electronic Dispatch Instruction as time permits) - Continue to monitor to determine the effect of the plan. |
| DC Tie Tags | Make every attempt to handle all DC Tie tags. If the workload makes it impossible to keep up with, the tags will be passively denied. |
| Electronic Dispatch Instruction | Follow-up with electronic Dispatch Instructions where appropriate when systems are functional or as time permits (See Desktop Guide Common to Multiple Desks section 2.3). When issuing a VDI or confirmation, ensure the use of three-part communication: - Issue the Operating Instruction - Receive a correct repeat back - Give an acknowledgement |
| Log | - Make log entry of events. |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Frosch, Hartmann, Stone, and Barcalow | Preparers | November 10, 2010 |
| Frosch and Hartmann | Procedure writers and editors | November 27, 2010 |
| Frosch and Hartmann | Procedure writers and editors | January 26, 2011 |
| Frosch and Hartmann | Procedure writers and editors | March 23, 2011 |
| Frosch and Hartmann | Procedure writers and editors | April 20, 2011 |
| Frosch and Hartmann | Procedure writers and editors | June 6, 2011 |
| Frosch and Hartmann | Procedure writers and editors | June 16, 2011 |
| Frosch and Hartmann | Procedure writers and editors | July 18, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 30, 2011 |
| Frosch and Hartmann | Procedure writers and editors | September 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | October 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 16, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | April 25, 2012 |
| Frosch and Hartmann | Procedure writers and editors | July 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | August 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | October 26, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 26, 2013 |
| Frosch and Hartmann | Procedure writers and editors | May 28, 2013 |
| Frosch and Hartmann | Procedure writers and editors | June 27, 2013 |
| Frosch and Hartmann | Procedure writers and editors | July 9, 2013 |
| Frosch and Hartmann | Procedure writers and editors | August 28, 2013 |
| Frosch and Hartmann | Procedure writers and editors | December 11, 2013 |
| Frosch and Hartmann | Procedure writers and editors | January 27, 2014 |
| Frosch and Hartmann | Procedure writers and editors | February 18, 2014 |
| Frosch and Hartmann | Procedure writers and editors | February 26, 2014 |
| Frosch, Gaddy and Hartmann | Procedure writers and editors | April 1, 2014 |
| Frosch, Gaddy and Hartmann | Procedure writers and editors | May 27, 2014 |
| Frosch, Gaddy and Hartmann | Procedure writers and editors | July 27, 2014 |
| Frosch and Hartmann | Procedure writers and editors | September 29, 2014 |
| Frosch Hartmann and Lopez | Procedure writers and editors | December 10, 2014 |
| Frosch and Hartmann | Procedure writers and editors | February 25, 2015 |
| Frosch and Hartmann | Procedure writers and editors | April 29, 2015 |
| Frosch, Hartmann and Gaddy | Procedure writers and editors | July 13, 2015 |
| Hartmann and Gaddy | Procedure writers and editors | December 22, 2015 |
| Hartmann, Gaddy and Frosch | Procedure writers and editors | February 23, 2016 |
| Hartmann, Gaddy and Frosch | Procedure writers and editors | April 22, 2016 |
| Hartmann, Gaddy and Frosch | Procedure writers and editors | June 24, 2016 |
| Hartmann and Gaddy | Procedure writers and editors | September 26, 2016 |
| Hartmann and Gaddy | Procedure writers and editors | October 31, 2016 |
| Hartmann and Gaddy | Procedure writers and editors | December 23, 2016 |
| Hartmann, Gaddy and Frosch | Procedure writers and editors | March 27, 2017 |
| Hartmann and Gaddy | Procedure writers and editors | April 5, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | May 26, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | September, 27, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | October 27, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | December 22, 2017 |

| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | February 22, 2018 |
| --- | --- | --- |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | February 22, 2018 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | April 27, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | May 25, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | August 24, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | September 26, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | October 29, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | December 21, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | January 25, 2019 |
| Hartmann, Gaddy, Luker and Frosch | Procedure writers and editors | March 25, 2019 |
| Hartmann, Gaddy and Pence | Procedure writers and editors | May 13, 2019 |
| Hartmann, Gaddy and Pence | Procedure writers and editors | May 28, 2019 |
| Hartmann, Gaddy and Pence | Procedure writers and editors | July 29, 2019 |

Manual Change History

| Procedure | Ver/Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All Sections | 1.0 / 0 | New procedures for all sections for Nodal implementation | November 30, 2010 |
| 3.1 3.3 3.12 3.13 3.14 3.16 3.17 4.1 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Updated step 1 Updated step 1 Updated step 1 and added Log Updated step 4 Updated step 3 Updated step 1 and added Log Updated step 3 Updated Constant Frequency, Respond to QSE’s, Stability Limits Reached and Thermal Limits Reached | December 1, 2010 |
| 2.3 3.4 4.1 4.2 4.3 | 1.0 / 0 1.0 / 1 1.0 / 2 1.0 / 1 1.0 / 1 | Added new procedure Updated step 1 Updated steps “Constant Frequency”, “QSE Hotline Call”, “TO Hotline Call”, “Respond to QSEs” “Respond to TOs”, “Stability Limits” and added “Nuclear Plants” Updated Note and “Additional Operators” Updated Hotline in “Notifications” | January 31, 2011 |
| 2.3 3.1 3.2 3.3 3.7 4.1 4.2 4.3 4.4 4.5 4.6 4.7 4.8 4.9 | 1.0 / 1 1.0 / 2 1.0 / 1 1.0 / 2 1.0 / 1 - / 2 1.0 / 2 - / 2 1.0 / 1 1.0 / 2 1.0 / 2 1.0 / 3 - / 2 1.0 / 2 | Updated NXT Test Updated 4th Note and step 1 Updated step 2 Updated 5th note, step 1, deleted step 4 and 6th Note Updated all sections Section number changed from 3.12 and updated all steps Section number changed from 3.13 and updated all steps Section number changed from 3.14 and updated all steps Section number changed from 3.15 and updated all steps Section number changed from 3.16 and updated step 1 Section number changed from 3.17 and updated step 1 Section number changed from 4.1 & updated multiple steps Section number changed from 4.2 & Note Section number changed from 4.3 | March 25, 2011 |
| 1.1 2.3 3.1 3.2 3.3 3.4 3.5 3.6 3.7 3.8 3.9 3.10 4.1 4.2 4.3 4.4 4.5 4.6 4.7 4.9 | 1.0 / 1 1.0 / 2 1.0 / 3 1.0 / 2 1.0 / 3 1.0 / 2 1.0 / 1 1.0 / 1 - / 2 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 3 1.0 / 3 1.0 / 3 1.0 / 2 1.0 / 3 1.0 / 3 1.0 / 4 1.0 / 3 | Updated text Updated step “Beginning of each Shift” Updated 1st & 3rd note and step 1, deleted 2nd note and added 5th note Updated 1st note and step 2 Updated 1st & 4th note, step 1 & 2, deleted 2nd and added 5th note Updated 1st & step 1 Updated steps 1, 2 and 3 Updated “Import” step 1 and “Export” steps 1 & 2 Updated all sections Updated all sections Updated all sections Updated 1st & 2nd note and step 1 and 2 Updated 1st note and step 1 Updated 1st note Updated 1st note Updated step 3 Updated step 1 Updated step 2 Updated step QSE Hotline Call Updated step 1 in Watch and Emergency Notice | April 22, 2011 |
| 3.1 3.2 3.3 3.4 3.5 3.6 3.73.8 3.9 3.10 3.11 4.1 4.2 4.3 4.4 4.5 4.6 4.7 4.9 | 1.0 / 4 1.0 / 3 1.0 / 4 1.0 / 3 1.0 / 2 1.0 / 2 1.0 / 31.0 / 2 1.0 / 1 1.0 / 2 1.0 / 1 1.0 / 4 1.0 / 4 1.0 / 3 1.0 / 3 1.0 / 4 1.0 / 4 - / 5 1.0 / 4 | Updated all steps Updated all steps Updated all steps Updated step 1 Updated step 1, 2, 3 & added 2nd note Updated step 1 and 2 Updated all steps Updated all steps Updated all steps Updated 3rd note and step 1 Updated all steps Updated all steps Updated all steps Updated all steps Updated all steps Updated step 1 Updated steps 2 & 3 Updated steps Call in Additional Operators and Respond to QSEs Updated all steps | June 8, 2011 |
| 3.1 3.3 3.7 3.9 4.2 | 1.0 / 5 1.0 / 5 1.0 / 4 1.0 / 2 1.0 / 5 | Changed 3rd Note to step 1, updated step 1 & 2 Updated step 1 Updated all steps in DC Tie Trips, step 1 in Transmission Issues within ERCOT & step 1 & 2 in Transmission Issues within CFE Updated webtrans references Updated step 1 | June 17, 2011 |
| 3.1 3.3 3.6 3.7 3.9 3.11 4.1 4.2 4.3 4.4 4.5 4.6 4.7 4.8 | 1.0 / 6 1.0 / 6 1.0 / 3 1.0 / 5 1.0 / 3 1.0 / 2 1.0 / 6 1.0 / 4 1.0 / 5 1.0 / 5 1.0 / 5 1.0 / 5 1.0 / 2 1.0 / 5 | Updated 1st Note and step 1 & 2 Updated step 1 Updated all steps Split procedure out, changed title and moved Transmission Issue within ERCOT to 4.5 Updated step 2 Updated steps 2, 4 and 5 Updated step 1, added steps 2 - 4 Updated all steps, added new step 3 Updated Turret phone label for SPP Tariff and all steps Changed section number from 4.4 to 4.3 and updated all steps Changed section number from 4.5 to 4.4 and updated all steps Changed section number from 4.6 to 4.5, updated all steps and moved Transmission Issues from 3.7 to 4.5 Changed section number from 4.7 to 4.6 Changed section number from 4.8 to 4.7 Changed section number from 4.9 to 4.8 and updated step 1 in Watch | July 20, 2011 |
| 2.3 3.1 3.2 3.3 3.6 3.7 3.8 3.9 3.11 4.1 4.2 4.3 4.5 4.6 4.8 | 1.0 / 3 1.0 / 7 1.0 / 4 1.0 / 7 1.0 / 4 1.0 / 6 1.0 / 3 1.0 / 4 1.0 / 3 1.0 / 7 1.0 / 5 1.0 / 6 1.0 / 6 1.0 / 6 1.0 / 6 | Updated step “Beginning of each Shift” Updated 1st note Updated steps 1, 2 & 3 Updated 1st, 4th note and step 1 Updated step 1 “Imports” and step 2 “Exports” Updated Steps 1, 2 and 4 in “CFE DC-Ties” Updated 2nd note and steps 1-3 Updated steps 1-3 Updated steps 1 and 2 Updated all steps Updated all steps Updated all steps Updated all steps Removed reference of Austin Control Room Added projected reserve capacity shortage and Extreme Hot Weather in Watch | September 1, 2011 |
| 3.1 3.3 4.1 4.2 4.3 | 1.0 / 8 1.0 / 8 1.0 / 8 1.0 / 6 1.0 / 7 | Updated step 2 Updated step 1 Updated Turret Phone, step 3a in Comision Federal de Electricidad (CFE) and step 5b to implement NPRR 379 Updated Turret Phone and step 3a in Comision Federal de Electricidad (CFE) Updated step 3 | October 1, 2011 |
| 4.6 | 1.0 / 7 | Updated step TO Hotline Call | November 1, 2011 |
| 3.1 3.3 4.6 4.8 | - / 9 1.0 / 9 1.0 / 8 1.0 / 7 | Updated step 2 Updated step 1 Added new section and updated all steps Updated Post in “Notifications” All procedures in this manual have been reviewed. | December 15, 2011 |
| 1.2 3.1 3.3 4.6 | 1.0 / 1 1.0 / 10 1.0 / 10 1.0 / 9 | Updated Scope Updated step 2 Updated step 1 Updated Hotline call scripts | January 19, 2012 |
| 2.1 2.3 3.1 3.2 3.7 4.1 4.2 4.3 4.5 4.8 | 1.0 / 1 1.0 / 4 1.0 / 11 1.0 / 5 1.0 / 7 1.0 / 9 1.0 / 7 1.0 / 8 1.0 / 7 1.0 / 8 | Added dispatch instructions paragraph Updated Desktop Guide reference Added 3rd Note Changed Shift Engineer to Operations Support Updated Desktop Guide references Updated Desktop Guide references Updated Desktop Guide references Updated Desktop Guide references Updated 2nd Note & all steps 1 – 3 Updated step 1 of Watch | March 1, 2012 |
| 3.1 3.3 3.7 3.8 3.9 4.54.6 4.8 | 1.0 / 12 1.0 / 11 1.0 / 8 1.0 / 4 1.0 / 5 1.0 / 8 1.0 / 10 1.0 / 9 | Updated step 2 Updated 3rd Note and step 1 Added posting and cancelling messages Updated overview Updated overview Updated procedure based on NPRR405 Updated W-N or N-H steps Updated OCN, Advisory, Watch and Emergency Notice for Cold Weather and Extreme Cold Weather | May 1, 2012 |
| 1.3 3.2 3.8 3.9 4.5 4.6 4.8 | 1.0 / 1 1.0 / 6 1.0 / 5 1.0 / 6 1.0 / 9 1.0 / 11 1.0 / 10 | Removed ERCOT Shift Supervisor paragraph Updated step 1 Updated step 4 Updated step 4 Added step Turret Phone & 1st Note, updated step 4 Updated several steps based on lessons learned from classroom training and simulation Updated all step 1’s | July 16, 2012 |
| 3.1 | 1.0 / 13 | Updated step 2 | August 29, 2012 |
| 2.2 3.2 4.5 4.6 | 1.0 / 1 1.0 / 7 1.0 / 10 1.0 / 12 | Added Hotline Call Communication Updated 1st Note Updated 1st and 2nd Note Updated steps West to North & North to Houston(IROL) All procedures in this manual have been reviewed. | November 1, 2012 |
| 3.1 3.10 4.6 | 1.0 / 14 1.0 / 3 1.0 / 13 | Updated step 2 Updated 2nd note Updated Additional Notifications on Systems Functional and Systems are not Functional | March 1, 2013 |
| 3.1 3.2 3.7 3.11 4.6 | 1.0 / 15 1.0 / 8 1.0 / 9 1.0 / 4 1.0 / 14 | Updated step 2 Updated step 1, deleted steps 2 & 3 Updated scripts Updated script Updated scripts, West to North & step North to Houston | June 1, 2013 |
| 3.6 4.3 4.4 4.5 4.6 | 1.0 / 5 1.0 / 9 1.0 / 6 1.0 / 11 1.0 / 15 | Updated Exports, step 1 Updated step 1 & 3 Updated step 1 Deleted 2nd Note, updated step 1, 2 & 4 Added Monitor Frequency and updated Constant Frequency | July 1, 2013 |
| 3.1 3.3 3.11 4.8 | 1.0 / 16 1.0 / 12 1.0 / 5 1.0 / 11 | Updated step 1 Updated 4th note Updated step 1 Updated step 1 in Watch & Emergency Notice | July 15, 2013 |
| 3.7 4.6 | 1.0 / 10 1.0 / 16 | Added CFE DC-Tie Derates and AEP DC-Tie Derates Removed HHGT TO reference | August 30, 2013 |
| 1.1 3.3 3.4 3.5 3.6 3.8 3.9 3.11 4.1 4.2 4.5 | 1.0 / 2 1.0 / 13 1.0 / 4 1.0 / 3 1.0 / 6 1.0 / 6 1.0 / 7 1.0 / 6 1.0 / 10 1.0 / 8 1.0 / 12 | Changed “Security” to “Reliability” Updated step 2 Updated both steps Updated last Note and step 3 Updated the Notes and step 1 and 2 Updated step 2 Updated step 2 New Loss of DC-Tie Operator E-tagging Updated step 6b Updated step 6b Added note to Transmission Issues within CFE All procedures in this manual have been reviewed. | December 13, 2013 |
| 3.8 4.1 4.2 4.3 4.4 4.5 4.8 | 1.0 / 7 1.0 / 11 1.0 / 9 1.0 / 10 1.0 / 7 1.0 / 13 1.0 / 13 | Updated step 2 Updated step Turret Phone, 3a, 6b, Note, & 7b Updated step Turret Phone, 3a, 6b, Note, & 7b Updated step 3 Updated step 2 Updated step Turret Phone & 4 Updated all step 1’s | January 29, 2014 |
| 3.3 3.6 3.7 3.9 3.10 3.11 3.12 4.1 4.2 4.3 4.5 | 1.0 / 14 1.0 / 7 1.0 / 11 1.0 / 8 1.0 / 0 1.0 / 4 1.0 / 7 1.0 / 12 1.0 / 10 1.0 / 11 1.0 / 14 | Updated 1st & 4th Note & step 1 to include Sharyland as Tie Operator Updated steps 1 & 2 Updated steps 1, 2, 3 & Cancel Message Updated 1st Note, step 2, 3 & 5 New procedure Updated section number Updated section number & step 2 Updated Turret Phone, 1st Note, CFE & SPP sections Updated Turret Phone, 1st Note, CFE & SPP sections Updated 1st None, steps 1, 2 & 3 Updated to include Sharyland change | February 25, 2014 |
| 3.1 3.4 3.5 3.7 3.8 3.9 3.10 3.11 3.12 4.1 4.24.3 4.4 4.5 4.6 4.7 4.8 | 1.0 / 17 1.0 / 5 1.0 / 4 1.0 / 12 1.0 / 8 1.0 / 9 1.0 / 1 1.0 / 5 - / 8 - / 13 - / 11 1.0 / 12 1.0 / 7 1.0 / 15 1.0 / 17 1.0 / 3 1.0 / 14 | Updated 1st Note Updated step 1 Updated steps 2 and 3 Updated step Post Message Updated steps Note through 5 Updated step 5 Updated step 5 Updated 1st Note, steps 1 to CFE DC-Ties and 2 to SPP DC-Ties Updated steps 2, 4 & 5 on Loss of ERCOT E-Tagging and step 1 on Loss of DC Tie Operator E-Tagging Updated steps Turret Phone, Note, 2b, 3b, 4b & 6b on Southwest Power Pool (SPP) Deleted ERCOT Declares EEA 2 or 3 Re-numbered procedure to 4.2 Delete Emergency Energy to SPP procedures Re-numbered procedure to 4.3 Re-numbered procedure to 4.4 Re-numbered procedure to 4.5 Re-numbered procedure to 4.6 | March 1, 2014 |
| 3.1 3.2 4.1 4.2 4.3 4.4 | 1.0 / 18 1.0 / 9 1.0 / 14 - / 13 - / 16 - / 18 | Updated step 2 Updated step 1 & 2 Updated VDI information Updated VDI information Updated VDI information Updated VDI information & Updated Guide Reference | April 4, 2014 |
| 2.2 3.1 3.3 3.8 3.9 3.10 4.1 4.6 | 1.0 / 2 1.0 / 19 1.0 / 15 1.0 / 9 1.0 / 10 1.0 / 2 1.0 / 15 1.0 / 15 | Added VDIs to Master QSEs Updated step 2 Updated step 1 Updated Monitor, deleted step Caution & added step 5 Updated Monitor & deleted step Caution Updated Monitor & deleted step Caution Updated title Added Note, updated Advisory & Watch | June 1, 2014 |
| 3.1 3.3 3.8 4.3 | 1.0 / 20 1.0 / 16 1.0 / 10 1.0 / 17 | Updated step 2 Updated step 1 & 2 Updated 2nd Note Updated step 4 in Emergency Condition within CFE | August 1, 2014 |
| 3.1 3.3 4.2 4.3 4.6 | 1.0 / 21 1.0 / 17 1.0 / 14 1.0 / 18 1.0 / 16 | Updated step 2 Updated step 1 Spilt step 3 into two steps for clarification Spilt step 4 into two steps for clarification Updated Generic Script | October 1, 2014 |
| 3.8 3.9 3.10 4.1 4.2 4.3 4.4 | 1.0 / 11 1.0 / 11 1.0 / 3 1.0 / 16 1.0 / 15 1.0 / 19 1.0 / 19 | Updated step 6 Updated step 5 Updated step 5 Updated step EEA Updated step Note Updated step 2nd Note Updated TO scripts, delete W-Ns & revised GTLs All procedures in this manual have been reviewed | December 15, 2014 |
| 2.2 3.8 4.1 4.2 4.3 4.4 | 1.0 / 3 1.0 / 12 1.0 / 17 1.0 / 16 1.0 / 20 1.0 / 20 | Added Dispatch and VDI definition Correction to step 5 Reformatted section Reformatted section Corrected VDI/Dispatch Instruction language Reformatted section | March 1, 2015 |
| 3.8 4.1 4.4 | 1.0 / 13 1.0 / 18 1.0 / 21 | Correction to step 2 Updated step 2 & 4 on DC-Ties with Southwest Power Pool (SPP) Updated GTL to new term GTC | May 1, 2015 |
| 3.1 3.3 | 1.0 / 22 1.0 / 18 | Updated step 2 Updated 4th Note and step 1 | July 15, 2015 |
| 4.1 | 1.0 / 19 | Added step 3, 4, and Log to DC-Ties with Comisión Federal de Electricidad (CFE) All procedures in this manual have been reviewed | December 31, 2015 |
| 1.3 2.1 | 1.0 / 2 1.0 / 2 | Removed Interchange Coordinator Updated System Operator Resonsibility and Authority | March 1, 2016 |
| 3.1 3.2 3.3 3.4 3.5 | 1.0 / 23 1.0 / 10 1.0 / 19 1.0 / 6 1.0 / 5 | Added Note 4 Updated steps 1, 2 & 3 Added Note 4, & renumbered steps Updated step 1 Updated steps 1, 2 & 3, deleted 2nd Note | April 29, 2016 |
| 2.1 2.2 4.1 4.2 4.3 4.4 4.6 | 1.0 / 3 1.0 / 4 1.0 / 20 1.0 / 17 1.0 / 21 1.0 / 22 1.0 / 17 | Updated for COM-002-4 Updated for COM-002-4 Updated for COM-002-4 Updated Step Electronic Dispatch Instruction Updated for COM-002-4 Updated Step Electronic Dispatch Instruction Updated for COM-002-4 Updated Step Electronic Dispatch Instruction Updated for COM-002-4 Updated for COM-002-4 | June 30, 2016 |
| 3.2 3.3 3.6 3.12 | 1.0 / 11 1.0 / 20 1.0 / 8 1.0 / 9 | Updated Note, Step 1 and Step 2. Removed Step 3 Updated Step 2 Updated Exports Step 1 Moved Exports step 2 to step 3 Added Exports Step 2 Updated Step 3 | September 30, 2016 |
| 3.2 3.3 | 1.0 / 12 1.0 / 21 | Updated Procedure Purpose Updated step Note Added step Adjustment Period Updated step 1 & 2 Updated step 2 | November 2, 2016 |
|  |  | All procedures in this manual have been reviewed | December 30, 2016 |
| 1.3 2.1 2.3 3.2 3.3 3.6 3.7 3.9 3.10 3.11 4.1 4.2 4.3 4.6 | 1.0 / 3 1.0 / 4 1.0 / 5 1.0 / 13 1.0 / 22 1.0 / 9 1.0 / 13 1.0 / 12 1.0 / 4 1.0 / 6 1.0 / 21 1.0 / 18 1.0 / 22 1.0 / 18 | Deleted section 1.3 Updated for IRO-001-4 Updated step NXT Updated CFE to CENACE Updated CFE to CENACE Updated CFE to CENACE Updated CFE to CENACE Updated CFE to CENACE Updated CFE to CENACE Updated CFE to CENACE Updated CFE to CENACE Updated CFE to CENACE Updated CFE to CENACE Updated heading title and OCN step 1 | March 31, 2017 |
| 4.3 | 1.0 / 23 | Transmission Watch Issued for Post-Contingency Overloads on the South DC Ties Added section Transmission Watch Issued for the Rio Grande Valley Import | April 6, 2017 |
| 3.2 3.7 3.10 4.2 4.3 | 1.0 / 14 1.0 / 14 1.0 / 5 1.0 / 19 1.0 / 24 | Updated all steps Updated step 1 & 2 Updated step 1 Updated step 1 Updated second note and step 4 in Emergency Condition within CENACE | June 1,2017 |
| 3.1 | 1.0 / 24 | Added East HVDC Tie Voltage Limits | September 29, 2017 |
| 3.3 | 1.0 / 23 | Moved step 4 to step 2 and deleted step 4 | October 31, 2017 |
|  |  | All procedures in this manual have been reviewed | December 28, 2017 |
| 3.5 4.1 | 1.0 / 6 1.0 / 22 | Updated steps Added new step #4 and updated step #4 to #5 | February 28, 2018 |
| 3.3 | 1.0 / 24 | Updated for NPRR861 | March 30, 2018 |
| 2.2 3.3 3.8 3.9 3.10 | 1.0 / 5 1.0 / 25 1.0 / 14 1.0 / 13 1.0 / 6 | Updated procedure purpose Updated step 2 Updated steps 2, 3, 4 & 6 Updated steps 3, 4, & 5 Updated steps 3, 4, & 5 | May 1, 2018 |
| 4.1 4.2 4.3 | 1.0 / 23 1.0 / 20 1.0 / 25 | Updated Electronic Dispatch Instruction steps Updated Electronic Dispatch Instruction steps Updated Emergency Condition within ERCOT step 5 | May 31, 2018 |
| 3.1 3.3 4.1 4.2 4.3 | 1.0 / 25 1.0 / 26 1.0 / 24 1.0 / 21 1.0 / 26 | Updated step 1 Updated step 1 Updated steps Electronic Dispatch Instruction Updated steps Electronic Dispatch Instruction Updated second note and Updated Emergency Condition within ERCOT step 5 | August 31, 2018 |
| 3.2 3.3 3.5 3.6 3.7 3.10 4.1 4.2 4.3 | 1.0 / 15 1.0 / 27 1.0 / 7 1.0 / 10 1.0 / 15 1.0 / 7 1.0 / 25 1.0 / 22 1.0 / 27 | Updated for NPRR825 Updated for NPRR825 Updated for NPRR825 Updated for NPRR825 Updated for NPRR825 Updated for NPRR825 Updated for NPRR825 Updated for NPRR825 Updated for NPRR825 | October 1, 2018 |
| 3.6 3.7 4.1 4.2 4.3 | 1.0 / 11 1.0 / 16 1.0 / 26 1.0 / 23 1.0 / 28 | Added step to cancel message Added steps to cancel message Added steps to post and cancel messages Added step to cancel message Added steps to post and cancel messages | November 1, 2018 |
|  |  | All procedures in this manual have been reviewed | December 28, 2018 |
| 3.3 | 1.0 / 28 | Updated step 2 | January 31, 2019 |
| 3.3 3.6 3.8 4.4 | 1.0 / 29 1.0 / 12 1.0 / 15 1.0 / 23 | Updated step 2 Added step Note Updated SPP Interchange to SPP Balancing Updated step Contact Security | March 29, 2019 |
| 3.3 3.6 3.10 3.12 4.1 4.2 4.3 | 1.0 / 30 1.0 / 13 1.0 / 8 1.0 / 10 1.0 / 27 1.0 / 24 1.0 / 29 | Updated SHARYLAND to ONCOR Updated SHARYLAND to ONCOR Updated SHARYLAND to ONCOR Updated SHARYLAND to ONCOR Updated SHARYLAND to ONCOR Updated SHARYLAND to ONCOR Updated SHARYLAND to ONCOR | May 16, 2019 |
| 3.1 3.3 | 1.0 / 26 1.0 / 31 | Updated step 1 & 2 Updated step 1 & 2 | May 31, 2019 |
| 4.1 4.4 | 1.0 / 28 1.0 / 24 | Added Note DC-Ties with Southwest Power Pool (SPP) Moved Typical Hotline Scripts to Scripts | August 1, 2019 |