- Power Operations Bulletin # 905

ERCOT has posted/revised the Scripts manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

- http://www.ercot.com/mktrules/guides/procedures/index.html

### Typical Scripts for QSEs

Q#1 Advisory for PRC <3000 MW:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back.  This is ERCOT Operator [first and last name].  At [xx:xx], ERCOT is issuing an Advisory due to Physical Responsive Capability falling below 3000 MW.  [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#2 Cancel Advisory for PRC <3000 MW:

“This is ERCOT Operator [first and last name].  At [xx:xx], ERCOT is canceling the Advisory for Physical Responsive Capability.  Physical Responsive Capability is now above 3000 MW.  [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

Q#3 Watch for PRC <2500 MW:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back.  This is ERCOT Operator [first and last name].  At [xx:xx], ERCOT is issuing a Watch due to Physical Responsive Capability falling below 2500 MW.    Suspend all Resource testing and update telemetered Resource Status Codes.  ERCOT is reminding you, that you can schedule available interchange into ERCOT across the DC Ties.  [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

Q#4 Cancel Watch for PRC < 2500 MW:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back.  This is ERCOT Operator [first and last name].  At, [xx:xx], ERCOT is canceling the Watch for Physical Responsive Capability.  At this time, the Advisory is still in effect.   Approved Resource testing may resume as scheduled.  [QSE] please repeat this back to me. ”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#5 EEA1 NOT deploying ERS:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name].  At [xx:xx], ERCOT is declaring EEA 1, QSEs are to perform their necessary steps for EEA 1.  [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#6 EEA1 deployed ERS-30 / ERS-30 including Weather Sensitive:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name].  At [xx:xx], ERCOT is declaring EEA 1, QSEs are to perform their necessary steps for EEA 1.  All [30 min / 30 min including Weather Sensitive] ERS Resources with an obligation have been deployed. [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#7 EEA2 deployed ERS-10 / ERS-30 / both ERS-10 and ERS 30 / ERS-30 including Weather Sensitive ERS / ERS-10 and ERS-30 including Weather Sensitive:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back.  This is ERCOT Operator [first and last name], at [xx:xx], ERCOT is declaring EEA 2 and is issuing an appeal through the public news media for voluntary energy conservation.  All [10 min / 30 min / both 10 min and 30 min / 30 min including Weather Sensitive / 10 min, 30 min including Weather Sensitive] ERS Resources with an obligation have been deployed.  Implement all measures associated with EEA 1 if not already implemented.  [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#8 EEA2 deployed Load Resources Group 1 / Load Resources Group 1 and 2:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back.  This is ERCOT Operator [first and last name], at [xx:xx], ERCOT is declaring EEA 2 and is issuing an appeal through the public news media for voluntary energy conservation.  [Group 1 / Group 1 and 2] Load Resources have been deployed.  Implement all measures associated with EEA 1, if not already implemented. [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#9 EEA2 deployed ERS-10 / ERS-30 / both ERS-10 and ERS-30 / ERS-10, ERS-30 including Weather Sensitive Script:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back.  This is ERCOT Operator [first and last name], at [xx:xx], ERCOT is in EEA 2.  All [10 min / 30 min / both the 10 min and 30 min / 10 min and 30 min including Weather Sensitive] ERS Resources with an obligation have been deployed.    [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#10 Media Appeal:

“This is ERCOT Operator [first and last name]; ERCOT has issued an appeal through the public news media for voluntary energy conservation.  Any questions?  Thank you”.

## Q#11 EEA3 With Firm Load Shed:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back.  This is ERCOT Operator [first and last name], at [xx:xx], ERCOT is declaring EEA 3 with firm load shed, [MW Amount] of firm load is being shed.  Implement all measures associated with EEA 1 and 2, if not already implemented. [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#12 EEA3 deployed ERS-10 / ERS-30 / both ERS-10 and ERS-30 / ERS-10, ERS-30 including Weather Sensitive:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back.  This is ERCOT Operator [first and last name], at [xx:xx], ERCOT is in EEA3.  All [10 min / 30 min / both the 10 min and 30 min / 10 min and 30 min including Weather Sensitive] ERS Resources with an obligation have been deployed.    [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#13 Restoring Firm Load:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back.  This is ERCOT Operator [first and last name], at [xx:xx], ERCOT is restoring firm load.

[QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#14 Moving from EEA3 to EEA2 recall Load Resource:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back.  This is ERCOT Operator [first and last name].  At [xx:xx], ERCOT is moving from EEA 3 to EEA 2.  QSEs are to recall all Load Resources at this time.  [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#15 Moving from EEA2 to EEA1 recall ERS:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back.  This is ERCOT Operator [first and last name].  At [xx:xx], ERCOT is moving from EEA 2 to EEA 1.  QSE’s are to recall [10 MIN], [30 MIN], [weather-sensitive ERS], [both 10 MIN and 30 MIN] or [both 10 MIN and 30 MIN including weather-sensitive] ERS Resources at this time. [QSE] please repeat this back to me.”

## Q#16 Terminate EEA:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back.  This is ERCOT Operator [first and last name].  At [xx:xx], ERCOT is terminating EEA 1.  A Watch still remains in effect.  [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”If INCORRECT, repeat the process until the repeat back is correct.

## Q#17 Cancel Watch for PRC below <2500:

“This is ERCOT Operator [first and last name].  At [xx:xx], ERCOT is canceling the Watch for Physical Responsive Capability.   At this time, Resource testing may resume.  [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#18 EMS Changes:

“This is ERCOT operator [first and last name], at [xx:xx], ERCOT will perform a [database load] [local failover] [EMS migration] on its Energy & [Market] Management System(s).  During this time, SCED Base Points will reflect accurate dispatch instructions.  In the event ICCP is temporarily suspended, all systems should re-establish automatically within a few minutes.  Any questions”?

## Q#19 MMS Changes:

“This is ERCOT operator [first and last name], at [xx:xx], ERCOT will perform a [migration] [patch] on its Market Management System.  [We do not expect to miss a SCED run] [Emergency Base Points may be issued during this time].  ERCOT will make another hotline call when the work is complete.  Any questions?”

## Q#20 Site Failover:

“This is ERCOT operator [first and last name], at [xx:xx], ERCOT will perform a site failover of its Energy & Market Management Systems.  During this time, market communications will be unavailable for about 20 minutes, and real-time communications will be unavailable for about 5 minutes.  All systems should re-establish communications automatically.  Any questions?”

## Q#21 Site Failover Complete:

“This call requires everyone to remain on the line until it is complete. At [xx:xx], the [site failover] [patch] [migration] is complete.  Any questions?  Thank you.”

## Q#22 Watch and Emergency Basepoints Needed until Site Failover complete:

“This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name], at [xx:xx],  ERCOT is issuing a Watch and Emergency Base Points will be issued.  ERCOT will make another hotline call when the site failover is complete.  [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#23 Cancel Watch and Emergency Basepoints, Site Failover Complete:

“This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name].  At [xx:xx], the site failover is complete, SCED basepoints are now valid and ERCOT is canceling the Watch.  All QSEs should continue normal operations.  [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#24 Working from Alternate Site:

“This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back.  This is ERCOT operator [first and last name], at [xx:xx], ERCOT will be working from the alternate control center until further notice, use the OPX numbers for Bastrop.  [QSE], please repeat that back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#25 Working from Primary Site:

“This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back.  This is ERCOT operator [first and last name], at [xx:xx], ERCOT will be working from the primary control center until further notice, use the OPX numbers for Taylor.  [QSE], please repeat that back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#26 Blank

## Q#27 Watch for SCED Failure:

“This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing a Watch due to the failure of SCED.  ERCOT may issue Emergency Base Points until the issue is resolved.  [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#28 Cancel Watch for SCED is Solving:

“This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], SCED base points are now valid and ERCOT is canceling the Watch.  [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#29 Watch for SCED Data Input Failure:

“This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing a Watch due to data input failure to SCED.  ERCOT may issue Emergency Base Points until the issue is resolved.  [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#30 Watch for RLC Failure:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back.  This is ERCOT Operator [first and last name].  At [xx:xx], ERCOT is issuing a Watch due to a SCED failure.  ERCOT may issue Emergency Base Points until the issue is resolved.  [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#31 Cancel Watch for RLC is Restored:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back.  This is ERCOT Operator [first and last name].  At [xx:xx], SCED solutions are now valid and ERCOT is canceling the Watch.  [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#32 Emergency Notice for a QSE on Constant Frequency for LFC/EMS Failure:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing an Emergency Notice due to [LFC/EMS] failure and has placed a QSE on Constant Frequency to provide regulation.  All remaining QSEs should hold their Resources to their current output level until instructed by ERCOT.  ERCOT may issue unit specific deployments to Resources as required.  [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#33 Cancel Emergency Notice for QSE on Constant Frequency for LFC/EMS Functioning:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], [LFC/EMS] is now functioning and ERCOT is canceling the Emergency Notice.  [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#34 Emergency Notice for a QSE on Constant Frequency for LFC/EMS and SCED failure:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back.  This is ERCOT Operator [first and last name].  At [xx:xx], ERCOT is issuing an Emergency Notice due to an [LFC/EMS] and SCED failure.  ERCOT has placed a QSE on Constant Frequency.  All remaining QSEs should hold their Resources to their current output level until instructed by ERCOT.  ERCOT may issue unit specific deployments to Resources as required.  [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#35 Cancel Emergency Notice with LFC/EMS Functioning, SCED valid:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back.  This is ERCOT operator [first and last name].  At, [xx:xx], [LFC/EMS] is now functional and SCED solutions are valid.  ERCOT is canceling the Emergency Notice.  [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#36 Recall Load Resources After a Frequency Event:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name].  At [xx:xx], ERCOT is recalling all Load Resources.  [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#37 Time Error Correction:

“This call requires everyone to remain on the line until it is complete.  This is ERCOT Operator [first and last name].  At [xx:xx], ERCOT is initiating a Time Error Correction, we will enter the frequency offset using [-0.02] or [+0.02] at [time].  The current time error is [time].  Thank you.”

## Q#38 End Time Error Correction:

“This call requires everyone to remain on the line until it is complete.  This is ERCOT Operator [first and last name].  ERCOT is ending the Time Error Correction at [xx:xx].  The current time error is [time].  Thank you.”

## Q#39 Watch for N-H Interface / Deploy Non-Spin:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back.  This is ERCOT operator [first and last name].  At [xx:xx], ERCOT is issuing a Watch for the North to Houston interface.  ERCOT will be deploying Non-Spin to specific resources to alleviate the condition.  [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#40 Emergency Notice for N-H Interface / Deploy Load Resources:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back.  This is ERCOT operator [first and last name].  At [xx:xx], ERCOT has issued an Emergency Notice for the North to Houston interface and has issued you an electronic instruction for the deployment of specific Load Resources to alleviate the condition.  [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#41 Cancel Emergency Notice for N-H Interface / Recall Load Resources:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back.  This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is canceling the Emergency Notice for the North to Houston interface and has issued you an electronic instruction for the recall of Load Resource deployments.  ERCOT is reminding everyone that a Watch is still in effect until further notice.   [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#42 Cancel Watch for N-H Interface / Recall Non-Spin:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back.  This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is canceling the Watch for the North to Houston interface.  ERCOT has recalled Non-Spin to specific resources to alleviate the condition.  [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#43 Advisory for GMD Alert:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an Advisory for a [state K-Index level] geomagnetic disturbance alert that has been issued for [date/hours].

[QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#44 GMD K-Level Increase/Decrease:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], The [state K-Index level] geomagnetic disturbance alert that we are currently under has [increase/decreased] to a [state K-Index level] until [date/hours].

[QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#45 Cancel Advisory for GMD:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is canceling the Advisory for the geomagnetic disturbance.  [QSE] please repeat this back to me.  ”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#46 Operating Condition Script:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name].  At [xx:xx], ERCOT is issuing a [state Notice type] for [state reason].  [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#47 Cancel Operating Condition Script:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name].  At [xx:xx], ERCOT is cancelling the [state Notice type] for [state reason].  [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#48 Advisory for State Estimator / RTCA Not Solved in 30 Min:

“This call requires everyone to remain on the line until it is complete.  .  [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name], at [xx:xx], ERCOT is issuing an Advisory due to ERCOTs [State Estimator/RTCA] has not solved in the last 30 minutes.

- Please monitor your Resources and notify ERCOT prior to any generation starting or shutting down.  Suspend any new planned outages, and notify ERCOT if any forced outages occur.

[QSE] please repeat that back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#49 Cancel Advisory for State Estimator/RTCA Now Solving:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back.  This is ERCOT operator [first and last name], at [xx:xx], ERCOT is canceling the Advisory, ERCOTs [State Estimator/RTCA] is now functional.  You may return to normal operations.  [QSE] please repeat that back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#50 Advisory for VSAT not solved in 30 Min:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back.  This is ERCOT Operator [first and last name],  at [xx:xx], ERCOT is issuing an Advisory due to ERCOTs Voltage Security Assessment Tool has not solved in the last 30 minutes.  This is for your information only, no action is required.  [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#51 Cancel Advisory for VSAT Now Solving :

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back.  This is ERCOT operator [first and last name], at [xx:xx], ERCOT is canceling the Advisory, ERCOTs VSAT tool is now functional.  [QSE] please repeat that back for me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#52 Emergency Notice for instructing Qualifying Facility to operate offline/below LSL:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back.  This is ERCOT Operator [first and last name].  At [xx:xx], ERCOT is issuing an Emergency Notice due to instructing a Qualifying Facility [offline or operate below its LSL].  [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#53 Cancel Emergency Notice for instructing Qualifying Facility to operate offline/below LSL:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back.  This is ERCOT Operator [first and last name].  At [xx:xx], ERCOT is canceling the Emergency Notice for instructing a Qualifying Facility [offline or operate below its LSL].  [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#54 OCN for a New Generic Transmission Constraint:

“This is ERCOT Operator [first and last name].  At [xx:xx], ERCOT is issuing an OCN to make notification of a new Generic Transmission Constraint.  A forced outage on [state forced outage] resulted in a GTC being created for [state reason for GTC].  [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#55 Transmission Watch for Post-Contingency Overload:

“This is ERCOT Operator [first and last name].  At [xx:xx], ERCOT is issuing a Transmission Watch due to the post-contingency overload of [constraint name] a [mitigation plan/temporary outage action plan] is being developed.  [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#56 Cancel Transmission Watch for Post-Contingency Overload:

“This is ERCOT Operator [first and last name].  At [xx:xx], ERCOT is canceling the Transmission Watch for post-contingency overload of [constraint name].  [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#57 Cancel Emergency Notice and Restore Primary Control Center:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back.  This is ERCOT operator [first and last name]; at [xx:xx], ERCOT is canceling the Emergency Notice and is resuming normal operations from the [alternate/primary] control center.  [Select QSE], Please repeat that back for me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#58 OCN for Hurricane/Tropical Storm:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an OCN for [Tropical Storm/Hurricane] [Name] due to a probability of making landfall in the ERCOT Region. QSEs are instructed to:

- Review fuel supplies and notify ERCOT of any known or anticipated fuel restrictions,

- Review Planned Resource outages and consider delaying maintenance,

- Review emergency operating procedures and notify ERCOT of any changes or conditions that could affect System Reliability.

ERCOT will continue to monitor the Storm. [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#59 Advisory for Hurricane/Tropical Storm:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an Advisory for the [Tropical Storm/Hurricane] [Name] in the Gulf of Mexico which is currently projected to impact the ERCOT Region. QSEs are instructed to:

- Review fuel supplies and notify ERCOT of any known or anticipated fuel restrictions,

- Review Planned Resource outages and consider delaying maintenance,

- Review emergency operating procedures and notify ERCOT of any changes or conditions that could affect System Reliability.

- Instruct Plant Operators to prepare for projected severe weather conditions and review procedures for operating in the lead due to possible high voltage concerns

- Notify ERCOT if relocating personnel to backup control centers

ERCOT will continue to monitor the Storm [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#60 Watch for Hurricane/Tropical Storm:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing a Watch for [Tropical Storm/Hurricane] [Name] in the Gulf of Mexico which is projected to make landfall near [Place] at [time].   QSEs are instructed to:

- Notify all Resources of conditions

- Review fuel supplies and notify ERCOT of any known or anticipated fuel restrictions,

- Review emergency operating procedures and notify ERCOT of any changes or conditions that could affect System Reliability.

- Make available, any Resources that can be returned to service and keep COPs and HSLs updated

ERCOT will continue to monitor the Storm. [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#61 Emergency Notice for Hurricane/Tropical Storm:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing an Emergency Notice due to [Tropical Storm/Hurricane Name] having an adverse impact on the ERCOT System [specify condition].  QSEs are instructed to:

- Be prepared to reduce Generator output due to anticipated load loss and respond to voltage support issues as requested,

- Keep COPs and HSLs current.

ERCOT will continue to monitor [Tropical Storm/Hurricane Name].  [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#62 OCN for Extreme Cold Weather:

“This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing an OCN for an extreme cold weather system approaching [time frame] with temperatures anticipated to remain 32°F or below.  QSEs are instructed to:

- Review fuel supplies, prepare to preserve fuel to best serve peak load, and notify ERCOT of any known or anticipated fuel restrictions,

- Review Planned Resource outages and consider delaying maintenance or returning from outage early,

- Review and implement winterization procedures. Notify ERCOT of any changes or conditions that could affect system reliability.

[QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#63 Advisory for Extreme Cold Weather:

“This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an Advisory for the extreme cold weather system approaching [time frame] with temperatures anticipated to remain 32°F or below.  QSEs are instructed to:

- Review fuel supplies, preserve fuel to best serve peak load, and notify ERCOT of any known or anticipated fuel restrictions,

- Review Planned Resource outages and consider delaying maintenance or returning from outage early,

- Review and implement winterization procedures.  Notify ERCOT of any changes or conditions that could affect system reliability.

[QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#64 Watch for Extreme Cold Weather:

“This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing a Watch for the extreme cold weather system approaching [time frame]. Temperatures are expected to remain 32°F or below.  QSEs are instructed to:

- Make available, any Resources that can be returned to service and keep COPs and HSLs updated,

- Review fuel supplies, preserve fuel to best serve peak load, and notify ERCOT of any known or anticipated fuel restrictions,

- Prepare for higher than usual loads and the possible need for additional Ancillary Services,

- Review and implement winterization and emergency operating procedures, including utilization of Resource pre-warming techniques.  Notify ERCOT of any changes or conditions that could affect system reliability.

[QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#65 Emergency Notice for Extreme Cold Weather:

“This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing an Emergency Notice, the extreme cold weather system is beginning to have an adverse impact on the system such as [state what the adverse impacts are].  QSEs are instructed to:

- Make Resources available that can be returned to service and keep COPs and HSLs updated,

- Keep ERCOT informed of  known or anticipated fuel restrictions,

- Notify ERCOT of any changes or conditions that could affect system reliability.

ERCOT will continue to monitor the extreme cold weather system. [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#66 OCN for Extreme Hot Weather:

“This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an OCN for the extreme hot weather with forecasted temperatures to be above [103°F or 94°F] in the North Central and South Central weather zones.   QSEs are instructed to:

- Review fuel supplies and notify ERCOT of any known or anticipated fuel restrictions,

- Review Planned Resource outages and consider delaying maintenance,

- Review and implement weatherization and emergency operating procedures and notify ERCOT of any changes or conditions that could affect System Reliability.

ERCOT will continue to monitor the weather system. [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#67 Advisory for Extreme Hot Weather:

“This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an Advisory for the extreme hot weather with forecasted temperatures to be above [103°F or 94°F] in the North Central and South Central weather zones.   QSEs are instructed to:

- Review fuel supplies and notify ERCOT of any known or anticipated fuel restrictions,

- Review Planned Resource outages and consider delaying maintenance,

- Review and implement weatherization and emergency operating procedures and notify ERCOT of any changes or conditions that could affect System Reliability.

ERCOT will continue to monitor the weather system. [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#68 Watch for Extreme Hot Weather:

“This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing a Watch for the extreme hot weather with forecasted temperatures to be above [103°F or 94°F] in the North Central and South Central weather zones [today or tomorrow].  ERCOT is expecting statewide power supplies to be very tight.  QSEs are instructed to:

- Make available any Resources that can be returned to service and keep COPs and HSLs updated,

- Review fuel supplies and notify ERCOT of any known or anticipated fuel restrictions,

- Review and implement weatherization and emergency operating procedures and notify ERCOT of any changes or conditions that could affect System Reliability.

ERCOT will continue to monitor the weather and will convey information and instructions as conditions warrant. [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

## Q#69 Emergency Notice for Extreme Hot Weather:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name].  At [xx:xx], ERCOT is issuing an Emergency Notice, the extreme hot weather system is beginning to have an adverse impact on the ERCOT System such as [state what the adverse impacts are].

- Make Resources available that are able to return to service and keep COPs and HSLs updated

- Review fuel supplies and notify ERCOT of any known or anticipated fuel restrictions,

- Prepare for higher than usual loads and the possibility of deploying Load Resources and/or ERS Resources.

ERCOT will continue to monitor the extreme hot weather system and will convey information and instructions as conditions warrant. [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#70 OCN/Advisory/Watch for other Weather Events:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name].  At [xx:xx], ERCOT is issuing a [OCN/Advisory/Watch] due to [type of weather event] in the [location on the grid].  If you experience any issues as a direct result of the weather event, notify ERCOT.  [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#71 Transmission Emergency for the Rio Grande Valley Area:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back.  This is ERCOT operator [first and last name].  At [xx:xx], ERCOT is issuing a Transmission Emergency for the Rio Grande Valley due to [state issue], this may result in the deployment of Load Resources, curtailment of DC-Tie exports to CENACE, request for emergency energy, and Valley area load shed.” [QSE] please repeat this back to me.

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct

## Q#72 Execute a SASM for Failure to Provide/Infeasibility:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back.  This is ERCOT Operator [first and last name], ERCOT will execute a SASM at [xx:xx] for operating day [xx/xx/xx] for HE [xx-xx] for [type of A/S] MW [X], [X], [X]”.  [QSE] please repeat this back to me.”  If repeat back is CORRECT, “That is correct, thank you.”  If INCORRECT, repeat the process until the repeat back is correct.

## Q#73 Watch to Increase A/S and open SASM:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back.  This is ERCOT Operator [first and last name], at [xx:xx] ERCOT is issuing a Watch due to the need to increase the system wide Ancillary Services requirement above what was procured in the Day-Ahead Market due to [state the reason].  At [xx:xx] ERCOT will open a SASM to procure the additional [type of A/S] Ancillary Services for hours [hours] for operating day [day].  [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#74 Cancel Watch to Increase A/S and SASM complete:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back.  This is ERCOT Operator [first and last name].  The SASM has completed and ERCOT is canceling the Watch for increasing Ancillary Services. [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct

## Q#75 Weekly QSE Hotline test:

“This is ERCOT Operator [first and last name].  ERCOT is conducting the weekly QSE Hotline test.  ERCOT is currently at NTAS Advisory level [state advisory level].  The following notices are currently in effect:

- List OCNs, Advisories, Watches and/or Emergency Notices in effect.

- State “None” if none are in effect.

This ends the test of the ERCOT Hotline.  That is all.”

## Q#76 Application issues:

“This is ERCOT Operator [first and last name].  This is a courtesy call to inform you that ERCOT is experiencing application problems which is causing QSEs issues with submittals.

## Q#77 Watch for projected reserve capacity shortage and RMR Resources have been committed:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name].  At [xx:xx], ERCOT is issuing a Watch for a projected reserve capacity shortage with no market solution available.  HRUC recommended RMR Resources have been committed.  [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#78 Cancel Watch for projected reserve capacity shortage:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name].  At [xx:xx], ERCOT is canceling the Watch for a projected reserve capacity shortage with no market solution available.  [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#79 Watch for HRUC failure/timeline deviation:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back.  This is ERCOT Operator [first and last name].  At [xx:xx], ERCOT is issuing a Watch due to HRUC not completing for [state HE] due to [failure or timeline deviation].  [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#80 Cancel Watch for HRUC failure/timeline deviation:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back.  This is ERCOT operator [first and last name].  At, [xx:xx], ERCOT is canceling the Watch for HRUC not completing for [state HE].  [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#81 Watch for insufficient A/S:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back.  This is ERCOT Operator [first and last name], at [xx:xx] ERCOT is issuing a Watch due to insufficient A/S offers; [HRUC/Assignments] will be used to commit the remaining A/S insufficiencies.  [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#82 Cancel Watch for insufficient A/S:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back.  This is ERCOT operator [first and last name].  At, [xx:xx], ERCOT is canceling the Watch due to insufficient A/S offers.  [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#83 Watch for projected reserve capacity shortage with no market solution:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name].  At [xx:xx], ERCOT is issuing a Watch for a projected reserve capacity shortage with no market solution available for [HE XX – XX], which causes a high risk for an EEA event.  [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#84 Cancel Watch for projected reserve capacity shortage with no market solution:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name].  At [xx:xx], ERCOT is cancelling the Watch for a projected reserve capacity shortage with no market solution available for [HE XX – XX].  [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#85 Watch for A/S insufficiency in DAM, procuring in DRUC:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back.  This is ERCOT Operator [first and last name], at [xx:xx] ERCOT is issuing a Watch due to A/S insufficiency in DAM for operating day [day].  The A/S insufficiencies will be procured in DRUC.  [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#86 Cancel Watch for A/S insufficiency in DAM:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name].  At [xx:xx], ERCOT is cancelling the Watch due to A/S insufficiency in DAM for operating day [day].  A/S insufficiencies were procured in DRUC.  [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#87 OCN for Excess Capacity:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back.  This is ERCOT Operator [first and last name].  At [xx:xx], ERCOT is issuing an OCN for [date] due to a projected excess reserve capacity for [HE XX – HE XX]. [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#88 Cancel OCN for Excess Capacity:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name].  At [xx:xx], ERCOT is cancelling the OCN for [date] due to a projected excess reserve capacity for [HE XX – HE XX].  [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#89 OCN for committing capacity in DRUC:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back.  This is ERCOT Operator [first and last name], at [xx:xx], ERCOT is issuing an OCN for [date] for a projected Reserve Capacity Shortage for [HE XX to HE XX].  ERCOT will commit Resources as needed.  [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#90 Cancellation for OCN for committing capacity in DRUC:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name].  At [xx:xx], ERCOT is cancelling the OCN for [date] due to a projected reserve capacity for [HE XX – HE XX].  [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#91 Advisory for DAM Timeline Deviation:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back.  This is ERCOT Operator [first and last name], at [xx:xx], ERCOT is issuing an Advisory for the timeline deviation of the Day Ahead Market; the start of DRUC will be delayed, until further notice.  [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#92 Cancel Advisory for DAM Timeline Deviation:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back.  This is ERCOT Operator [first and last name].  At [xx:xx], ERCOT is canceling the Advisory for the delay of DAM.  DAM is now complete; DRUC will begin at [time]. [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#93 Advisory for DRUC Delay:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back.  This is ERCOT Operator [first and last name], at [xx:xx], ERCOT is issuing an Advisory for the timeline deviation of DRUC for [effected date] due to [state issue].  ERCOT will continue to try to complete DRUC by 18:00.  [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#94 Cancel Advisory for DRUC Delay:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back.  This is ERCOT Operator [first and last name], at [xx:xx], ERCOT is canceling the Advisory for the timeline deviation of DRUC.  DRUC completed at [time].  [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#95 Watch for DRUC not complete by 18:00:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back.  This is ERCOT Operator [first and last name], at [xx:xx], ERCOT is issuing a Watch due to DRUC not completing by 1800 due to [state reason].  [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#96 Cancel Watch for DRUC not complete by 18:00:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name].  At [xx:xx], ERCOT is cancelling the Watch due to DRUC not completing by 1800.  ERCOT will procure in HRUC if needed.  [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#97 Watch for Insufficient A/S in DAM, requesting Additional Offers:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back.  This is ERCOT Operator [first and last name], at [xx:xx] ERCOT is issuing a Watch due to insufficient Ancillary Service offers in the Day Ahead Market.  ERCOT is requesting additional Ancillary Service Offers for [Up/Down Regulation, Responsive Reserve, Non-Spin].  DAM will run again in 30 minutes.  [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#98 Cancel Watch, DAM completed with A/S:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back.  This is ERCOT Operator [first and last name], at [xx:xx] ERCOT is canceling the Watch for insufficient Ancillary Services offers in the Day Ahead Market.  Sufficient offers were received.  [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#99 Cancel Watch for Insufficient A/S:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back.  This is ERCOT Operator [first and last name], at [xx:xx] ERCOT is canceling the Watch for insufficient Ancillary Services offers in the Day Ahead Market.  A/S was covered through DRUC.  [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#100 Watch for DAM Failure:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back.  This is ERCOT Operator [first and last name], at [xx:xx] ERCOT is issuing a Watch due to the Day Ahead Market being aborted for [effected date] due to [state issue].  At [xx:xx] ERCOT will open a SASM to procure Ancillary Services for tomorrow’s operating day.  MPs update or submit new AS offers that may have expired for SASM and Self AS.  [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#101 Cancel Watch for DAM Failure:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back.  This is ERCOT Operator [first and last name], at [xx:xx] ERCOT is canceling the Watch for the failure of the Day Ahead Market for [effected date].  All Ancillary Services have been procured for tomorrow’s operating day.  [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#102 Blank:

## Q#103 EEA 3 PRC <1375 Without Firm Load Shed:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back.  This is ERCOT Operator [first and last name], at [xx:xx], ERCOT is declaring EEA3 due to Physical Responsive Capability falling below 1375 MW.  Firm load shed is not being requested at this time.  Implement all measures associated with EEA 1 and 2, if not already implemented. [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#104 Transmission Watch for the Rio Grande Valley Import:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back.  This is ERCOT operator [first and last name].  At [xx:xx], ERCOT is issuing a Transmission Watch for the Rio Grande Valley due to the Rio Grande Valley Import, this may result in the curtailment of DC-Tie exports to CENACE.” [QSE] please repeat this back to me.

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct

## Q#105 Cancel Transmission Watch for Rio Grande Valley Import:

“This is ERCOT Operator [first and last name].  At [xx:xx], ERCOT is canceling the Transmission Watch for the Rio Grande Valley Import.  [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#106 Emergency Notice Loss of Primary Control Center (Systems are Functional):

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]; at [xx:xx], ERCOT is issuing an Emergency Notice due to the loss of primary control center and is transferring operations to the alternate control center.  Direct all urgent phone calls thru the [Bastrop][Taylor] OPX.  All ERCOT systems are functioning at this time.  HRUC will be delayed until additional staffing arrives.  If you represent a Nuclear Plant, please inform them that RTCA results will not be viewed in a timely manner and is expected to last for approximately 1 hour.” [Select QSE], “Please repeat this back for me.”

- If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#107 Emergency Notice Loss of Primary Control Center (Systems are NOT Functional):

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]; at [xx:xx], ERCOT is issuing an Emergency Notice due to loss of primary control center functionality, LFC and SCED failure.  ERCOT has put a QSE on constant frequency.  All remaining QSEs should hold their Resources to their current output level until instructed by ERCOT.  ERCOT may issue unit specific deployments to any Resources as required. Direct all urgent phone calls thru the [Bastrop][Taylor] OPX. [Select QSE].  If you represent a Nuclear Plant, please inform them that RTCA and State Estimator are not functioning and are expected to last approximately 2 hour. “Please repeat this back for me.”

- If repeat back is CORRECT, “That is correct, thank you.”

- If INCORRECT, repeat the entire process until the repeat back is correct.

## Q#108 ERCOT’s ICCP, MIS, or the Outage Scheduler Planned or Unplanned Outage:

- “This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back.  This is ERCOT operator [first and last name], at [xx:xx], ERCOT is notifing QSEs that ERCOT’s [ICCP, MIS, or Outage Scheduler] has a [planned / unplanned] outage that is expected to last 30 minutes or more.

- [QSE] please repeat that back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#109 ERCOT’s ICCP, MIS or Outage Scheduler back to Normal:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back.  This is ERCOT operator [first and last name], at [xx:xx], ERCOT is notifing QSEs that ERCOT’s [ICCP, MIS or Outage Scheduler] is now functional.  [QSE] please repeat that back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#110 OCN for Projected Reserve Capacity Shortage:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back.  This is ERCOT Operator [first and last name].  At [xx:xx], ERCOT is issuing an OCN for [date] for a projected Reserve Capacity Shortage for [HE XX to HE XX].  ERCOT may and will commit Resources as needed”.  [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#111 Cancel OCN for Projected Reserve Capacity Shortage:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back.  This is ERCOT operator [first and last name].  At, [xx:xx], ERCOT is canceling the OCN for [date] for a projected Reserve Capacity Shortage for [HE XX to HE XX]”.  [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#112 Instruct a QSE on Constant Frequency for LFC Failure:

“This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is instructing you to go on constant frequency control until further notice due to an LFC failure.  The frequency bias to enter into your control system is [bias].  Please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#113 Instruct QSE to End  Constant Frequency for LFC Functioning:

“This is ERCOT Operator [first and last name]. At [xx:xx], LFC is now functioning,  end constant frequency control and return to normal.  Please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#114 Instruct a QSE on Constant Frequency for LFC/SCED Failure:

“This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is Instructing you to go on constant frequency control until further notice due to an LFC and SCED failure.  The frequency bias to enter into your control system is [bias].  Please repeat this back to me.

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#115 Instruct a QSE to end Constant Frequency for LFC/SCED Functioning:

“This is ERCOT Operator [first and last name]. At [xx:xx], LFC and SCED is now functioning, ERCOT is instructing you to end constant frequency control.  Please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#116 Start Constant Frequency Control Test:

“This is ERCOT operator [first and last name]. At [time], ERCOT is conducting an unannounced constant frequency control test with [QSE].  The frequency bias to enter into your control system is [bias].  The test will be up to 15 minutes.  I will give another call when you can return to normal operation.  [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#117 End Constant Frequency Control Test:

“This is ERCOT operator [first and last name]. At [time], ERCOT is ending the unannounced constant frequency control test with [QSE]; please remove the bias and change your control mode back to normal.  I will follow-up with an electronic Dispatch Instruction confirmation that you will need to acknowledge.  [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#118 QSE on Constant Frequency Control for Unannounced Constant Frequency Control Test:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is conducting an unannounced Constant Frequency Control test and will place a QSE on Constant Frequency Control. [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#119 Cancel QSE on Constant Frequency Control for Unannounced Constant Frequency Control Test:

“This call requires everyone to remain on the line until it is complete.  [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT has ended the unannounced Constant Frequency Control test. [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#120 Perform Unannounced Unit Test:

“This is ERCOT operator [first and last name]. ERCOT is issuing a VDI at [time] to perform an Unannounced Unit Test on [Resource name].  Release all Ancillary Service obligations carried by the unit, change the Resource status to “ONTEST” and increase the Resource output to the current telemetered HSL of XXX MW.  The Resource will have [XXX] minutes to reach the telemetered HSL.  Once the Resource has met the time requirement or reached its HSL, HOLD the Resource at its HSL or above for at least 30 minutes.  [QSE] please repeat this back to me.

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#121 End Unannounced Unit Test:

“This is ERCOT operator [first and last name]. At [time], ERCOT is ending the unannounced test on [Resource name], please return to normal operation.  I will be sending you the electronic Dispatch Instruction that you will need to acknowledge.  Submit the results from the test on the NDCRC within 2 business days.  [QSE] please repeat this back to me.

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#122 ERCOT requests SWGR:

“This is ERCOT Operator [first and last name].  At [xx:xx], ERCOT declared [EEA 1 / anticipated Emergency Condition]. ERCOT has coordinated with [RC region] for [specific SWGR] to be released for operations into ERCOT.  ERCOT is issuing an Operating Instruction to initiate the switch and start [specific SWGR] into ERCOT.  ERCOT will issue an electronic Dispatch Instruction to commit the Resource.  [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#123 SPP or MISO requests SWGR:

“This is ERCOT Operator [first and last name].  At [xx:xx], [RC region] declared [EEA 1/anticipated Emergency Condition]. [RC region] has coordinated with ERCOT for [specific SWGR] to be released for operations into [RC region].  ERCOT is issuing an Operating Instruction for [specific SWGR] to coordinate with [RC region] to mitigate the Emergency Condition.  [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## Q#124 Notification to QSE of  Release:

“This is ERCOT Operator [first and last name].  At [xx:xx], [RC region]

has requested release of [specific SWGR] to address an existing or anticipated Emergency Condition. The SWGR is now under the operational control of the [RC region].”  ERCOT is issuing an Operating Instruction for [specific SWGR] to coordinate with [RC region] to mitigate the Emergency Condition.  [QSE] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

### Typical Scripts for TOs

## T#1 Advisory for PRC <3000 MW:

“This call requires everyone to remain on the line until it is complete.  [TO] I will be asking you for the repeat back.  This is ERCOT Operator [first and last name].  At [xx:xx], ERCOT is issuing an Advisory due to Physical Responsive Capability falling below 3000 MW.  [TO] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## T#2 Cancel Advisory for PRC <3000 MW:

“This is ERCOT Operator [first and last name].  At [xx:xx], ERCOT is canceling the Advisory for Physical Responsive Capability.  Physical Responsive Capability is now above 3000 MW.  [TO] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## T#3 Watch for PRC <2500 MW:

“This is ERCOT Operator [first and last name].  At [xx:xx], ERCOT is issuing a Watch due to Physical Responsive Capability falling below 2500 MW.  [TO] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## T#4 Cancel Watch for PRC <2500 MW:

“This is ERCOT Operator [first and last name].  At, [xx:xx], ERCOT is canceling the Watch for Physical Responsive Capability.  At this time, the Advisory is still in effect.   [TO] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## T#5 EEA1:

“This call requires everyone to remain on the line until it is complete.  [TO] I will be asking you for the repeat back.  This is ERCOT Operator [first and last name]; at [xx:xx], ERCOT is declaring EEA 1. [TO] please repeat this back to me.  That is correct, thank you”

## T#6 EEA2 Deploy Load Management Program:

“This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back.  This is ERCOT Operator [first and last name]; This call applies to the following Transmission Operators:  AEP, CenterPoint, Oncor and TNMP.  At [xx:xx], ERCOT is requesting that these TOs deploy all available capacity from their Load Management Programs due to continued increased load growth.

[TO] please repeat this back to me.  That is correct, thank you.”

## T#7 EEA2 Media Appeal and Voltage Reduction:

“This call requires everyone to remain on the line until it is complete.  [TO] I will be asking you for the repeat back.  This is ERCOT Operator [first and last name], at [xx:xx], ERCOT is declaring EEA 2 and is issuing an appeal through the public news media for voluntary energy conservation.  Reduce customer loads by using distribution voltage reduction measures, if deemed beneficial and any available capacity from Load Management Programs, [Load Resources and / or ERS have been deployed].

[TO] please repeat this back to me.  That is correct, thank you”

## T#8 EEA3 Firm Load Shed:

“This call requires everyone to remain on the line until it is complete.  [TO] I will be asking you for the repeat back.  This is ERCOT Operator [first and last name], at [xx:xx], ERCOT is declaring EEA 3 firm load shed.  ERCOT is issuing an Operating Instruction for all Transmission Operators to shed their share of [amount] MW.  Transmission Operators are to report to ERCOT when this is complete.  Implement all measures associated with EEA 1 and 2, if not already implemented. [TO] please repeat this back to me.  That is correct, thank you”.

## T#9 EEA3 Restore a Portion of Firm Load:

“This call requires everyone to remain on the line until it is complete.  [TO] I will be asking you for the repeat back.  This is ERCOT Operator [first and last name], “at [xx:xx], ERCOT is issuing an Operating Instruction for all Transmission Operators to restore their share of [amount] MW leaving [amount] MW still off.  Report to ERCOT when this task is complete.  [TO] please repeat this back to me.  “That is correct, thank you.”

## T#10 EEA3/BAAL Restore All Firm Load:

“This call requires everyone to remain on the line until it is complete.  [TO] I will be asking you for the repeat back.  This is ERCOT Operator [first and last name], “at [xx:xx], ERCOT is issuing an Operating Instruction for all Transmission Operators to restore all firm load.  Report to ERCOT when this task is complete.  [TO] please repeat this back to me.  “That is correct, thank you.”

## T#11 Moving from EEA3 to EEA2:

“This call requires everyone to remain on the line until it is complete.  [TO] I will be asking you for the repeat back.  This is ERCOT Operator [first and last name].  At [xx:xx], ERCOT is moving from EEA 3 to EEA 2.  Load Resources are being recalled.  [TO] please repeat this back to me.  “That is correct, thank you.”

## T#12 Moving from EEA2 to EEA1:

“This call requires everyone to remain on the line until it is complete.  [TO] I will be asking you for the repeat back.  This is ERCOT Operator [first and last name].  At [xx:xx], ERCOT is moving from EEA 2 to EEA 1, [Load Resources and/or ERS Resources] are being restored. Distribution voltage measures can be returned to normal, if used, *as well as Load Management Programs.  [TO] please repeat this back to me.  That is correct, thank you.”

## T#13 Terminate EEA1:

“This call requires everyone to remain on the line until it is complete.  [TO] I will be asking you for the repeat back.  This is ERCOT Operator [first and last name].  At [xx:xx], ERCOT is terminating EEA 1, a Watch still remains in effect.  [TO] please repeat this back to me.  “That is correct, thank you.”

## T#14 Cancel Watch for PRC<2500 MW:

“This is ERCOT Operator [first and last name].  At [xx:xx], ERCOT is canceling the Watch for Physical Responsive Capability.  Physical Responsive Capability is now above 2800 MW.  [TO] please repeat this back to me.  That is correct, thank you.”

## T#15 EMS Changes:

“This is ERCOT operator [first and last name], at [xx:xx], ERCOT will perform a [database load] [local failover] [EMS migration] on its Energy & [Market] Management System(s).   In the event ICCP is temporarily suspended, all systems should re-establish automatically within a few minutes.  Any questions?”

## T#16 MMS Changes:

“This is ERCOT operator [first and last name], at [xx:xx], ERCOT will perform a [migration] [patch] on its Market Management System.  [We do not expect to miss a SCED run] [Emergency basepoints may be issued during this time].  ERCOT will make another hotline call when the work is completed.  Any questions?”

## T#17 Site Failover:

“This is ERCOT operator [first and last name], at [xx:xx], ERCOT will perform a site failover of its Energy & Market Management Systems.  During this time, market communications will be unavailable for about 20 minutes, and real-time communications will be unavailable for about 5 minutes.  All systems should re-establish communications automatically.  Any questions?”

## T#18 Site Failover Complete:

“This is ERCOT operator [first and last name].  At [xx:xx], the [site failover] [patch] [migration] is complete.  Thank you.”

## T#19 Working from Alternate Site:

“This call requires everyone to remain on the line until it is complete.  [TO] I will be asking you for the repeat back.  This is ERCOT operator [first and last name], at [xx:xx], ERCOT will be working from the alternate control center until further notice, use the OPX numbers for Bastrop.  [TO] please repeat that back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## T#20 Working from Primary Site:

“This call requires everyone to remain on the line until it is complete.  [TO] I will be asking you for the repeat back.  This is ERCOT operator [first and last name], at [xx:xx], ERCOT will be working from the primary control center until further notice, use the OPX numbers for Taylor.  [TO] please repeat that back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## T#21 Advisory for State Estimator/RTCA Not Solved:

- “This call requires everyone to remain on the line until it is complete.  [TO] I will be asking you for the repeat back.  This is ERCOT operator [first and last name], at [xx:xx], ERCOT is issuing an Advisory due to ERCOTs [State Estimator/RTCA] has not solved in the last 30 minutes.

- Please monitor your own service area and notify ERCOT if you exceed the normal ratings of your transmission elements.  Report if power flows on any GTCs reach 85% of their respective limits, suspend any new planned outages, and notify ERCOT of any forced line operations.

- [TO] please repeat that back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## T#22 Cancel Advisory for State Estimator/RTCA:

“This call requires everyone to remain on the line until it is complete.  [TO] I will be asking you for the repeat back.  This is ERCOT operator [first and last name], at [xx:xx], ERCOT is canceling the Advisory for [State Estimator/RTCA], ERCOTs [State Estimator/RTCA] is now functional.  You may return to normal operations.  [TO] please repeat that back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## T#23 Advisory for VSAT Tool Not Solved:

“This call requires everyone to remain on the line until it is complete.  [TO] I will be asking you for the repeat back.  This is ERCOT Operator [first and last name], at [xx:xx],  ERCOT is issuing an Advisory due to ERCOTs Voltage Security Assessment Tool has not solved in the last 30 minutes.  We will be monitoring the GTC flows to the last posted limits. Please notify us if there is a topology change that could affect these interfaces. Notify ERCOT if you have reactive reserve issues within your system.  Suspend any new planned outages.

[TO] please repeat this back to me. ”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## T#24 Cancel Advisory for VSAT Tool:

“This call requires everyone to remain on the line until it is complete.  [TO] I will be asking you for the repeat back.  This is ERCOT operator [first and last name], at [xx:xx], ERCOT is canceling the Advisory for VSAT Tool, ERCOTs VSAT tool is now functional.  [TO] please repeat that back for me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## T#25 Advisory for GMD Alert:

“This call requires everyone to remain on the line until it is complete.  [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an Advisory for a [state K-Index level] geomagnetic disturbance alert that has been issued from [date/hours].  ERCOT is instructing you to increase your situational awareness in the following areas:

- Monitor reactive reserves

- Monitor for unusual voltage and MVAR swings

- Monitor abnormal temperatures or gas in transformers

- Prepare for possible false SCADA/EMS indications if telecommunications systems are disrupted

Report to ERCOT if you suspect any issues due to a GMD.  The most current space weather information can be located at the NOAA Space Weather Information Site.

[TO] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## T#26 GMD K-Index Level Increase/Decrease:

“This call requires everyone to remain on the line until it is complete.  [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], The [state K-Index level] geomagnetic disturbance storm alert that we are currently under has [increase/decreased] to a [state K-Index level] until [date/hours].  ERCOT is reminding you to continue with your situational awareness in the following areas:

- Monitor reactive reserves

- Monitor for unusual voltage and MVAR swings

- Monitor abnormal temperatures or gas in transformers

- Prepare for possible false SCADA/EMS indications if telecommunications systems are disrupted

Report to ERCOT if you suspect any issues due to a GMD.  The most current space weather information can be located at the NOAA Space Weather Information Site.

[TO] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## T#27 Cancel Advisory for GMD:

“This call requires everyone to remain on the line until it is complete.  [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is canceling the Advisory for the geomagnetic disturbance.  [TO] please repeat this back to me.  ”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## T#28 Emergency Notice for instructing Qualifying Facility to operate offline/below LSL:

“This call requires everyone to remain on the line until it is complete.  [TO] I will be asking you for the repeat back.  This is ERCOT Operator [first and last name].  At [xx:xx], ERCOT is issuing an Emergency Notice due to  instructing a Qualifying Facility [offline or operate below its LSL].  [TO] please repeat this back to me.

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## T#29 Transmission Emergency for the Rio Grande Valley Area:

“This call requires everyone to remain on the line until it is complete.  [TO] I will be asking you for the repeat back.  This is ERCOT operator [first and last name].  At [xx:xx], ERCOT is issuing a Transmission Emergency for the Rio Grande Valley due to [state issue], this may result in the deployment of Load Resources, curtailment of DC-Tie exports to CENACE, request for emergency energy, and Valley area load shed.” [TO] please repeat this back to me.

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct

## T#30 Transmission Emergency for Cascading Condition:

“This is ERCOT Operator [first and last name].  At [xx:xx], ERCOT is issuing a Transmission Emergency due to an expected cascading condition in the [general location] which is [TOs] service area.  Load will be shed to correct this condition.  [TO] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## T#31 Watch for North to Houston Interface:

“This is ERCOT operator [first and last name].  At [xx:xx], ERCOT is issuing a Watch for the North-Houston interface.  Non-Spin is being deployed in the Houston area to help mitigate the issue.  [TO] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## T#32 Emergency Notice for North to Houston Interface:

“This is ERCOT operator [first and last name].  At [xx:xx], ERCOT is issuing an Emergency Notice for the North-Houston interface.  Load Resources in the Houston area are being deployed to help mitigate the issue.  [TO] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## T#33 Emergency Notice for North to Houston Interface, Firm Load Shed:

“At [xx:xx], ERCOT is continuing the Transmission Emergency Notice for the North-Houston interface.  [*** MW] of Firm Load is being shed in the Houston area to help mitigate the issue.  [TO] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## T#34 Transmission Watch for Post-Contingency Overload:

“This is ERCOT Operator [first and last name].  At [xx:xx], ERCOT is issuing a Transmission Watch due to the post-contingency overload of [constraint name] a [mitigation plan/temporary outage action plan] is being developed.  [TO] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## T#35 Cancel Transmission Watch for Post-Contingency Overload:

“This is ERCOT Operator [first and last name].  At [xx:xx], ERCOT is canceling the Transmission Watch for post-contingency overload of [constraint name] a [mitigation plan/temporary outage action plan] has been developed.  [TO] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## T#36 OCN for Generic Transmission Constraint:

“This is ERCOT Operator [first and last name].  At [xx:xx], ERCOT is issuing an OCN to make notification of a new Generic Transmission Constraint.  A forced outage on [state forced outage] resulted in a GTC being created for [state reason for GTC].  [TO] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## T#37 Operating Condition [OCN/Advisory/Watch/Emergency]:

“This call requires everyone to remain on the line until it is complete.  [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name].  At [xx:xx], ERCOT is issuing a [state Notice type] for [state reason].  [TO] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## T#38 Cancel Operating Condition [OCN/Advisory/Watch/Emergency]:

“This call requires everyone to remain on the line until it is complete.  [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name].  At [xx:xx], ERCOT is cancelling the [state Notice type] for [state reason].  [TO] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## T#39 Blank

## T#40 Blank

## T#41 Watch for SCED/RLC Failure:

“This call requires everyone to remain on the line until it is complete.  [TO] I will be asking you for the repeat back.  This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing a Watch due to the failure of SCED.  ERCOT may issue Emergency Base Points until the issue is resolved.  Suspend any new planned outages”. [TO] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## T#42 Cancel Watch for SCED/RLC Failure:

“This call requires everyone to remain on the line until it is complete.  [TO] I will be asking you for the repeat back.  This is ERCOT operator [first and last name]. At [xx:xx], SCED base points are now valid and ERCOT is canceling the Watch”.  [TO] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## T#43 Emergency Notice for LFC/EMS and SCED Failure:

“This call requires everyone to remain on the line until it is complete.  [TO] I will be asking you for the repeat back.  This is ERCOT Operator [first and last name].  At [xx:xx], ERCOT is issuing an Emergency Notice due to an [LFC/EMS] and SCED failure. ERCOT has placed [Name] QSE on Constant Frequency.  Please monitor your own service area and notify ERCOT if you exceed the normal ratings of your transmission elements.  Report if power flows reach 85% of their respective limits, suspend any new planned outages and notify ERCOT of any forced line operations”.  [TO] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## T#44 Cancel Emergency Notice for LFC Functioning, SCED valid:

“This call requires everyone to remain on the line until it is complete.  [TO] I will be asking you for the repeat back.  This is ERCOT operator [first and last name].  At, [xx:xx], [LFC/EMS] is now functional and SCED solutions are valid.  ERCOT is canceling the Emergency Notice”.  [TO] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## T#45 Watch to Increase Ancillary Services and Open SASM:

“This call requires everyone to remain on the line until it is complete.  [TO] I will be asking you for the repeat back.  This is ERCOT Operator [first and last name].  At [xx:xx], ERCOT is issuing a Watch due to the need to increase the system wide Ancillary Services (A/S) requirement above what was procured in the Day-Ahead Market due to [state the reason].  ERCOT will open a Supplemental Ancillary Service Market (SASM) to procure the additional A/S for hours [hours] for operating day [date]”.  [TO] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## T#46 Cancel Watch to Increase Ancillary Services:

This call requires everyone to remain on the line until it is complete.  [TO] I will be asking you for the repeat back.  This is ERCOT operator [first and last name].  At, [xx:xx], ERCOT is canceling the Watch for increasing the system wide A/S requirement”.  [TO] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## T#47 Watch for Insufficient A/S Offers in DAM:

“This call requires everyone to remain on the line until it is complete.  [TO] I will be asking you for the repeat back.  This is ERCOT Operator [first and last name].  At [xx:xx], ERCOT is issuing a Watch due to an insufficiency in A/S offers in the Day Ahead Market.  Currently, ERCOT is requesting additional A/S Offers from QSEs”.  [TO] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## T#48 Cancel Watch for Insufficient A/S Offers in DAM:

“This call requires everyone to remain on the line until it is complete.  [TO] I will be asking you for the repeat back.  This is ERCOT operator [first and last name].  At, [xx:xx], ERCOT is canceling the Watch for insufficient A/S offers in the Day Ahead Market.  Sufficient offers have been received”.  [TO] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

OR:

“This call requires everyone to remain on the line until it is complete.  [TO] I will be asking you for the repeat back.  This is ERCOT operator [first and last name].  At, [xx:xx], ERCOT is canceling the Watch for insufficient A/S offers in the Day Ahead Market.  A/S were covered through DRUC”.  [TO] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## T#49 Watch for insufficiency of A/S in DAM:

“This call requires everyone to remain on the line until it is complete.  [TO] I will be asking you for the repeat back.  This is ERCOT Operator [first and last name].  At [xx:xx], ERCOT is issuing a Watch due to A/S insufficiency in DAM for operating day [day].  The A/S insufficiencies will be procured in DRUC”.  [TO] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## T#50 – Cancel Watch for insufficiency of A/S in DAM:

“This call requires everyone to remain on the line until it is complete.  [TO] I will be asking you for the repeat back.  This is ERCOT operator [first and last name].  At, [xx:xx], ERCOT is canceling the Watch due to A/S insufficiency in DAM”.  [TO] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## T#51 Watch for Insufficient A/S Offers:

“This call requires everyone to remain on the line until it is complete.  [TO] I will be asking you for the repeat back.  This is ERCOT Operator [first and last name].  At [xx:xx], ERCOT is issuing a Watch due insufficient A/S offers; [HRUC/Assignments] will be used to commit the remaining A/S insufficiencies”.  [TO] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## T#52 Cancel Watch for Insufficient A/S Offers:

“This call requires everyone to remain on the line until it is complete.  [TO] I will be asking you for the repeat back.  This is ERCOT operator [first and last name].  At, [xx:xx], ERCOT is canceling the Watch due insufficient A/S offers”.  [TO] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## T#53 Advisory for DAM Timeline Deviation:

“This call requires everyone to remain on the line until it is complete.  [TO] I will be asking you for the repeat back.  This is ERCOT Operator [first and last name].  At [xx:xx], ERCOT is issuing an Advisory for the timeline deviation of the Day Ahead Market; the start of DRUC will be delayed”.

## T#54 Cancel Advisory for DAM Timeline Deviation:

“This is ERCOT operator [first and last name].  At, [xx:xx], ERCOT is canceling the Advisory for the delay of DAM.  DAM is now complete”.  [TO] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## T#55 Watch for DAM Failure:

“This call requires everyone to remain on the line until it is complete.  [TO] I will be asking you for the repeat back.  This is ERCOT Operator [first and last name].  At [xx:xx], ERCOT is issuing a Watch due to the failure of the Day Ahead Market for [effected date] due to [state issue].  ERCOT will open a SASM to procure Ancillary Services for tomorrow’s operating day”. [TO] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## T#56 Cancel Watch for DAM Failure:

“This call requires everyone to remain on the line until it is complete.  [TO] I will be asking you for the repeat back.  This is ERCOT operator [first and last name].  At, [xx:xx], ERCOT is canceling the Emergency Notice for the failure of the Day Ahead Market for [effected date].  All Ancillary Services have been procured for tomorrow’s operating day”.  [TO] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## T#57 Advisory for DRUC Timeline Deviation:

“This call requires everyone to remain on the line until it is complete.  [TO] I will be asking you for the repeat back.  This is ERCOT Operator [first and last name].  At [xx:xx], ERCOT is issuing an Advisory for the timeline deviation of DRUC for [effected date] due to [state issue].  ERCOT will continue to try to complete DRUC by 18:00”.  [TO] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct

## T#58 Cancel Advisory for DRUC Timeline Deviation:

“This call requires everyone to remain on the line until it is complete.  [TO] I will be asking you for the repeat back.  This is ERCOT operator [first and last name].  At, [xx:xx], ERCOT is canceling the Advisory for the timeline deviation of DRUC.  DRUC completed at [time]”.  [TO] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## T#59 Watch for DRUC not completing by 18:00:

“This call requires everyone to remain on the line until it is complete.  [TO] I will be asking you for the repeat back.  This is ERCOT Operator [first and last name].  At [xx:xx], ERCOT is issuing a Watch due to DRUC not completing by 1800 due to [state reason]”.  [TO] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## T#60 Cancel Watch for DRUC not completing by 18:00:

“This call requires everyone to remain on the line until it is complete.  [TO] I will be asking you for the repeat back.  This is ERCOT operator [first and last name].  At, [xx:xx], ERCOT is canceling the Watch due to DRUC not completing by 1800 due to [state reason].  ERCOT will procure in HRUC if needed”.  [TO] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## T#61 Watch for HRUC Failure / Timeline Deviation:

“This call requires everyone to remain on the line until it is complete.  [TO] I will be asking you for the repeat back.  This is ERCOT Operator [first and last name].  At [xx:xx], ERCOT is issuing an Watch due to HRUC not completing for [state HE] due to [failure or timeline deviation]”.  [TO] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## T#62 Cancel Watch for HRUC Failure / Timeline Deviation:

“This call requires everyone to remain on the line until it is complete.  [TO] I will be asking you for the repeat back.  This is ERCOT operator [first and last name].  At, [xx:xx], ERCOT is canceling the Watch due to HRUC not completing for [state HE]”.  [TO] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## T#63 OCN for Projected Reserve Capacity Shortage:

“This call requires everyone to remain on the line until it is complete.  [TO] I will be asking you for the repeat back.  This is ERCOT Operator [first and last name].  At [xx:xx], ERCOT is issuing an OCN for [date] for a projected Reserve Capacity Shortage for [HE XX to HE XX].  ERCOT may and will commit Resources as needed”.  [TO] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## T#64 Cancel OCN for Projected Reserve Capacity Shortage:

“This call requires everyone to remain on the line until it is complete.  [TO] I will be asking you for the repeat back.  This is ERCOT operator [first and last name].  At, [xx:xx], ERCOT is canceling the OCN for [date] for a projected Reserve Capacity Shortage for [HE XX to HE XX]”.  [TO] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## T#65 OCN for Projected Excess Reserve Capacity:

“This call requires everyone to remain on the line until it is complete.  [TO] I will be asking you for the repeat back.  This is ERCOT Operator [first and last name].  At [xx:xx], ERCOT is issuing an OCN for [date] due to a projected excess reserve capacity for [HE XX – HE XX]”.  [TO] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## T#66 Cancel OCN for Projected Excess Reserve Capacity:

“This call requires everyone to remain on the line until it is complete.  [TO] I will be asking you for the repeat back.  This is ERCOT operator [first and last name].  At, [xx:xx], ERCOT is canceling the OCN for [date] due to a projected excess reserve capacity for [HE XX – HE XX]”.  [TO] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## T#67 Watch for Projected Reserve Capacity Shortage with No Market Solution:

“This call requires everyone to remain on the line until it is complete.  [TO] I will be asking you for the repeat back.  This is ERCOT operator [first and last name].  At [xx:xx], ERCOT is issuing a Watch for a projected reserve capacity shortage with no market solution available for [HE XX – XX], which causes a high risk for an EEA event”.  [TO] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## T#68 Cancel Watch for Projected Reserve Capacity Shortage with No Market Solution:

“This call requires everyone to remain on the line until it is complete.  [TO] I will be asking you for the repeat back.  This is ERCOT operator [first and last name].  At, [xx:xx], ERCOT is canceling the Watch for a projected reserve capacity shortage with no market solution available for [HE XX – XX]”.  [TO] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## T#69 Watch for Projected Reserve Capacity Shortage with No Market Solution, RMR recommended:

“This call requires everyone to remain on the line until it is complete.  [TO] I will be asking you for the repeat back.  This is ERCOT operator [first and last name].  At [xx:xx], ERCOT is issuing a Watch for a projected reserve capacity shortage with no market solution available.  HRUC recommended RMR Resources have been committed”.  [TO] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## T#70 Cancel Watch for Projected Reserve Capacity Shortage with No Market Solution, RMR recommended:

“This call requires everyone to remain on the line until it is complete.  [TO] I will be asking you for the repeat back.  This is ERCOT operator [first and last name].  At, [xx:xx], ERCOT is canceling the Watch for a RMR projected reserve capacity shortage with no market solution available”.  [TO] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## T#71 Cancel Emergency Notice and Restore Primary Control Center:

- “This call requires everyone to remain on the line until it is complete.  [TO] I will be asking you for the repeat back.  This is ERCOT operator [first and last name]; at [xx:xx], ERCOT is canceling the Emergency Notice and is resuming normal operations from the [alternate/primary] control center.  [Select TO], please repeat that back for me. If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## T#72 OCN for Hurricane / Tropical Storm:

“This call requires everyone to remain on the line until it is complete.  [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an OCN for a [Tropical Storm/Hurricane] [Name] due to a probability of making landfall in the ERCOT Region. TOs are instructed to:

- Review planned and existing transmission outages to be canceled and/or restored

- Review emergency operating procedures, evacuation plans, and the possible need to staff backup facilities.

ERCOT will continue to monitor the Storm. [TO] please repeat this back to me.  That is correct, thank you.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## T#73 Advisory for Hurricane / Tropical Storm:

“This call requires everyone to remain on the line until it is complete.  [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an Advisory for [Tropical Storm/Hurricane] [Name] in the Gulf of Mexico which is currently projected to impact the ERCOT Region.  TOs are instructed to:

- Review planned and existing transmission outages to be canceled and/or restored.

- Review emergency operating procedures, evacuation plans, and the possible need to staff backup facilities.

- Test communication with other TOs and QSEs prior to the hurricane making landfall.

ERCOT will continue to monitor the Storm. [TO] please repeat this back to me.  That is correct, thank you.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## T#74 Watch for Hurricane / Tropical Storm:

“This call requires everyone to remain on the line until it is complete.  [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing a Watch for [Tropical Storm/Hurricane] [Name] in the Gulf of Mexico which is expected to make landfall near [Place] at [time].  TOs are instructed to:

- Be prepared to lose load and expect high voltage conditions

- Keep ERCOT informed of transmission outages.

ERCOT will continue to monitor the Storm. [TO] please repeat this back to me.  That is correct, thank you.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## T#75 Emergency for Hurricane / Tropical Storm:

“This call requires everyone to remain on the line until it is complete.  [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an Emergency Notice due to [Tropical Storm/Hurricane Name] having an adverse impact on the ERCOT System [specify condition]. TOs are instructed to:

- Be prepared to lose load and expect high voltage conditions

- Keep ERCOT informed of any issues

ERCOT will continue to monitor the Storm. [TO] please repeat this back to me.  That is correct, thank you.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## T#76 OCN for Extreme Cold Weather:

“This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an OCN for an extreme cold weather system approaching [time frame] with temperatures anticipated to remain 32°F or below.  TOs are instructed to:

- Review Planned outages and existing outages for the possibility of canceling or restoring equipment,

- Review and implement winterization procedures. Notify ERCOT of any changes or conditions that could affect system reliability.

[TO] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## T#77 Advisory for Extreme Cold Weather:

“This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an Advisory for the extreme cold weather system approaching [time frame] with temperatures anticipated to remain 32°F or below.   TOs are instructed to:

- Review Planned outages and existing outages for the possibility of canceling or restoring equipment,

- Review and implement winterization procedures. Notify ERCOT of any changes or conditions that could affect system reliability.

[TO] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## T#78 Watch for Extreme Cold Weather:

“This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing a Watch for the extreme cold weather system approaching [time frame].  Temperatures are expected to remain 32°F or below.  TOs are instructed to:

- Review Planned outages and existing outages for the possibility of canceling or restoring equipment,

- Prepare for higher than usual loads,

- Review and implement winterization and emergency operating procedures. Notify ERCOT of any changes or conditions that could affect system reliability.

[TO] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## T#79 Emergency for Extreme Cold Weather:

“This call requires everyone to remain on the line until it is complete.  [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name].  At [xx:xx], ERCOT is issuing an Emergency Notice, the extreme cold weather system is beginning to have an adverse impact on the system such as [state what the adverse impacts are].

- Prepare for higher than usual loads and the possibility of load shedding.

ERCOT will continue to monitor the extreme cold weather system and will convey information and instructions as conditions warrant. [TO] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## T#80 OCN for Extreme Hot Weather:

“This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an OCN for the extreme hot weather with forecasted temperatures to be above [103°F or 94°F] in the North Central and South Central weather zones.   TOs are instructed to:

- Review Planned and existing transmission outages for the possibility of canceling or restoring equipment,

- Review and implement weatherization and emergency operating procedures and notify ERCOT of any changes or conditions that could affect system reliability.

ERCOT will continue to monitor the weather system. [TO] please repeat this back to me.  That is correct, thank you.”

## T#81 Advisory for Extreme Hot Weather:

“This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an Advisory for the extreme hot weather with forecasted temperatures to be above [103°F or 94°F] in the North Central and South Central weather zones.   TOs are instructed to:

- Review Planned and existing transmission outages for the possibility of canceling or restoring equipment,

- Review and implement weatherization and emergency operating procedures and notify ERCOT of any changes or conditions that could affect system reliability.

ERCOT will continue to monitor the weather system. [TO] please repeat this back to me.  That is correct, thank you.”

## T#82 Watch for Extreme Hot Weather:

“This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing a Watch for the extreme hot weather with forecasted temperatures to be above [103°F or 94°F] in the North Central and South Central weather zones [today or tomorrow].  ERCOT is expecting statewide power supplies to be very tight.  TOs are instructed to:

- Review Planned and existing transmission outages for the possibility of canceling or restoring equipment,

- Prepare for higher than usual loads,

- Review and implement weatherization and emergency operating procedures and notify ERCOT of any changes or conditions that could affect system reliability.

ERCOT will continue to monitor the weather and will convey information and instructions as conditions warrant. [TO] please repeat this back to me.  That is correct, thank you.”

T#83 Emergency for Extreme Hot Weather:

“This call requires everyone to remain on the line until it is complete.  [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name].  At [xx:xx], ERCOT is issuing an Emergency Notice, the extreme hot weather system is beginning to have an adverse impact on the ERCOT System such as [state what the adverse impacts are].

- Prepare for higher than usual loads and the possibility of load shedding.

ERCOT will continue to monitor the extreme hot weather system and will convey information and instructions as conditions warrant. [TO] please repeat this back to me.  That is correct, thank you.”

## T#84 OCN/Advisory/Watch for other Weather Events:

“This call is requires everyone to remain on the line until it is complete.  [TO] I will be asking you for the repeat back.  This is ERCOT Operator [first and last name].  At [xx:xx], ERCOT is issuing a [OCN/Advisory/Watch] due to [type of weather event] in the [location on the grid].  If you experience any issues as a direct result of the weather event, notify ERCOT”.

## T#85 – Weekly TO Hotline Test:

“This is ERCOT Operator [first and last name].  ERCOT is conducting the weekly TO Hotline test.  ERCOT is currently at NTAS Advisory level [state advisory level].  The following notices are currently in effect:

- List OCNs, Advisories, Watches and/or Emergency Notices in effect.

- State “None” if none are in effect.

This ends the test of the ERCOT Hotline.  That is all.”

## T#86 Execute a SASM for Failure to Provide/Infeasibility:

“This call requires everyone to remain on the line until it is complete.  [TO] I will be asking you for the repeat back.  This is ERCOT Operator [first and last name], ERCOT will execute a SASM at [xx:xx] for operating day [xx/xx/xx] for HE [xx-xx] for [type of A/S] MW [X], [X], [X]”.  [TO] please repeat this back to me.”  If repeat back is CORRECT, “That is correct, thank you.”  If INCORRECT, repeat the process until the repeat back is correct.

## T#87 Blank:

## T#88 EEA3 PRC <1375 MW Without Firm Load Shed:

“This call requires everyone to remain on the line until it is complete.  [TO] I will be asking you for the repeat back.  This is ERCOT Operator [first and last name], at [xx:xx], ERCOT is declaring EEA3 due to Physical Responsive Capability falling below 1375 MW.  Firm load shed is not being requested at this time.  Implement all measures associated with EEA 1 and 2, if not already implemented. [TO] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## T#89 Transmission Watch for the Rio Grande Valley Import:

“This call requires everyone to remain on the line until it is complete.  [TO] I will be asking you for the repeat back.  This is ERCOT operator [first and last name].  At [xx:xx], ERCOT is issuing a Transmission Watch for the Rio Grande Valley due to Rio Grande Valley Import, this may result in the curtailment of DC-Tie exports to CENACE.” [TO] please repeat this back to me.

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct

## T#90 Cancel Transmission Watch for Rio Grande Valley Import:

“This is ERCOT Operator [first and last name].  At [xx:xx], ERCOT is canceling the Transmission Watch for the Rio Grande Valley Import.  [TO] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## T#91 Emergency Notice Loss of Primary Control Center (Systems are NOT Functional):

“This call requires everyone to remain on the line until it is complete.  [TO] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]; at [xx:xx], ERCOT is issuing an Emergency Notice due to the loss of primary control center and is transferring operations to the alternate control center.  Please monitor your own service area and notify ERCOT if you exceed the normal ratings of your transmission elements.  Report if power flows on any GTCs reach 85% of their respective limits and notify ERCOT of any forced line operations.  Direct all urgent phone calls thru the [Bastrop][Taylor] OPX.  [Select TO], Please repeat this back for me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## T#92 Emergency Notice Loss of Primary Control Center (Systems are NOT Functional):

“This call requires everyone to remain on the line until it is complete.  [TO] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]; at [xx:xx], ERCOT is issuing an Emergency Notice due to the loss of primary control center functionality and is transferring operations to the alternate control center.  Please monitor your own service area and notify ERCOT if you exceed the normal ratings of your transmission elements.  Report if power flows on any GTCs reach 85% of their respective limits and notify ERCOT of any forced line operations.  Direct all urgent phone calls thru the [Bastrop][Taylor] OPX.  [Select TO], Please repeat this back for me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the entire process until the repeat back is correct.

## T#93 Rio Grande Valley Reliability Margin ≤350 MW:

“This is ERCOT Operator [first and last name].  At [xx:xx], TOs are instructed to coordinate with connected generators and other nearby TOs to increase voltages by placing capacitor banks in-service and turning off reactors near the weak busses that are available without exceeding high Voltage SOLs.

[TO] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## T#94 Rio Grande Valley Reliability Margin returned to normal:

- “This call requires everyone to remain on the line until it is complete.  [TO] I will be asking you for the repeat back.  This is ERCOT operator [first and last name]; at [xx:xx], ERCOT is requesting TOs to coordinate and return to normal voltage operations related to the Rio Grande Valley Reliability Margin.  [Select TO], please repeat that back for me. If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## T#95 North – Houston Reliability Margin ≤500 MW:

“This is ERCOT Operator [first and last name].  At [xx:xx], TOs are instructed to coordinate with connected generators and other nearby TOs to increase voltages by placing capacitor banks in-service and turning off reactors near the weak busses that are available without exceeding high Voltage SOLs.

[TO] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## T#96 North – Houston  Reliability Margin returned to normal:

- “This call requires everyone to remain on the line until it is complete.  [TO] I will be asking you for the repeat back.  This is ERCOT operator [first and last name]; at [xx:xx], ERCOT is requesting TOs to coordinate and return to normal voltage operations related to the North – Houston  Reliability Margin.  [Select TO], please repeat that back for me. If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## T#97 ERCOT’s ICCP, MIS, or the Outagage Scheduler Planned or Unplanned  Outage:

- “This call requires everyone to remain on the line until it is complete.  [TO] I will be asking you for the repeat back.  This is ERCOT operator [first and last name], at [xx:xx], ERCOT is notifing the TOs that ERCOT’s [ICCP, MIS, or Outage Scheduler] has a [planned / unplanned] Outage that is expected to last 30 minutes or more.

- [TO] please repeat that back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## T#98 ERCOT’s ICCP, MIS, or the Outage Scheduler back to Normal:

“This call requires everyone to remain on the line until it is complete.  [TO] I will be asking you for the repeat back.  This is ERCOT operator [first and last name], at [xx:xx], ERCOT is notifing the TOs that ERCOT’s [ICCP, MIS, or Outage Scheduler] is now functional.  [TO] please repeat that back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## T#99 QSE on Constant Frequency Control for Unannounced Constant Frequency Control Test:

“This call requires everyone to remain on the line until it is complete.  [TO] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is conducting an unannounced Constant Frequency Control test and will place a QSE on Constant Frequency Control. [TO] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

## T#100 Cancel QSE on Constant Frequency Control for Unannounced Constant Frequency Control Test:

“This call requires everyone to remain on the line until it is complete.  [TO] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT has ended the unannounced Constant Frequency Control test. [TO] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Frosch and Hartmann | Prepares | April 23,2015 |
| Frosch, Hartmann and Gaddy | Procedure writers and editors | July 13, 2015 |
| Hartmann and Gaddy | Procedure writers and editors | September 25, 2015 |
| Hartmann, Gaddy and Drummond-Bunner | Procedure writers and editors | December 22, 2015 |
| Hartmann and Gaddy | Procedure writers and editors | January 22, 2016 |
| Hartmann and Gaddy | Procedure writers and editors | February 23, 2016 |
| Hartmann and Gaddy | Procedure writers and editors | April 22, 2016 |
| Frosch, Hartmann and Gaddy | Procedure writers and editors | June 24, 2016 |
| Frosch, Hartmann and Gaddy | Procedure writers and editors | September 26, 2016 |
| Hartmann and Gaddy | Procedure writers and editors | October 31, 2016 |
| Hartmann and Gaddy | Procedure writers and editors | December 22, 2016 |
| Hartmann, Gaddy and Frosch | Procedure writers and editors | March 27, 2017 |
| Hartmann and Gaddy | Procedure writers and editors | April 5, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | May 26, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | June 23, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | August 30, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | September 27, 2017 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | February 22, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | March 26, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | April 27, 218 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | August 24, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | September 27, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | October 29, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | December 21, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | January 25, 2019 |
| Hartmann, Gaddy and Luker | Procedure writers and editors | April 26, 2019 |
| Hartmann, Gaddy and Pence | Procedure writers and editors | May 13, 2019 |
| Hartmann, Gaddy and Pence | Procedure writers and editors | May 28, 2019 |
| Hartmann, Gaddy and Pence | Procedure writers and editors | July 29, 2019 |

Manual Change History

| Procedure | Ver/Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All Sections | 1.0 / 0 | New script document | May 1, 2015 |
| All Sections 1 | 1.0 / 1 1.0 / 1 | Added a “Q” for QSE scripts and a “T” for TO scripts Updated Scripts Q62, Q63, Q64 | July 15, 2015 |
| 3 | 1.0 / 2 | Updated Script T#8 Content Updated Script T#29 Content and Script Title Corrected Script T#71 Content and Script titles | October 1,2015 |
| 2 3 | 1.0 / 2 1.0 / 3 | Updated QSE script titles Q#1, Q#2, Q#3, Q#4, Q#5, Q#6, Q#7, Q#8, Q#9, Q#12, Q#14, Q#15, Q#16, Q#22, Q#23, Q#26, Q#27, Q#28, Q#29, Q#30, Q#31, Q#32, Q#33, Q#34, Q#35, Q#36, Q#38, Q#39, Q#40, Q#41, Q#42, Q#43, Q#44, Q#46, Q#47, Q#48, Q#49, Q#50, Q#51, Q#52, Q#53, Q#54, Q#55, Q#56, Q#57, Q#61, Q#65, Q#69, Q#70, Q#71, Q#72, Q#73, Q#74, Q#75, Q#78, Q#79, Q#80, Q#81, Q#82, Q#84, Q#86, Q#87, Q#88, Q#91, Q#92, Q#94, Q#95, Q#96, Q#97, Q#99, Q#100, & Q#101 Deleted scripts Q#71 & Q#72 Updated Transmission script titles T#2, T#4, T#9, T#10, T#13, T#14, T#18, T#19, T#20, T#21, T#22, T#23, T#24, T#25, T#26, T#27, T#28, T#29, T#30, T#31, T#32, T#33, T#34, T#35, T#36, T#37, T#38, T#39, T#40, T#41, T#42, T#43, T#44, T#45, T#46, T#47, T#48, T#51, T#52, T#53, T#54, T#55, T#56, T#57, T#58, T#59, T#60, T#61, T#62, T#63, T#64, T#65, T#66, T#67, T#68, T#69, T#70, T#71, T#75, T#76, T#77, T#78, T#79, T#80, T#81, T#82, T#83, T#84, & T#85 Updated script content T#7, T#15, T#22, & T#24 | December 31, 2015 |
| 2 3 | 1.0 / 3 1.0 / 4 | Added Script Q#72 Updated Script Titles Q#75, Q#77, Q#78, Q#81, Q#83, & Q#84 Updated Script T#52 & T#85 Added Script T#86 | February 10, 2016 |
| 2 3 | 1.0 / 4 - / 5 | Updated Script Q#24, Q#25 and Q#75 Updated Script Title Q#72 Updated Script T#85 Updated Script Title T#86 | March 1, 2016 |
| 2 3 | 1.0 / 5 1.0 / 6 | Updated Script Q#19 and Q#21 Updated Script Title Q#21 Updated Script T#16 and T#18 Updated Script Title T#18 | April 29, 2016 |
| 1 2 3 | 1.0 / 2 1.0 / 6 1.0 / 7 | Updated 1.2 Updated Scripts Q#40, Q#41, Q#52, Q#53, Q#59, Q#68, Q#69 & added Script Q#102 Updated Scripts T#8, T#9, T#10, T#28, T#79, T#82, T#83 & added Script T#87 | June 30, 2016 |
| 2 3 | 1.0 / 7 1.0 / 8 | Updated scripts Q#20, Q#32, Q#33, Q#34, Q#35, & Q#69 Updated scripts T#21, T#23, T#41, T#43 T#44, T#61, & T#62 | September 30, 2016 |
| 2 | 1.0 / 8 | Added script Q#71 | November 2, 2016 |
|  |  | Updated Table of Contents Links | December 30, 2016 |
| 2 3 | 1.0 / 9 1.0 / 9 | Updated script Q#11 and Q#71 Added script Q#103 Updated scripts T#8, T#25, T#26 and T#29 Added script T#88 | March 31, 2017 |
| 2 3 | 1.0 / 10 1.0 / 10 | Added scripts Q#104, Q#105, Q#106, Q#107, Q#108 and Q#109 Added scripts T#89, T#90, T#91, T#92, T#93, T#94, T#95, T#96, T#97 and T#98 | April 6, 2017 |
| 2 3 | 1.0 / 11 1.0 / 11 | Updated script Q#106 Updated script T#91 | June 1, 2017 |
| 2 3 | 1.0 / 12 1.0 / 12 | Deleted script Q#102 Deleted script T#87 Updated script T#91 | June 30, 2017 |
| 2 3 | 1.0 / 13 1.0 / 13 | Added scripts Q#110 and Q#111 Updated script T#63 and T#92 | August 31, 2017 |
| 2 3 | 1.0 / 14 1.0 / 14 | Updated script Q#22, Q#50, Q#89, Q#91, Q#93, Q#94, Q#95, & Q#107 Updated script T#23 | September 29, 2017 |
| 2 3 | 1.0 / 15 1.0 / 15 | Updated script Q108 & 109 Updated script T6, T97 & T98 | February 28, 2018 |
| 3 | 1.0 / 16 | Updated scripts T25 and T26 | March 30, 2018 |
| 2 3 | 1.0 / 16 1.0 / 17 | Added sceipts Q112 through Q119 Updated script T17 Added scripts T99 & T100 | May 1, 2018 |
| 2 | 1.0 / 17 | Added scripts Q#120 & Q#121 | August 31, 2018 |
| 2 3 | 1.0 / 18 1.0 / 18 | Deleted script #Q106 & Q#107 for NPRR 825 Deleted script #T91 & T#92 for NPRR 825 | October 1, 2018 |
| 2 3 | 1.0 / 19 1.0 / 19 | Updated script Q#18 & Q#21 Updated script T#18 | November 1, 2018 |
| 2 3 | 1.0 / 20 1.0 / 20 | Update scripts Q#32, Q#48, Q#49 & Q#71 Updated script T#22 & T#29 | December 28, 2018 |
| 2 | 1.0 / 21 | Updated script Q#100 | January 31, 2019 |
| 2 | 1.0 / 22 | Updated scripts Q#6, Q#7, Q#9 & Q#12 | May 1, 2019 |
| 2 | 1.0 / 23 | Added scripts Q#122, Q#123, and Q#124 | May 16, 2019 |
| 2 3 | 1.0 / 24 1.0 / 21 | Updated script Q#124 Updated script title T#6 | May 31, 2019 |
| 2 3 | 1.0 / 25 1.0 / 22 | Deleted Script Q#26 Added Scripts Q#106 & Q#107 Deleted Scripts T#39 & T#40 Added Scripts T#91 & T#92 | August 1, 2019 |