- Power Operations Bulletin # 909

ERCOT has posted/revised the Real Time manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

- http://www.ercot.com/mktrules/guides/procedures/index.html

## 3.5	Monitor Capacity and Reserves and Respond to Shortages or Surplus

Procedure Purpose:  Monitoring sufficient operating reserves and capacity surplus.  Deploying/Recalling Non-Spin and manually Deploying/Recalling RRS.

| Protocol Reference | 6.5.7.6.2.3 |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.8 |  |  |  |
| NERC Standard | IRO-001-4 R1 | TOP-001-4 R2 |  |  |

| Version: 1 | Revision: 18 | Effective Date: November 1, 2019 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | The Day-Ahead process, the Adjustment Period process, and the Real-Time process must be utilized before ordering Resources to specific output levels with Emergency Base Point instructions. |
| ## Insufficient Generation |  |
| RMR | Prior to declaring EEA, start RMR Units available in the time frame of the emergency. RMR Units should be loaded to full capability. |
| Deploying Non-Spin | Triggers to deploy Non-Spin MONITOR: - The Splunk Dashboard - MOS - 01 SCED GEN ONLINE and scroll down to Lookahead Load Ramping from MTLF - Avail CAP 30Min represents (HASL – Gen) – (30 minute load ramp) IF: - Avail_CAP_30Min < 0 THEN: - Coordinate with the Resource Operator to deploy half of available Non-Spin. IF: - Avail_CAP_30Min < -300, OR - PRC is < 2500 MW; THEN: - Coordinate with the Resource Operator to deploy all of available Non-Spin. |
| Recalling Non-Spin | WHEN: - Avail_CAP_30Min > 1000, AND - PRC is > 2800 MW; THEN: - Coordinate with the Resource Operator to recall half of the deployed Non-Spin. WHEN: - Avail_CAP_30Min > 1000, AND - PRC is > 3000 MW; THEN: - Coordinate with the Resource Operator to recall all of the deployed Non-Spin. |
| NOTE | RRS for capacity may be manually deployed (HASL released) when the system approaches scarcity conditions so that the capacity reserved behind HASL will be released to Security-Constrained Economic Dispatch (SCED). The existing measure of scarcity is Physical Responsive Capability (PRC) and spinning reserves. If PRC and spinning reserves drop below 3,000 MW, this process may be used. Scarcity conditions may occur during the Peak Load Season when ERCOT System Load is above 60,000 MW. For all other months, they could occur when ERCOT System Load is above 50,000 MW. |
| HASL Release – Manually Deploy RRS | Triggers to manually deploy RRS MONITOR: - “HASL – Load Ramp” value on the Generation Area Status display, this is HASL – (Gen + 5 minute load ramp) IF: - HASL – Load Ramp < = 200 MW; THEN: - Ensure all Non-Spin has been deployed first before manually deploying RRS. - Manually deploy up to 500 MW of RRS. IF: - After Resources have responded to the previous deployment, AND - HASL – Load Ramp < = 200 MW; THEN: - Manually deploy up to another 500 MW of RRS (it is incremental, enter 1,000). IF: - PRC < = 2000 MW; THEN: Manually deploy all remaining RRS. |
| HASL - RRS Recall | WHEN: - HASL – (Gen + 5 minute load ramp) > 1600 MW AND/OR - PRC > = 3300 MW, AND - Frequency is 59.970 HZ or above; THEN: - Manually recall the RRS, which can be done in up to 500 MW steps. |
| ## Surplus Generation |  |
| SCED Surplus | MONITOR: - The Generation Area Status Page IF: - (GEN-LDL) < 200 MW; THEN: - Consult with RUC Operator to ensure HRUC is seeing the situation and is decommitting Resources, - If needed, request the RUC Operator to issue VDI to decommit a Resource to help alleviate the surplus |
| Log | Log all actions. |
| ## Valley Generation |  |
| Monitor | Market Operations>Reliability Unit Commitment>HRUC Displays>UC Displays>Output Display Menu>Generator Outputs>Generation Schedule OR Market Operations>Reliability Unit Commitment>HRUC Displays>UC Displays>Input Display Menu>Generation Self-Commitment Status |
| 1 | WHEN: - Two or more Generation plants (DUKE, NEDIN and/or SILASRAY) are scheduled to go Off-Line at the same time; THEN: - Discuss with Transmission and Security Operator AND Shift Supervisor - Ensure AEP TO is notified with the shut down time and with at least an hours’ notice, they need to pre-posture reactive devices. |
| Log | Log all actions. |

## 5.3	Implement EEA Levels

Procedure Purpose:  To provide for maximum possible continuity of service while maintaining the integrity of the ERCOT System to reduce the chance of Cascading Outages.

| Protocol Reference | 6.5.9.3.4(6) | 6.5.9.4 | 6.5.9.4.2 | 6.5.9.4.3 |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.5.3 | 4.5.3.1 | 4.5.3.2 | 4.5.3.3 |
|  | 4.5.3.4 |  |  |  |
| NERC Standard | EOP-011-1 R2, R2.1, R2.2, R2.2.2, R2.2.3, R2.2.3.1, R2.2.3.4, R2.2.4, R2.2.7 | IRO-001-4 R1 | TOP-001-4 R2 |  |

| ### Version: 1 | Revision: 27 | Effective Date: November 1, 2019 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - IF steady state system frequency falls < 59.91 Hz, ERCOT CAN immediately implement EEA 3. - IF steady state system frequency falls < 59.5 Hz, ERCOT SHALL immediately implement EEA 3. |
| NOTE | Confidentiality requirements regarding Transmission Operations and System Capacity information will be lifted, as needed to restore reliability. |
| ERS-30 | ERS with a thirty-minute ramp period. |
| ERS-10 | ERS with a ten-minute ramp period. |
| TCEQ | When increased generation is requested during EEA events, Texas Commission on Environmental Quality (TCEQ) will exercise enforcement discretion for exceedances of emission limits as well as operational limits for power generating plants for Generators who exceed air permit limits in order to maximize generation for the duration of the EEA event. ERCOT General Council will send out a Market Notice each time ERCOT enters into an EEA with this reminder. |
| Media Appeal | When an ERCOT-wide appeal through the public news media for voluntary energy conservation is made. Notify the QSEs by hotline. |
| ### Implement EEA Level 1 |  |
| EEA 1 PRC<2300 | IF: - PRC < 2300 MW and is not projected to be recovered above 2300 MW within 30 minutes without the use of EEA Level 1; THEN: - Select the activate EEA flag in EMS, - Maintain steady state system frequency near 60 Hz and maintain PRC above 1750 MW, - Determine whether system conditions warrant the deployment of ERS-30. Refer to the ERS tab on the Real-Time Values Spreadsheet for amounts in each time period and number of times deployed: - Consider the peak hour, deploy all ERS-30 if needed to prevent PRC from falling < 1750 MW, - When deploying the ERS-30, also deploy the weather-sensitive ERS if available for the current time period. - Using the Hotline, notify all QSEs to implement EEA 1. Q#5 - Typical Hotline Script for EEA1 NOT deploying ERS OR IF: - Deploying ERS, the Resource Operator must complete the XML deployment of the ERS before the Hotline call is made. - Deploy all ERS Resources as a single group - If it is June – September and during time period TP3 or TP4 on a business day, use this script. Q#6 - Typical Hotline Script for EEA1 deploying ERS-30 / ERS-30 including Weather Sensitive |
| When ERS Time Periods Change | IF: - ERS Resources are deployed and the Time Period is changing - If it is June – September and during time period TP3 or TP4 on a business day; THEN: - After Resource Operator has completed the XML deployment, make the QSE hotline call Q#26 - Typical Hotline Script for EEA1 deploying ERS-30 / ERS -30 including Weather Sensitive Script for New Time Period |
| RRS Release to HASL | REVIEW REFERENCE DISPLAY: EMP Applications>Generation Area Status>Nodal Operations Status>Responsive Reserve Service Summary Data IF: - PRC < 2000 MW; THEN: - Activate Manual Responsive Reserve - Manually deploy all remaining RRS |
| Log | Log all actions. |
| ### Implement EEA Level 2 |  |
| Note | ERCOT may declare an EEA Level 2 when the clock-minute average system frequency falls below 59.91 Hz for 15 consecutive minutes. |
| EEA 2 PRC<1750 | IF: - PRC < 1750 MW or unable to maintain system frequency at a minimum of 59.91 Hz and is not projected to be recovered above 1750 MW within 30 minutes without the use of EEA Level 2; THEN: - Verify with Shift Supervisor a public appeal has been issued - Maintain steady state system frequency at a minimum of 59.91 Hz and maintain PRC above 1,375 MW, - Determine when system conditions require the deployment of Load Resources and/or ERS Resources (Do Not forget the WS ERS if available): - Deploy ERS-30 if not already done in EEA 1 - Deploy ERS-10 - Deploy Load Resources Group 1 and/or 2 - Using the Hotline, notify all QSEs to implement EEA 2 and any measures associated with EEA 1, if not already implemented. |
| ERS Resources | IF: - Deploying ERS, the Resource Operator must complete the XML deployment of the ERS before the Hotline call is made. - Deploy all ERS Resources as a single group. - If it is June – September and during time period TP3 or TP4 on a business day Q#7 - Typical Hotline Script for EEA2 deploying ERS-10 / ERS-30 / both ERS-10 and ERS 30 / ERS-30 including Weather Sensitive ERS / ERS-10 and ERS-30 including Weather Sensitive |
| Load Resources | IF: - Deploying Load Resources, the Resource Operator must complete the XML deployment of the Load Resources before the Hotline call is made. - PRC < 1750 MW, deploy Group 1 - PRC < 1375 MW, deploy both Groups 1 and 2 simultaneously Q#8 - Typical Hotline Script for EEA2 deploying Load Resources Group 1 / Load Resources Group 1 and 2 |
| When ERS Time Periods Change | IF: - ERS Resources are deployed and the Time Period is changing - If it is June – September and during time period TP3 or TP4 on a business day; THEN: - After Resource Operator has completed the XML deployment, make the QSE hotline call Q#9 - Typical Hotline Script for EEA2 deploying ERS-10 / ERS-30 / both ERS-10 and ERS-30 / ERS-10, ERS-30 including Weather Sensitive Script |
| NOTE | - All Load Resources, 10 MIN ERS, and 30 MIN ERS must be deployed before firm load |
| Media Appeal | - Unless already in effect, verify with the Shift Supervisor that the communications group has issued an appeal through the public news media for voluntary energy conservation, - Notify QSEs, via Hotline, that a media appeal for conservation is in effect. Q#10 - Typical Hotline Script for Media Appeal |
| Log | Log all actions. |
| ### Implement EEA Level 3 |  |
| Note | ERCOT may declare an EEA Level 3 when the clock-minute average system frequency falls below 59.91 Hz for 20 consecutive minutes. |
| EEA3 PRC <1375 MW | ERCOT will declare an EEA Level 3 when PRC cannot be maintained above 1,375 MW. Using the Hotline, notify all QSEs to implement EEA 3 Without Firm Load Shed and any measures associated with EEA 1 and 2, if not already implemented. Q#103 - Typical Hotline Script for EEA3 PRC <1375 Without Firm Load Shed |
| EEA3 Unable to Maintain 59.91 Hz or PRC <1000 MW | IF: - PRC < 1000 MW and is not projected to be recovered above 1,000 MW within 30 minutes or unable to maintain system frequency at 59.91 Hz for 25 consecutive minutes; THEN: - Using the Hotline, notify all QSEs to implement EEA 3 Firm Load Shed and any measures associated with EEA 1 and 2, if not already implemented. Q#11 - Typical Hotline Script for EEA3 With Firm Load Shed |
| When ERS Time Periods Change | IF: - ERS Resources are deployed and the Time Period is changing - If it is June – September and during time period TP3 or TP4 on a business day; THEN: - After Resource Operator has completed the XML deployment, make the QSE hotline call Q#12 - Typical Hotline Script for EEA3 deploying ERS-10 / ERS-30 / both ERS-10 and ERS-30 / ERS-10, ERS-30 including Weather Sensitive |
| RRS Release to HASL | REVIEW REFERENCE DISPLAY: EMP Applications>Generation Area Status>Nodal Operations Status>Responsive Reserve Service Summary Data IF: - Unable to maintain PRC > 1000 MW; THEN: - May be necessary to de-activate Manual Responsive Reserve |
| Log | Log all actions. |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Frosch, Hartmann, Stone, and Barcalow | Prepares | November 10 , 2010 |
| Frosch and Hartmann | Procedure writers and editors | November 29, 2010 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2010 |
| Frosch, Foster and Hartmann | Procedure writers and editors | January 3, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 26, 2011 |
| Frosch and Hartmann | Procedure writers and editors | March 23, 2011 |
| Frosch and Hartmann | Procedure writers and editors | April 20, 2011 |
| Frosch and Hartmann | Procedure writers and editors | June 6, 2011 |
| Frosch and Hartmann | Procedure writers and editors | July 18, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 1, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 30, 2011 |
| Frosch and Hartmann | Procedure writers and editors | September 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | October 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 16, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | April 25, 2012 |
| Frosch and Hartmann | Procedure writers and editors | May 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | May 30, 2012 |
| Barcalow, Frosch and Hartmann | Procedure writers and editors | July 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | August 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | October 26, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 26, 2013 |
| Frosch and Hartmann | Procedure writers and editors | May 28, 2013 |
| Frosch and Hartmann | Procedure writers and editors | July 8, 2013 |
| Frosch and Hartmann | Procedure writers and editors | August 7, 2013 |
| Frosch and Hartmann | Procedure writers and editors | September 25, 2013 |
| Frosch and Hartmann | Procedure writers and editors | December 11, 2013 |
| Frosch and Hartmann | Procedure writers and editors | December 20, 2013 |
| Frosch, Gaddy, Hartmann and Solis | Procedure writers and editors | April 1, 2014 |
| Frosch, Gaddy and Hartmann | Procedure writers and editors | May 27, 2014 |
| Frosch and Hartmann | Procedure writers and editors | July 29, 2014 |
| Frosch and Hartmann | Procedure writers and editors | September 29, 2014 |
| Drummond, Frosch and Hartmann | Procedure writers and editors | December 10, 2014 |
| Frosch and Thompson | Procedure writers and editors | December 19, 2014 |
| Frosch and Hartmann | Procedure writers and editors | February 25, 2015 |
| Frosch and Hartmann | Procedure writers and editors | March 25, 2015 |
| Frosch and Hartmann | Procedure writers and editors | April 29, 2015 |
| Frosch, Hartmann and Gaddy | Procedure writers and editors | July 13, 2015 |
| Hartmann and Gaddy | Procedure writers and editors | December 22, 2015 |
| Hartmann, Gaddy and Frosch | Procedure writers and editors | February 23, 2016 |
| Hartmann and Gaddy | Procedure writers and editors | April 22, 2016 |
| Hartmann, Gaddy and Frosch | Procedure writers and editors | June 24, 2016 |
| Hartmann and Gaddy | Procedure writers and editors | July 15, 2016 |
| Hartmann, Gaddy and Frosch | Procedure writers and editors | September 26, 2016 |
| Hartmann and Gaddy | Procedure writers and editors | October 31, 2016 |
| Hartmann, Gaddy and Frosch | Procedure writers and editors | December 23, 2016 |
| Hartmann, Gaddy and Frosch | Procedure writers and editors | March 24, 2017 |
| Hartmann and Gaddy | Procedure writers and editors | April 5, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | May 26, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | June 23, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | July 24, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | September 27, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | October 27, 2017 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | December 22, 2017 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | February 22, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | April 2, 2018 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | April 27, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | August 24, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | September 27, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | December 21, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | January 25, 2019 |
| Hartmann, Gaddy and Frosch | Procedure writers and editors | March 26, 2019 |
| Hartmann, Gaddy and Pence | Procedure writers and editors | July 29, 2019 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | October 29, 2019 |

Manual Change History

| Procedure | Ver/Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All Sections | 1.0 / 0 | New procedures for all sections for Nodal implementation | November 28, 2010 |
| 2.4 3.1 3.2 3.4 3.5 3.6 4.2 5.3 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Updated Categories and Priorities Updated Response to High Frequency steps 15, 20 and 25 minutes and Response to Low Frequency step 15 Updated steps Failure Indication/Issues and QSE Capacity Issues Updated steps AGC/RLC Issues, System Wide Capacity Issue and AGC/RLC Issues Resolved Updated step 1 Updated step Capacity Surplus Updated step 2, 3, 4 and 5 Updated all steps of “Implement Level 2B” | December 1, 2010 |
| 4.1 4.2 5.2 | 1.0 / 1 1.0 / 2 1.0 / 1 | Updated step “MP unable to Override” Updated step 1 & 2 Updated step 1 in sections WATCH and Advisory | December 15, 2010 |
| 3.1 3.2 3.3 3.4 4.1 5.1 5.4 | 1.0 / 2 1.0 / 2 1.0 / 1 1.0 / 2 1.0 / 2 1.0 / 1 1.0 / 1 | Updated step “BAAL” Updated step “AGC Issues Resolved” Updated step “Hotline” Updated step “Failure Indications, AGC/RLC Issues, System Wide Capacity Issue, AGC/RLC Issues Resolved” Updated step 2 in “Workflow Controller Messages”, added new procedure “Exceeding West – North Stability Limit”, updated Note in “Generation Resource Shut-down/Start-up Process” Updated step 1 in “Watch” and step Hotline in “Scripts” Updated step 1 in “Move from EEA level 3 to EEA lever 2B” | January 5, 2011 |
| 2.4 2.5 2.6 2.7 3.1 3.2 3.3 3.4 3.5 4.1 4.2 5.1 5.2 5.3 5.4 5.5 6.1 6.2 6.3 | 1.0 / 0 1.0 / 2 1.0 / 0 1.0 / 0 1.0 / 3 1.0 / 3 1.0 / 2 1.0 / 2 1.0 / 1 1.0 / 3 1.0 / 3 1.0 / 2 1.0 / 2 1.0 / 2 1.0 / 2 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Added new procedure Changed procedure number Added new procedure Added new procedure Updated sections “Maintain System Frequency”, “Response to High Frequency”, “Response to Low Frequency” and “Actions when Frequency Telemetry in Incorrect. Combined sections 3.3, 3.4 & 4.2 into 3.2 Changed 3.5 “Potential DCS Event” to 3.3 & updated whole procedure Changed 3.6 “Monitor Capacity Reserves & Respond to Capacity Issues to 3.4 Changed 3.7 “Monitor and Control Time Error Correction to 3.5 & updated script Deleted Exceeding West-North Stability Limit Deleted Procedure Updated script Updated step 1 in “Advisory” and “Watch” Updated all steps Updated all steps Updated all steps Updated all steps Updated all steps Updated OCN | January 31, 2011 |
| 2.6 3.2 3.3 3.4 3.6 5.1 5.2 | 1.0 / 1 1.0 / 4 1.0 / 3 - / 3 1.0 / 0 1.0 / 3 1.0 / 3 | Updated step Site Failovers Updated step 3 in SCED Failure, step 4 in RLC Failure, Note in LFC (AGC) Failure and step 2 in EMS (LFC and RLC/SCED Failure Updated step 3 Updated step Capacity Shortage Added new procedure Updated Watch and Emergency Notice All step 1’s | March 25, 2011 |
| 2.6 3.1 3.2 3.3 3.6 5.1 5.4 5.5 | 1.0 / 2 1.0 / 4 1.0 / 5 1.0 / 4 1.0 / 1 - / 4 1.0 / 3 1.0 / 2 | Added steps and updated whole procedure Added new step to Maintain System Frequency and updated Response to High Frequency & Response to Low Frequency Updated steps 2, 3, 5 in SCED Failure; steps 2, 3, 4, 6 in RLC Failure; steps 1, 3 in LFC (AGC) Failure; steps 2, 5 in EMS (LFC and RLC/SCED) Failure Updated NERC Recovery Criteria, step 1 & 4 Updated 1st script Updated step 1 in Watch and Emergency Notice and step Post Updated 1st and 2nd script in Restore Firm Load, Updated 1st in Move From EEA Level 3 to EEA Level 2B Updated step 3 | April 22, 2011 |
| 3.3 5.1 5.3 5.4 6.1 6.2 6.3 6.4 | 1.0 / 5 1.0 / 5 1.0 / 3 1.0 / 4 1.0 / 2 1.0 / 0 1.0 / 2 1.0 / 2 | Updated step NERC Recovery Criteria Updated all step 1’s Updated step 1 in Implement EEA Level 1, step 1 in Implement EEA Level 2A, added note and updated step 2 in Implement EEA Level 2B, step 1 in Implement EEA Level 3 Updated all step 1’s Updated all steps Added new procedure Updated section number and all steps Updated section number and all steps | June 8, 2011 |
| 2.6 3.1 5.1 5.2 5.3 5.4 8.1 | 1.0 / 3 1.0 / 5 1.0 / 6 1.0 / 4 1.0 / 4 1.0 / 5 1.0 / 1 | Added step If EBPs are needed”, updated step IF EBPs are needed and W-N was Active before site failover started Added step Hydro, updated step Frequency Deviations Updated step Watch Updated all steps Updated 1st note, step 1 in EEA level 1 & 2A Updated step 1 in Move for EEA level 1 to 0 Added Market Participant Backup Control Center Transfer procedure | July 20, 2011 |
| 3.1 3.2 3.4 4.1 6.4 6.5 | 1.0 / 6 1.0 / 6 1.0 / 4 1.0 / 4 1.0 / 0 1.0 / 3 | Updated step Monitor, 15 minutes, 20 minutes and 25 minutes in Response to High Frequency Updated step 2 in LFC Failure, step 4 & 5in EMS Failure Updated step Capacity Surplus Updated step 2 in Workflow Controller Messages Added new procedure “Extreme Hot Weather” Changed section number | August 3, 2011 |
| 2.7 3.1 5.1 5.2 5.3 5.4 6.4 7.1 | 1.0 / 1 1.0/ 7 1.0 / 7 1.0 / 5 1.0 / 5 1.0 / 6 1.0 / 1 1.0 / 1 | Updated step Hotline Call Updated NERC Standard reference table Added projected reserve capacity shortage and Extreme Hot Weather in Watch Updated step 1 in Advisory & Watch Updated 2nd Note, step 1 in Implement EEA 1, step Media Appeal & 1 in Implement EEA 2A, 1st Note & step 2 in Implement EEA 2B Added Note to Move From EEA 3 to EEA 2B and Move From EEA 2A to EEA 1 Updated temperature from 102 to 103 Updated 4th note and step 1 | September 1, 2011 |
| 3.2 5.3 5.4 | 1.0 / 7 1.0 / 6 1.0 / 7 | Updated SCED Failure step 2 and 3, RLC Failure step 3 and LFC (AGC) Failure step 3 Combined EEA 2A & B per NPRR 379 Combined EEA 2 A & B per NPRR 379 | October 1, 2011 |
| 3.2 | 1.0 / 8 | Updated script for LFC and EMS Failure | November 1, 2011 |
| 2.4 2.6 4.1 5.1 6.3 | 1.0 / 1 1.0 / 4 1.0 / 5 1.0 / 8 1.0 / 3 | Added step Review, Updated “Site Failover with W-N Active” Added Note to Large Resource Trips or Runbacks Updated Post in “Scripts” Updated “OCN” and “Advisory” All procedures in this manual have been reviewed. | December 15, 2011 |
| 1.2 3.1 4.1 8.1 | 1.0 / 1 1.0 / 7 1.0 / 6 - / 2 | Updated Scope Updated Response to High Frequency & Response to Low Frequency Updated Large Resource Trips or Runbacks, Quick Start Generation Resource Updated Market Participant Backup Control Center Transfer | January 19, 2012 |
| 2.1 3.1 5.1 5.3 7.1 8.1 | 1.0 / 1 1.0 / 8 1.0 / 7 1.0 / 9 1.0 / 7 1.0 / 2 1.0 / 3 | Updated paragraph 4 Updated BAAL Updated Desktop Guide reference & step QSE Override & QSE unable to Override Updated step 1 in Watch Updated Step 1 in Implement EEA Level 1 Updated Desktop Guide references Changed title names, updated steps 1 & 3 & step Power System Stabilizers (PSS) & Automatic Voltage Regulators (AVR) | March 1, 2012 |
| 2.1 3.1 3.2 3.3 3.5 4.1 5.1 6.2 6.3 6.4 8.1 | 1.0 / 2 1.0 / 9 1.0 / 9 1.0 / 6 1.0 / 2 1.0 / 8 1.0 / 10 1.0 / 4 1.0 / 2 1.0 / 4 1.0 / 4 | Changed TSO, DSP to TO Changed Shift Engineer to Operations Support Engineer, removed Automatic SCED Runs & Hydro Generation in Fast Response Mode, updated Note, Monitor/Deploy, 15 minutes, 20 minutes in Response to Low Frequency Updated step 2, 4 & 5, added SCED Data Input Failure, updated RLC Failure, LFC Failure, & EMMS Failure sections Updated Nerc Recovery Criteria step & step 3 Updated Requirements and Notes Changed Shift Engineer to Operations Support Engineer, deleted Large Resource Trips or Runbacks section Updated OCN, Advisory, Watch, Emergency Notice sections Deleted Cold Weather, replaced with Extreme Cold Weather Section changed to Extreme Hot Weather, added OCN and Emergency Notice steps Section number changed Changed Shift Engineer to Operations Support Engineer | May 1, 2012 |
| 3.1 3.4 5.2 | 1.0 / 10 1.0 / 5 1.0 / 6 | Added back step Hydro Generation Operating in Synchronous Condenser Fast Response Mode Updated to reflect changes in the TAC approved Non-Spin document Updated to reflect changes in the TAC approved Non-Spin document | May 14, 2012 |
| 2.6 5.3 5.4 6.3 | 1.0 / 5 1.0 / 8 1.0 / 8 1.0 / 3 | Updated Site Failover step Updated EILS to ERS per NPRR 451 Updated EILS to ERS per NPRR 451 Updated EILS to ERS per NPRR 451 | June 1, 2012 |
| 1.3 2.6 5.1 5.3 5.4 6.2 6.3 7.1 | 1.0 / 1 1.0 / 6 1.0 / 11 1.0 / 9 1.0 / 9 1.0 / 5 1.0 / 4 1.0 / 3 | Removed ERCOT Shift Supervisor paragraph Updated all steps Updated all step 1’s Updated 2nd note, added TCEQ, & XML for ERS Clarified LR and ERS recalls Updated script for Emergency Notice Updated script for Emergency Notice Updated 4th note | July 16, 2012 |
| 2.6 3.1 4.1 5.3 | 1.0 / 7 1.0 / 11 1.0 / 9 1.0 / 10 | Added note to step Database Load Updated Frequency Deviations and Monitor Frequency for the Loss of EMS or Site Failover Incorporated NPRR348 Added 30 MIN ERS and updated steps 1, 2 & 3 on Implement EEA Level 1 | August 29, 2012 |
| 2.2 2.5 3.5 4.1 5.3 | 1.0 / 1 1.0 / 3 1.0 / 3 1.0 / 10 1.0 / 11 | Added Hotline Call Communication Updated step 3 Updated per NOGRR100 Added Note to Shut-down/Start-up Process and new Combine Cycle Generation Resources section Updated ERS scripts All procedures in this manual have been reviewed. | November 1, 2012 |
| 2.5 3.1 3.2 3.3 3.4 3.5 3.6 3.7 5.4 | 1.0 / 4 1.0 / 12 1.0 / 0 1.0 / 10 1.0 / 7 1.0 / 6 1.0 / 4 1.0 / 2 1.0 / 10 | Updated step 3 Updated BAAL New procedure, Monitor Large Ramp Events Updated section # & SCED failure step 2 Updated section # Updated section # Updated section # Updated section # Updated Cancel Watch All procedures in this manual have been reviewed. | March 1, 2013 |
| 2.6 2.7 3.1 3.2 3.3 3.4 3.7 4.1 5.1 5.2 5.3 5.4 5.5 6.1 6.2 6.3 6.4 | 1.0 / 8 1.0 / 2 1.0 / 13 1.0 / 1 1.0 / 11 1.0 / 8 1.0 / 3 1.0 / 11 1.0 / 12 1.0 / 8 1.0 / 12 1.0 / 11 1.0 / 3 1.0 / 3 1.0 / 6 1.0 / 5 1.0 /5 | Updated scripts Updated scripts Updated Monitor Frequency for the Loss of EMS or Site Failover & Actions when Frequency Telemetry is Incorrect Updated scripts Updated scripts Updated script Updated scripts Added QSGR Decommitment step to QSGR Added Generic and Specific scripts Updated Note and scripts Updated TCEQ section and scripts Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts Correct spelling and updated script | June 1, 2013 |
| 2.6 3.1 3.2 3.8 5.1 5.3 5.4 | 1.0 / 9 1.0 / 14 1.0 / 2 1.0 / 0 1.0 / 13 1.0 / 13 1.0 / 12 | Changed title name & updated step EMS Changes & added MMS Changes Updated steps Base Point Deviation & 10 Minutes Updated 1st note Moved procedures from Resource desk Updated step 1 in Watch & Emergency Notice Updated step Pilot Project WS ERS Updated step Reserves | July 15, 2013 |
| 2.6 3.2 3.8 4.1 | 1.0 / 10 1.0 / 3 1.0 / 1 1.0 / 12 | Updated MMS Changes Updated 1st Note Updated Unit & Load RRS Shortage & Not Dispatchable to SCED Updated Shutdown/Startup | August 9, 2013 |
| 3.8 | 1.0 / 2 | Updated Unit RRS Shortage, Load RRS Shortage, REG Shortage, & added Real-Time Non-Spin Shortage | September 27, 2013 |
| 2.4 3.1 3.2 3.3 3.4 3.5 3.7 4.1 5.1 5.2 5.3 5.4 5.5 6.1 6.2 6.3 6.4 7.1 8.1 | 1.0 / 2 1.0 / 15 1.0 / 4 1.0 / 12 1.0 / 9 1.0 / 7 1.0 / 4 1.0 / 13 1.0 / 14 1.0 / 9 1.0 / 14 1.0 / 13 1.0 / 4 1.0 / 4 1.0 / 7 1.0 / 6 1.0 / 6 1.0 / 4 1.0 / 5 | Updated step Log Updated step Frequency Deviations & step Log Updated step Log Updated step Log Updated step Log Added step RMR & updated step Log Updated step Log Updated step Log Updated step Log Updated step Log Updated step Log Updated step Log Updated step Log Updated step Log Updated step Log Updated step Log Updated note and step Log Updated step Log Added & updated step Log All procedures in this manual have been reviewed | December 13, 2013 |
| 2.6 3.3 5.1 | 1.0 / 11 1.0 / 13 1.0 / 15 | Updated for NPRR542 Updated for NPRR542 Updated for NPRR542, deleted West to North GTL and updated procedure for North to Houston to a new GTL | January 1, 2014 |
| 2.6 3.1 3.3 3.5 3.6 4.1 5.3 5.4 6.4 8.1 | 1.0 / 12 1.0 / 16 1.0 / 14 1.0 / 8 1.0 / 5 1.0 / 14 1.0 / 15 1.0 / 14 1.0 / 7 1.0 / 6 | Updated Site Failover Complete Updated VDI information, step Monitor/Deploy & step 10 Minutes in Response to Low Frequency Updated VDI information Updated VDI information Updated step Terminating Time Error Correction Updated VDI information Updated ERS, Media appeal, TCEQ and VDI information Updated steps Reserves and 1 in Restore firm load and step 2 in Move From EEA Level 2 to EEA Level 1 Updated Note Updated Requests to Decommit Self-committed Resource in Operating Period | April 4, 2014 |
| 2.2 3.1 3.3 4.1 5.1 5.2 6.2 6.3 | 1.0 / 2 1.0 / 17 1.0 / 15 1.0 / 15 1.0 / 16 1.0 / 10 1.0 / 8 1.0 / 7 | Added VDIs to Master QSEs Updated step BAAL Updated SCED Failure & SCED Data Input Failure steps Updated QSGR in Quick Start Generation Resource Added Note, updated Market Notices Advisory & Watch Updated Watch steps Updated Emergency Notice step Updated Emergency Notice step | June 1, 2014 |
| 3.5 5.3 | 1.0 /9 1.0 / 16 | Updated Deploying Non-Spin, added HASL Release & Recall Added Media Appeal | August 1, 2014 |
| 4.1 5.1 5.3 | 1.0 / 16 1.0 / 17 1.0 / 17 | Updated Reference section step 2 Updated Generic Script Added HASL Release step | October 1, 2014 |
| 2.3 2.4 2.6 3.3 3.5 5.1 5.3 | 1.0 / 1 1.0 / 3 1.0 / 13 1.0 / 16 1.0 / 10 1.0 / 18 1.0 / 18 | Updated all steps Updated step Send E-mail Deleted Site Failover with W-N Active & updated step If EBPs are Needed Updated 1st note & updated scripts Added new procedure, “Valley Generation” Updated GMD scripts Updated scripts to consolidate All procedures in this manual have been reviewed | December 15, 2014 |
| 6.2 | 1.0 / 9 | Updated Note and scripts | December 22, 2014 |
| 2.2 3.1 3.2 3.5 3.9 6.2 | 1.0 / 3 1.0 / 18 1.0 / 5 1.0 / 11 1.0 / 0 1.0 / 10 | Added Dispatch and VDI definitions Updated Objective and BAAL Updated procedure Updated step 1 and added Log on Valley Generation Added new procedure for NOGRR136 Updated scripts | March 1, 2015 |
| 3.1 3.3 3.5 3.10 4.1 5.1 | 1.0 / 19 1.0 / 17 1.0 / 12 1.0 / 0 1.0 / 17 1.0 / 19 | Clarification to step Frequency Deviation & Hydro Operating in Synch. Condenser Mode Updated Dispatch Instruction scripts Clarification to step HASL Release Manually Deploy RRS New GMD procedure Updated Dispatch Instruction scripts Deleted script for GMD | March 30, 2015 |
| 2.6 2.7 3.2 3.3 3.4 3.63.7 3.10 5.1 5.2 5.3 5.4 5.5 6.1 6.2 6.3 6.4 | 1.0 / 14 1.0 / 3 1.0 / 6 1.0 / 18 1.0 / 10 1.0 / 6 1.0 / 5 1.0 / 1 1.0 / 20 1.0 / 11 1.0 / 19 1.0 / 15 1.0 / 5 1.0 / 5 1.0 / 11 1.0 / 8 1.0 / 8 | Moved scripts to new script procedure Moved scripts to new script procedure Updated 1st note and moved scripts to new script procedure Updated step 2 on SCED Data Input Failure & moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Updated 4th bullet on Emergency Notice & moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure | May 1, 2015 |
| All Sections 2.6 3.5 3.9 3.10 5.1 5.2 6.3 | 1.0 / 1 1.0 / 15 1.0 / 13 1.0 / 1 1.0 / 2 1.0 / 21 1.0 / 12 1.0 / 9 | Added a “Q” for numbered QSE scripts Renamed section to Site Failovers and Database Loads Updated link for Monitor in the Valley Generation Updated 1st Note Updated Procedure Purpose and removed script Updated Specific Scripts, New GTC Updated Q#1, Q#2, Q#3, & Q#4 Script titles Removed Watch script | July 15, 2015 |
| 2.6 3.2 3.3 3.4 3.6 3.7 3.9 3.10 5.1 5.2 5.3 5.4 5.5 6.1 6.2 6.3 6.4 | 1.0 / 16 1.0 / 7 1.0 / 19 1.0 / 11 1.0 / 7 1.0 / 6 1.0 /2 1.0 / 3 1.0 / 21 1.0 / 13 1.0 / 20 1.0 / 16 1.0 / 6 1.0 / 6 1.0 / 12 1.0 / 10 1.0 / 9 | Updated step MMS Changes Typical Script Q#19 Updated step Site Failover Q#20 Updated step Site Failover Complete Q#21 Updated Step If EBP’s are needed Q#22 Updated step Site Failover Complete If EBP’s were needed Q#23 Updated step 2 Q#26 Updated SCED Failure step 2 Q#27 & step 4 Q#28 Updated SCED Data Input Failure step 1 Q#29 Updated RLC Failure step 2 Q#30 & step 4 Q#31 Updated LFC (AGC) Failure step 1 Typical Script step 2 Q#32, step 4 Typical script & Q#33 Updated EMMS (LFC and RLC/SCED) Failure step 1 Typical Script, step 2 Q#34, step 5 Typical Script & Q#35 Updated step 3 Q#36 Updated step Initiating Time Error Correction Q#37 Updated step Terminating Time Error Correction Q#38 Updated step Issue Watch and Deploy Non-Spin Q#39 Updated step Issue Emergency Notice & Deploy Load Resources Q#40 Updated step Recall Load Resources Q#41 Updated step Recall Non-Spin Q#42 Updated step Start CFC Test & End CFC Test Typical Scripts Updated step 1 Q#43 Updated step K Level Increases/Decreases Q#44 Updated step Cancel Q#45 Updated Title Operating Condition Script Updated step Hotline Q#46 Updated step Hotline Cancellation Q#47 Updated Title Specific Scripts for Transmission Operator [State Estimator/RTCA/VSAT] Updated step State Estimator/RTCA Not Solved In 30 MIN Q#48 & Q#49 Updated step VSAT Not Solved In 30 MIN Q#50 & Q#51 Updated step Qualifying Facility Directed to Operate Below LSL Q#52 & Q#53 Updated step New GTC Q#54 Updated step Transmission Watch Q#55 & Q#56 Updated Advisory step Issue Advisory Q#1 Updated Advisory step Cancel Advisory Q#2 Updated Watch step Issue Watch Q#3 Updated Watch step Cancel Watch Q#4 First Note, Updated Implement EEA Level 1 step EEA 1 PRC <2300 Q#5 & Q#6 Updated Implement EEA Level 2 step ERS Resources Q#7 Updated Implement EEA Level 2 step Load Resources Q#8 Updated Implement EEA Level 2 step When ERS Business Hours Change Q#9 Updated Implement EEA Level 3 step When ERS Business Hours Change Q#12, and Implement NPRR708 for EEAUpdated Restore Firm Load step 1 Q#13 Updated Move From EEA Level 3 to EEA Level 2 step 1 Q#14 Updated Move From EEA Level 2 to EEA Level 1 step 1 Q#15 Updated Move From EEA Level 1 to EEA Level 0 step 1 Q#16 Updated Cancel Watch step 1 Q#17 Updated step Return to Normal QSE Notification Q#57 Updated step Emergency Notice Q#61 Updated step Emergency Notice Q#65 Updated step Emergency Notice Q#69 Updated step OCN/Advisory/Watch Q#70 All procedures in this manual have been reviewed | December 31, 2015 |
| 1.3 2.1 3.3 5.1 | 1.0 / 2 1.0 / 3 1.0 / 20 1.0 / 22 | Removed Interchange Coordinator Updated System Operator Responsibility and Authority Updated SCED Failure Note Corrected spelling Qualifying Facility Directed to Operate below LSL Q#52 | March 1, 2016 |
| 2.4 3.1 3.2 4.1 | 1.0 / 4 1.0 / 20 1.0 / 8 1.0 / 18 | Added 2nd Send E-Mail Updated Frequency bias and BAAL step Updated Down Ramp Event step 2 Updated QSGR Qualification Test | April 29, 2016 |
| 2.1 2.2 3.1 3.3 3.5 3.9 4.1 5.1 5.5 | 1.0 / 4 1.0 / 4 1.0 / 21 1.0 / 21 1.0 / 14 1.0 / 3 1.0 / 19 1.0 / 23 1.0 / 7 | Updated for COM-002-4 Updated for COM-002-4 Updated for BAL-001-2 and COM-002-4 Updated for COM-002-4 Updated Deploying Non-Spin step Updated for COM-002-4 Updated for COM-002-4 Updated for COM-002-4 Updated for COM-002-4 | June 30, 2016 |
| 5.3 | 1.0 / 21 | Changed Business Hour to Time Period | July 15, 2016 |
| 2.2 3.3 | 1.0 / 5 1.0 / 22 | Added Hotline Call Communication Note Added SCED Failure Frequency Guidelines Updated LFC Failure Step 2 Q#32 Script Title Updated LFC Failure Step 4 Q#33 Script Title Updated EMMS Failure step 2 Q#34 Script Title Updated EMMS Failure step 5 Q#35 Script Title | September 30, 2016 |
| 3.5 5.1 | 1.0 / 15 1.0 / 24 | Updated Valley Generation step 1 Added Specific Scripts for Transmission Operator step Transmission Emergency script Q#71 | November 2, 2016 |
| 4.1 | 1.0 / 20 | Added Real-Time Data Issues known by the QSE All procedures in this manual have been reviewed | December 30, 2016 |
| 1.3 2.1 2.5 2.6 2.7 3.2 3.10 5.1 5.3 5.5 6.1 6.2 6.3 8.1 | 1.0 / 3 1.0 / 5 1.0 / 5 1.0 / 17 1.0 / 4 1.0 / 9 1.0 / 4 1.0 / 25 1.0 / 22 1.0 / 8 1.0 / 7 1.0 / 13 1.0 / 11 1.0 / 7 | Updated Roles/Responsibilities section Updated for IRO-001-4 Updated categories to show RAS Updated procedure purpose Updated procedure purpose Deleted ELRAS and held location open Updated procedure purpose Updated title and all 1st steps Removed step WS ERS Added Implement EEA Level 3 step EEA3 PRC <1000 MW Updated first note Updated procedure purpose Updated procedure purpose Updated procedure purpose Updated procedure purpose | March 31, 2017 |
| 3.1 | 1.0 / 22 | Updated Frequency bias | April 4, 2017 |
| 3.3 5.1 | 1.0 / 23 1.0 / 26 | Added section on ICCP Outages Updated Transmission Watch | April 6, 2017 |
| 3.1 3.5 | 1.0 / 23 1.0 / 16 | Updated Response to Low Frequency step Monitor/Deploy Updated Insufficient Generation step Deploying Non-Spin | June 1, 2017 |
| 3.1 5.3 | 1.0 / 24 1.0 / 23 | Updated Response to Low Frequency step 25 Minutes Updated 1st note, step EEA Level 2 and EEA Level 3 | June 30, 2017 |
| 2.4 3.1 5.3 | 1.0 / 5 1.0 / 25 1.0 / 24 | Updated steps Added note Response to Low Frequency Updated step 20 Minutes and added scripts Added note Implement EEA Level 2 and Level 3 | July 28, 2017 |
| 3.1 3.3 | 1.0 / 26 1.0 / 24 | Updated Response to Low Frequency step 10 Minutes Updated LFC (AGC) Failure steps 1 & 3 Updated EMMS (LFC and RLC/SCED) Failure steps 1,3, &4 | September 29, 2017 |
| 3.9 | 1.0 / 4 | Updated note | October 31, 2017 |
| 2.4 3.4 7.1 | 1.0 / 6 1.0 / 12 1.0 / 5 | All procedures in this manual have been reviewed Updated steps Updated procedure for BAL-002-2 Updated Primary Control Center 4th note | December 28, 2017 |
| 3.3 3.5 3.9 | 1.0 / 25 1.0 / 17 1.0 / 5 | Updated ICCP Ouages to include MIS and outage scheduler Added Note Updated Start CFC Test & End CFC Test | February 28, 2018 |
| 3.1 | 1.0 / 27 | Updated Maintain System Frequency step Objective | April 5, 2018 |
| 2.2 2.7 3.3 3.9 | 1.0 / 6 1.0 / 5 1.0 / 26 1.0 / 6 | Updated procedure purpose Updated steps Updated steps LFC (AGC) Failure and EMMS (LFC and RLC/SCED) Updated steps | May 1, 2018 |
| 3.1 3.3 3.9 5.3 | 1.0 / 28 - / 27 1.0 / 7 1.0 / 25 | Updated Response to High Frequency & Response to Low Frequency steps Monitor Updated SCED Failure step3 Updated SCED Data Input Failure step 2 Updated RLC Failure step NOTE and step 3 Updated LFC (AGC) Failure NOTE, step 1 & 5 Added step 4. Moved step 4 to step 5 Updated EMMS (LFC and RLC/SCED) Failure step 1, 3, & 5 Updated Note Added Implement EEA Level 3 step | August 31, 2018 |
| 3.1 5.1 | 1.0 / 29 1.0 / 27 | Updated Monitor Frequency for the Loss of EMS or Site Failover Updated for NPRR 825 | October 1, 2018 |
| 3.3 5.3 | 1.0 / 28 1.0 / 26 | Added STATE ESTIMATOR (SE)/Real-Time Contingency Analysis (RTCA) Deleted duplicate Log step All procedures in this manual have been reviewed | December 28, 2018 |
| 2.4 | 1.0 / 7 | Updated steps | January 31, 2019 |
| 3.1 | 1.0 / 30 | Updated Maintain System Frequency step Objective | April 1, 2019 |
| 3.1 4.1 | 1.0 / 31 1.0 / 21 | Updated Response to High Frequency step Monitor & Response to Low Frequency steps Updated SCED Solution Time Parameter step Automatic Trigger | August 1, 2019 |
| 3.5 5.3 | 1.0 / 18 1.0 / 27 | Updated Manually Deploy RRS and Recall steps Added Implement EEA Level 1 step | November 1, 2019 |