- Power Operations Bulletin # 910

ERCOT has posted/revised the Reliability Risk Desk manual.

A copy of the procedure can be found at:

- http://www.ercot.com/mktrules/guides/procedures/index.html

## 4.1	Responding to Wind Forecast Errors

Procedure Purpose:  Make corrections to errors in the weather forecast data (in EMS) and/or  switch between two wind forecasts needed to contribute to reliable system performance.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 3 | Effective Date: November 1, 2019 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | The wind forecasts produced by both UL (formerly AWS Trupower) and Energy & Meteo (E&M) provide enhanced situational awareness by additional means of validating the expected wind conditions. The selected wind forecast between two is sent to Wind QSEs to update their COP and used by the downstream EMS applications. |
| NOTE | Do not continuously switch between two wind forecasting services for a small gain in accuracy (i.e. “chasing the forecast”) |
| STWPF Selection Change due to forecast vs. output deviation | IF: - The end of adjustment period selected wind forecast which is currently in use has been greater than the actual wind HSL for more than 2000 MW for at least three hours or 3000 MW for at least one hour or reliability concern and the other vendor forecast has been more accurate; THEN: - Log the period of time for which the forecast has been underperforming and the accuracy of both forecasts. Inform the Shift Supervisor and potentially switch forecast selection to alternative wind forecast which has been more accurate, - E-mail the information to: - Operations Analysis - 1 ERCOT Shift Supervisors Reference Display: ERCOT EMP Applications>Wind Forecasting Service>Hourly EMS wind forecast and other necessary displays. |
| NOTE | The projected wind ramp rate (PWRR) calculation is such that it will revert to using persistence (PWRR=0) if the actual wind HSL has been ramping in the opposite direction of the PWRR value for more than 25 minutes (5 intervals). RLC will set the PWRR to 0 to minimize the impact and then cancel the flag after the PWRR is forecasting the ramp to be the same as the actual ramp again. |
| Intra-Hour wind Forecast | IF: - Alarmed, make sure frequency isn’t rapidly declining and wind hasn’t turned direction and is ramping very fast (really only need to be concerned when getting above 300-400 MW per 5 minutes and causing frequency to decline below 59.95 Hz). If frequency does drag and regulation is exhausted, the Real-Time Desk should follow their procedure for manually running SCED. Watch the PWRR and wind ramp to help inform the Real-Time Desk; THEN: - Notify an Operations Analysis Engineer to do further analysis, - E-mail the information to: - Operations Analysis - 1 ERCOT Shift Supervisors |
| LOG | Log all actions. |

## 4.7  Weather Forecast Errors

Procedure Purpose:  Make corrections to errors in the weather forecast data (in EMS) to contribute to reliable system performance.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 0 | Effective Date: November 27, 2019 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Weather Forecast |  |
| Weather Forecast | IF: - The weather forecast seems invalid; THEN: - Notify the ERCOT Meteorologist and/or Load Forecasting team, - E-mail the information to: - 1 ERCOT EMMS Production - Load Forecasting & Analysis - 1 ERCOT Shift Supervisors |
| LOG | Log all actions. |

## 5.1	STNET Study

Procedure Purpose: To review and analyze future voltage violations.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standand | IRO-001-4 R1 | TOP-001-4 R2 | VAR-001-5 R2 |  |

| Version: 1 | Revision: 4 | Effective Date: November 1, 2019 |
| --- | --- | --- |

| Step | Action |  |
| --- | --- | --- |
| ### Reliability Risk Desk performs STNET Study |  |  |
| NOTE | Each hour run a STNET study for four hours out (example it is 0100, run study for 0500) to review voltage violations. |  |
| Voltage Contingencies | IF: - Voltage contingencies exist; THEN: - Check “Voltage Tracking Issues spreadsheet” on Sharepoint to ensure the contingency is not listed. - If not listed, convey the voltage violations to the Transmission and Security Operator with the potential resolution - Validate the resolution - Create a savecase, use naming convention “SC_RRD(HE)_(DATE) - Make at least one detailed log entry per shift that the studies are being executed. If any new voltage violations are identified that do not have a solution, log the information and notify the Transmission and Security Operator of the new violation(s) - Update the “Voltage Tracking Issues spreadsheet” listing the new voltage violation with the contingency resolution. IF: - Unsolved contingencies exists; THEN: - Communicate any unsolved contingency to the Shift Engineer and Transmission Security Desk Operator with potential solutions. - Some potential solutions could be transmission switching, creation of a manual constraint, bringing on an additional Resource, returning a planned outage, or development of a CMP. - Validate the resolution - Update the “Voltage Tracking Issues spreadsheet” listing the new unsolved contingency with the contingency resolution. |  |
| Violated Constraints | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP Binding Constraint Summary Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP Constraint Summary REVIEW: - Violated constraints. If needed, notify Operations Support Engineer to determine the validity; IF: - Invalid, no further action is required; IF: - Valid; AND - Related to a phase shifter tap settings, THEN: - Notify Operations Support Engineer to determine and determine if adjusting a Phase Shifter would reduce the flow, - Create Suggestion Plan for Constraint, - Manually commit resources as needed - Refer to Desktop Guide Reliability Risk Desk Section 2.5 and 2.6. |  |
| Phase Angles | Monitor phase angles during the 4 hour ahead voltage studies IF: - Phase angle exceedances exists; THEN: - Communicate any phase angle exceedances to the Shift Engineer and Transmission Security Desk Operator for potential solutions. - Some potential solutions could be transmission switching, creation of a manual constraint, bringing on an additional Resource, returning a planned outage, or development of a CMP. |  |
| LOG | Log actions taken. |  |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Hartmann, Gaddy, Self, and Frosch | Preparers | January 24, 2017 |
| Hartmann, Gaddy and Frosch | Procedure writers and editors | March 27, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | May 26, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | June 23, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | July 24, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | September 27, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | December 22, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | February 22, 2018 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | March 26, 2018 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | April 27, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | May 25, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | August 24, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | December 21, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | January 25, 2019 |
| Hartmann, Gaddy and Pence | Procedure writers and editors | July 29, 2019 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | October 29, 2019 |

Manual Change History

| Procedure | Ver/Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All | 1.0 / 0 | New procedures | January 30, 2017 |
| 2.1 3.1 4.4 5.1 7.1 7.2 9.1 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Updated System Operator Responsibility and Authority Updated Up Ramp Event step 2 Updated Panhandle Region Updated Reliability Risk Desk performs STNET Study Updated title and all 1st steps Updated Implement EEA Level 3 steps Updated Title | March 31, 2017 |
| 3.1 | 1.0 / 2 | Updated Down Ramp Event step 1, 2 & 3 Updated Up Ramp Event step 1 & 2 | June 1, 2017 |
| 3.1 7.2 | 1.0 / 3 1.0 / 2 | Updated Down Ramp Event step 2 Updated 1st note, step 1 changed to EEA Level 3 | June 30, 2017 |
| 7.2 | 1.0 / 3 | Added note Implement EEA Level 2 and Level 3 | July 28, 2017 |
| 7.2 | 1.0 / 4 | Updated Implement EEA Level 3 | September 29, 2017 |
| 8.1 | 1.0 / 1 | All procedures in this manual have been reviewed Updated Primary Control Center 4th note | December 28, 2017 |
| 3.3 | 1.0 / 1 | Updated Day Ahead RRS Sufficiency Monitoring, moved Real-time RRS Sufficiency Monitoring down, added Look Ahead Critical Inertia Level Sufficiency Monitoring and Real-time Critical Inertia Level Sufficiency Monitoring | February 28, 2018 |
| 9.1 | 1.0 / 2 | Updated Note | March 30, 2018 |
| 2.2 | 1.0 / 1 | Updated procedure purpose | May 1, 2018 |
| 5.1 | 1.0 / 2 | Added Phase Angles steps | May 31, 2018 |
| 5.1 | 1.0 / 3 | Updated and named step to Voltage contingencies | August 31, 2018 |
| 4.1 4.2 | 1.0 / 1 1.0 / 1 | Updated procedure purpose, added note and updated step Updated procedure purpose, added note and updated step All procedures in this manual have been reviewed | December 28, 2018 |
| 4.2 | 1.0 / 2 | Updated steps | January 31, 2019 |
| 3.1 4.1 | 1.0 / 3 1.0 / 2 | Deleted all steps Monitor Large Ramp Events Added Intra-Hour Wind Forecast and added Note Updated STWPF Selection Change due to forecast vs. output deviation and added Note | August 1, 2019 |
| 4.1 4.7 5.1 | 1.0 / 3 1.0 / 0 1.0 / 4 | Removed Weather Forecast Created section Weather Forecast Errors Updated Voltage Contingencies | November 1, 2019 |