- Power Operations Bulletin # 919

ERCOT has posted/revised the Reliability Risk Desk manual.

A copy of the procedure can be found at:

- http://www.ercot.com/mktrules/guides/procedures/index.html

## 7.2	Implement EEA Levels

Procedure Purpose:  To provide for maximum possible continuity of service while maintaining the integrity of the ERCOT system to reduce the chance of cascading outages. If required to assist other Desk during an EEA event refer to appropriate Operating Procedures.

| Protocol Reference | 6.5.7.6.2.2(1)(b) & (13) | 6.5.9.4 | 6.5.9.4.2 |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.5.3 | 4.5.3.1 | 4.5.3.2 | 4.5.3.3 |
|  | 4.5.3.4 |  |  |  |
| NERC Standard | EOP-011-1 R2, R2.1, R2.2, R2.2.3, R2.2.3.1, R2.2.3.4 |  |  |  |

| Version: 1 | Revision: 5 | Effective Date: January 1, 2020 |
| --- | --- | --- |

|  | Step |  | Action |  |
| --- | --- | --- | --- | --- |
|  | NOTE |  | - IF steady state system frequency falls below 59.91 Hz, ERCOT CAN immediately implement EEA 3. - IF steady state system frequency falls below 59.5 Hz, ERCOT SHALL immediately implement EEA 3. |  |
|  | TCEQ |  | When increased generation is requested during EEA events, Texas Commission on Environmental Quality (TCEQ) will exercise enforcement discretion for exceedances of emission limits as well as operational limits for power generating plants for Generators who exceed air permit limits in order to maximize generation for the duration of the EEA event. ERCOT General Council will send out a Market Notice each time ERCOT enters into an EEA with this reminder. |  |
| ### Implement EEA Level 1 |  |  |  |  |
| 1 |  | IF: - PRC < 2300 MW; |  |  |
| 2 |  | Assist Control Room as needed and monitor Intermittent Renewable Resources (IRR). |  |  |
| LOG |  | Log all actions. |  |  |
| ### Implement EEA Level 2 |  |  |  |  |
|  | Note |  | ERCOT may declare an EEA Level 2 when the clock-minute average system frequency falls below 59.91 Hz for 15 consecutive minutes. |  |
|  | 1 |  | IF: - PRC < 1750 MW or unable to maintain system frequency at 59.91 Hz and is not projected to be recovered above 1750 MW within 30 minutes without the use of EEA Level 2; |  |
|  | 2 |  | Assist Control Room as needed and monitor Intermittent Renewable Resources (IRR). |  |
|  | LOG |  | Log all actions. |  |
| ### Implement EEA Level 3 |  |  |  |  |
|  | Note |  | ERCOT may declare an EEA Level 3 when the clock-minute average system frequency falls below 59.91 Hz for 20 consecutive minutes. |  |
|  | EEA3 PRC <1430 MW |  | ERCOT will declare an EEA Level 3 when PRC cannot be maintained above 1,430 MW. |  |
|  | EEA3 Unable to Maintain 59.91 Hz or PRC <1000 MW |  | IF: - PRC <1000 MW or Unable to maintain system frequency at 59.91 Hz and is not projected to be recovered above 1000 MW or 59.91 Hz within 25 minutes without the use of EEA Level 3; THEN: - Assist Control Room as needed and monitor Intermittent Renewable Resources (IRR). |  |
|  | LOG |  | Log all actions. |  |

## 7.3	Restore EEA Levels

Procedure Purpose:  To restore the ERCOT grid to normal state as system conditions warrant while recovering from an EEA event.

| Protocol Reference | 6.5.9.4.3 |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.5.3.5 |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 1 | Effective Date: January 1, 2020 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| RESERVES | 1430 MW of PRC must be restored within 90 minutes. |
| ### Restore Firm Load |  |
| 1 | IF: - Sufficient Regulation Service exist to control to 60 Hz, AND - PRC – Regulation Up Responsibility ≥ 1430 MW for the last 15 minutes; THEN: - Transmission Operator will restore firm load. - Assist Control Room as needed and monitor Intermittent Renewable Resources (IRR). |
| ### Move from EEA Level 3 to EEA Level 2 |  |
| 1 | IF: - Sufficient Regulation Service exist to control to 60 Hz, AND - PRC is ≥ 1750 MW, AND - All firm load have been instructed to be restored; - Assist Control Room as needed and monitor Intermittent Renewable Resources (IRR). |
| ### Move from EEA Level 2 to EEA Level 1 |  |
| 1 | IF: - The system can maintain PRC ≥ 2300 MW, AND - All Load Resources have been instructed to be restored; - Assist Control Room as needed and monitor Intermittent Renewable Resources (IRR). |
| ### Move from EEA Level 1 to EEA 0 |  |
| 1 | IF: - The system can maintain PRC ≥ 2300 MW, AND - All uncommitted units secured in EEA 1 can be released, AND - Emergency energy from the DC Ties is no longer needed; - Assist Control Room as needed and monitor Intermittent Renewable Resources (IRR). |
| LOG | Log all actions. |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Hartmann, Gaddy, Self, and Frosch | Preparers | January 24, 2017 |
| Hartmann, Gaddy and Frosch | Procedure writers and editors | March 27, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | May 26, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | June 23, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | July 24, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | September 27, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | December 22, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | February 22, 2018 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | March 26, 2018 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | April 27, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | May 25, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | August 24, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | December 21, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | January 25, 2019 |
| Hartmann, Gaddy and Pence | Procedure writers and editors | July 29, 2019 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | October 29, 2019 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | December 20, 2019 |

Manual Change History

| Procedure | Ver/Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All | 1.0 / 0 | New procedures | January 30, 2017 |
| 2.1 3.1 4.4 5.1 7.1 7.2 9.1 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Updated System Operator Responsibility and Authority Updated Up Ramp Event step 2 Updated Panhandle Region Updated Reliability Risk Desk performs STNET Study Updated title and all 1st steps Updated Implement EEA Level 3 steps Updated Title | March 31, 2017 |
| 3.1 | 1.0 / 2 | Updated Down Ramp Event step 1, 2 & 3 Updated Up Ramp Event step 1 & 2 | June 1, 2017 |
| 3.1 7.2 | 1.0 / 3 1.0 / 2 | Updated Down Ramp Event step 2 Updated 1st note, step 1 changed to EEA Level 3 | June 30, 2017 |
| 7.2 | 1.0 / 3 | Added note Implement EEA Level 2 and Level 3 | July 28, 2017 |
| 7.2 | 1.0 / 4 | Updated Implement EEA Level 3 | September 29, 2017 |
| 8.1 | 1.0 / 1 | All procedures in this manual have been reviewed Updated Primary Control Center 4th note | December 28, 2017 |
| 3.3 | 1.0 / 1 | Updated Day Ahead RRS Sufficiency Monitoring, moved Real-time RRS Sufficiency Monitoring down, added Look Ahead Critical Inertia Level Sufficiency Monitoring and Real-time Critical Inertia Level Sufficiency Monitoring | February 28, 2018 |
| 9.1 | 1.0 / 2 | Updated Note | March 30, 2018 |
| 2.2 | 1.0 / 1 | Updated procedure purpose | May 1, 2018 |
| 5.1 | 1.0 / 2 | Added Phase Angles steps | May 31, 2018 |
| 5.1 | 1.0 / 3 | Updated and named step to Voltage contingencies | August 31, 2018 |
| 4.1 4.2 | 1.0 / 1 1.0 / 1 | Updated procedure purpose, added note and updated step Updated procedure purpose, added note and updated step All procedures in this manual have been reviewed | December 28, 2018 |
| 4.2 | 1.0 / 2 | Updated steps | January 31, 2019 |
| 3.1 4.1 | 1.0 / 3 1.0 / 2 | Deleted all steps Monitor Large Ramp Events Added Intra-Hour Wind Forecast and added Note Updated STWPF Selection Change due to forecast vs. output deviation and added Note | August 1, 2019 |
| 4.1 4.7 5.1 | 1.0 / 3 1.0 / 0 1.0 / 4 | Removed Weather Forecast Created section Weather Forecast Errors Updated Voltage Contingencies | November 1, 2019 |
| 7.2 7.3 | 1.0 / 5 1.0 / 1 | Updated MSSC Updated MSSC All procedures in this manual have been reviewed | January 1, 2020 |