- Power Operations Bulletin # 923

ERCOT has posted/revised the Shift Supervisor Desk manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

## http://www.ercot.com/mktrules/guides/procedures/index.html

## 3.3	Disseminating Information to System Security Response Group (SSRG)

Procedure Purpose: To communicate information concerning disturbances or unusual occurrences to appropriate parties in the Interconnection.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 3.8(4) |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 15 | Effective Date: January 1, 2020 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | Threat alerts can be viewed at either of the following links: https://www.eisac.com/, OR http://www.dhs.gov/files/programs/ntas.shtm The definitions for the threat alert levels are listed in the Security Alert Plan which can be found in the Operating Procedure Manual. |
| NOTE | - The SSRG e-mail exploder list is used to disseminate information to the SSRG members of the ERCOT Region when an SSRG conference call is not necessary. - This information is intended for use within the industry and not for public release. - At the beginning of each e-mail state the follow “This information is intended for use within the industry and not for public release” - At the bottom of each e-mail, be sure to include a Confidentiality Notice and your signature. - The Reliability Coordinator Information System (RCIS) is used to disseminate information to other RCs in other Interconnections. - Do not list the entity name on the SSRG e-mails or on the RCIS. |
| ### Events not Considered an Act of Suspected Sabotage |  |
| 1 | IF: - A TO or QSE reports an event that is not considered an act of suspected sabotage, such as the following: - Copper thefts - Substation break-in - Vandalism - Malicious mischief - Suspicious photos THEN: - Disseminate this information using the ‘SSRG’ distribution list: - State in the e-mail that the event is “currently not considered as an act of suspected sabotage”. - State the county of the event |
| 2 | MONITOR: - The RCIS (CIP Free Form) for ERCOT events which meet the criteria in step 1 that should be disseminated to SSRG; THEN: - Follow instructions in step 1 to disseminate the information |
| LOG | Log all actions. |
| ### Suspected Sabotage or Sabotage Events |  |
| Physical | When notified by Physical Security of an actual or suspected physical sabotage at the ERCOT facilities, refer to section 6.1 for reporting requirements. An RCIS posting and SSRG email may also be required. |
| Cyber | When notified by Cyber Security of an actual or suspected event at ERCOT, Refer to section 6.1 for reporting requirements. An RCIS posting (CIP Free Form) and SSRG email may also be required. |
| 1 | IF: - A TO or QSE reports an act of suspected sabotage or a sabotage event; THEN: - Verify that the FBI has been notified, - Disseminate the information using the ‘SSRG’ distribution list: - State in the e-mail that the event is considered “an act of suspected sabotage OR further investigation/information is needed to determine if event is an act of suspected sabotage,” - State the county the event occurred ONCE: - Enough information has been received; NOTIFY: - TOs and QSEs via Hotline with information you have, - Post on the RCIS using “CIP Free Form”, - Coordinate with the Director Control Room Operations and/or Designee to determine if procedure 3.4 SSRG Conference Calls is necessary and for any NERC and DOE reporting requirements. Typical Hotline Script: “This is ERCOT operator [first and last name], at [xx:xx], ERCOT notified the System Security Response Group (SSRG) of a suspected sabotage event [give information]. Please notify your SSRG representative.” |
| 2 | WHEN: - Updates are received; THEN: - Send an updated e-mail to the ‘SSRG’ distribution list, - Update RCIS posting as needed |
| LOG | Log all actions. |

## 3.4	SSRG Conference Calls

Procedure Purpose: To communicate information concerning disturbances or unusual occurrences to appropriate parties in the ERCOT Region by making a SSRG conference call.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 11 | Effective Date: January 1, 2020 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | The SSRG conference call will be used to inform the SSRG members of suspected sabotage or sabotage events, including multi-site sabotage events affecting larger portions of the Interconnection. The SSRG conference call will also be used for the following: - When the Threat Alert Level has increased, - To disseminate information and develop plans related to system emergencies and business continuity threats, - To conduct quarterly tests with the minimum objective of reviewing and updating the contact list (test to be conducted in February, May, August and November); AND - For any other events as warranted by the Director Control Room Operations and/or Designee Refer to Hotline and email scripts below for notifications. |
| Threat & Emergency Classifications | Threats and emergencies can be classified as, but are not limited to, the following four SSRG event-types: 1. Internal to ERCOT ISO: Physical Security: Verifiable attacks or sabotage, or threats of attacks or sabotage that could jeopardize the operation of physical equipment within the electrical boundaries of the ERCOT grid that have a direct effect on the reliability of the ERCOT grid. This could be, but is not limited to, generation equipment, transmission equipment, and communication equipment. b. Cyber Security: Verifiable loss of control of the ERCOT EMS or MMS that is identified by EMMS Production Support as an actual or probable act of sabotage or the loss of control by any TOs or QSEs EMS Systems that is reported to ERCOT as an act of sabotage. 2. External to ERCOT ISO: a. Physical Security: Verifiable attacks or sabotage, or threats of attacks or sabotage that could jeopardize the operation of physical equipment in any electrical sector outside of the boundaries of ERCOT. b. Cyber Security: Verifiable loss of control over the EMS System of any participant in the electrical sector outside of the boundaries of ERCOT that is identified as an actual or probable act of sabotage. 3. Pandemic 4. Other unforeseen business continuity events (not to include grid instability) |
| QSE Notification | Using the Hotline, notify the QSEs of the SSRG conference call: Typical Hotline Script: “This is [first and last name] at ERCOT. There will be an SSRG conference call today at [time] Central Prevailing Time. The topic will be [quarterly test call, physical security, cyber security, pandemic or other topic]. Please notify your SSRG representative. The conference call number is 1-866-642-1665. Participants pass code is [code]. Any questions? Thank you.” |
| TO Notification | Using the Hotline, notify the TOs of the SSRG conference call: Typical Hotline Script: “This is [first and last name] at ERCOT. There will be an SSRG conference call today at [time] Central Prevailing Time. The topic will be [quarterly test call, physical security, cyber security, pandemic or other topic]. Please notify your SSRG representative. The conference call number is 1-866-642-1665. Participants pass code is [code]. Any questions? Thank you.” |
| Send E-mail | Send an e-mail to “1 SSRG” to make notification of the SSRG conference call. Typical Subject line for e-mail: SSRG conference call Typical Script for e-mail: An SSRG conference call has been scheduled for today at [time] Central Prevailing Time (CPT). The topic will be [quarterly test call, physical security, cyber security, pandemic or other topic]. The conference call number is 1-866-642-1665. Participant pass code is [code]. Participation is mandatory. Include signature on email. |
| Log | Log all actions. |

## 3.6	Monitoring the IROL

Procedure Purpose: To collect data on the  North – Houston VSAT voltage stability limit for the NERC Reliability Metric.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | TOP-001-4 R12 |  |  |  |

| Version: 1 | Revision: 6 | Effective Date: January 1, 2020 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| IROL | The North to Houston is an IROL; the actual flow MUST NOT exceed the limit for more than 30 minutes. This is a violation of the NERC Reliability Standards. |
| NERC | Ensure that the transmission system is operated so that instability, uncontrolled separation, or cascading outages will not occur as a result of the most severe single Contingency and specified multiple Contingencies. |
| 1 | Monitor N-H voltage limits. |
| 2 | If the N-H voltage stability exceed the limit at any time: - Log it under log type “Exceeding Limits”. - Include the date and time of the violation - The system conditions that caused the violation. - Run a System Security Analysis (Real Time Snapshot) Study near the highest flow. (usually run by the Operations Support Engineer) - Save the snapshot in the STNET directory. If the N-H voltage stability limit is exceeded for more than 30 consecutive minutes, notify the Director Control Room Operations and/or Designee immediately. |
| 3 | Notify by e-mail (including data from step 2) - Shift Supervisors - Ops Support Engineering - Operations Analysis |

## 3.7	Monitoring Transmission Congestion

Procedure Purpose:  Monitoring transmission congestion to ensure ERCOT remains in a secure state.

| Protocol Reference | 6.3(3) |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 8 | Effective Date: January 1, 2020 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| TCM | VERIFY: - Constraints with a 2% shift factor or greater are activated at 98%. IF: - A constraint is unsolved in SCED; ENSURE: - All appropriate steps have been taken to resolve (T/S desk section 4.1 Managing Constraints in SCED step 2) IF: - Constraint remains unsolved in SCED; ENSURE: - The Operations Support Engineer is developing a TOAP or MP. IF: - A post-contingency overload reaches 125%; ENSURE: - The Operations Support Engineer has validated whether it is an IROL. |
| RTMONI | VERIFY: - The GTLs in RTMONI are being updated in a timely manner. - Assign this task to another desk if needed |
| LMP Map | Monitor the real-time LMP map: IF: - Any LMP appears unreasonable; THEN: - Notify Director Control Room Operations or Designee, and - Ensure transmission congestion is solvable and not being over-constrained. |
| South DC Ties | Ensure all available generation has been committed and the constraint binding before curtailing any South DC-Ties. Curtail only enough to maximize the flow across the South DC-Ties at all times. |

## 4.1	Resource Testing and In-Service Approvals

Procedure Purpose: This procedure provides direction and guidelines for conducting various testing and approval processes for resources and transmission elements.

| Protocol Reference | 3.3.1 | 6.5.7.8(1) | 8.5.1.1 | 8.5.1.2 |
| --- | --- | --- | --- | --- |
| Guide Reference | 3.3.2.2 |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 15 |  |  | Effective Date: January 1, 2020 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Step |  | Action |  |  |  |  |  |
| ### Unit Testing |  |  |  |  |  |  |  |
| NOTE |  | QSEs will submit test requests to shiftsupv@ercot.com. If e-mail is down, a fax will be accepted at (512) 248-6858. Test request forms are located on the ERCOT website under ‘Operating Procedures’. |  |  |  |  |  |
| 1 |  | As requests for unit tests are received, make every reasonable effort to accommodate testing. Reasons for not accommodating testing: - Unit has best shift factor to manage congestion for an outage. Without unit, contingency may reach max shadow price and become unsolvable, - The request exceeds 7 days, - A pattern of repeated requests for the same unit(s) indicate that abuse of the testing privilege may be taking place. If any request is refused for this reason, notify the Director Control Room Operations and/or Designee. |  |  |  |  |  |
| CAUTION |  | If deployment of the testing unit is necessary to maintain system security, instruct the test be canceled and deploy as needed. |  |  |  |  |  |
| NOTE |  | The tests mentioned below are not an exhausted list, they are tests that required coordination with other ERCOT departments. |  |  |  |  |  |
| OK to Test |  | If the testing can be accommodated, RESPOND via e-mail or fax to the requesting party similar to the following: “ERCOT approves. ERCOT intends to make system adjustments to accommodate this testing to the extent possible consistent with system security. This intent is NOT a guarantee of accommodation”. ___________________ (Shift Supervisor) |  |  |  |  |  |
| Not OK to Test |  | IF the request cannot be accommodated, RESPOND via e-mail or fax to the requesting party similar to the following: “ERCOT cannot accommodate the request for the following reason(s) : <List reasons>”. __________________ (Shift Supervisor) |  |  |  |  |  |
| ### Approved Resources to be ONTEST |  |  |  |  |  |  |  |
| Approval |  | - As Resource tests are approved, update “Approved Unit Tests” spreadsheet located on the System Operations SharePoint. - All operators will be able to view the list to determine which resources are approved to use the status of ONTEST. |  |  |  |  |  |
| ### In Service Approval (or Approval to Energize) |  |  |  |  |  |  |  |
| 1 |  | IF: - A TO or QSE makes a request to energize new or relocated equipment; THEN: - Review notification provided by Operations Support Engineering, - Approve the request if notification has been provided; IF: - The equipment has not been approved by Operations Support Engineering, THEN: - Delay the request and notify Operations Support Engineer. |  |  |  |  |  |
| ### Ancillary Service Testing Coordination |  |  |  |  |  |  |  |
| 1 |  | Ancillary Service Qualification Testing will be done in coordination with Operations Analysis and EMMS Production Support. IF: - A QSE requests an Ancillary Service Qualification Test; VERIFY: - A Wholesale Account Manager is in the notification or instruct the QSE representative to notify their Wholesale Account Manager to start the process. |  |  |  |  |  |
| 2 |  | The coordination of the testing times will be between System Operations, Operations Analysis and EMMS Production Support. When contacted by Operations Analysis: - Wholesale Account Manager will notify QSE of scheduled test, - Ensure reliable conditions exist at all times. |  |  |  |  |  |
| Log |  | Log all actions. |  |  |  |  |  |
| ### Coordinated Reactive Tests |  |  |  |  |  |  |  |
| NOTE |  | The Resource Entity requesting to perform a Coordinated Test will provide ERCOT Operations and the TO with notice of the proposed test date before 1500 on the day prior to the day of the test. Requests shall be made between 0800 and 1700 on Business Days. Upon receipt of a request for test, ERCOT Operations and the TO will evaluate the expected conditions and determine whether ERCOT System conditions are conducive to a valid test can be created through coordinated network switching, modification of the generation reactive dispatch of nearby Generation Resources, or by some other means. Having established that suitable ERCOT System conditions exist or can be created, ERCOT Operations, and the TO shall confirm with the Resource Entity and the QSE the agreed upon test time and date or a rejection of the test time and date before 1700 on the day prior to the day of the test. |  |  |  |  |  |
| 1 |  | Coordinated Reactive Tests will be done in coordination with System Operations, Resource Integration Department, the Transmission Operator (TO), and the Qualified Scheduling Entity (QSE). WHEN: - A QSE makes a request for a Coordinate Reactive Test; VERIFY: - Date/Time of Testing - MVAR Leading and/or Lagging expected during the test - CURL/D-Curve is attached - Estimated MW output If all information is included in the test request, proceed to step 2. If not, reply to e-mail from QSE and request the missing information. |  |  |  |  |  |
| 2 |  | The coordination of the testing times will be between System Operations, Resource Integration Department and the Transmission Operator (TO). WHEN: - All information above is received; VERIFY: - TO has approved the test, - TO can approve verbally on a recorded line or by email Once the TO has approved and all information is accurate, approve the QSE test request. Include for following in the approval: - Resource Integration Department - Shift Supervisors |  |  |  |  |  |
| OK to Test |  | If the testing can be accommodated, RESPOND via e-mail to the requesting party similar to the following: “ERCOT recognizes the need of <Company Name> to perform a Coordinated Reactive test with its unit <name> on <date and time>. ERCOT intends to make system adjustments to accommodate this testing to the extent possible consistent with system security. [TO] concurs with the test as long as real-time conditions allow for it. This will require the Generator Operator to contact the local transmission company prior to test initiation. This intent is NOT a guarantee of accommodation”. ___________________ (Shift Supervisor) |  |  |  |  |  |
| Not OK to Test |  | If the request cannot be accommodated, RESPOND via e-mail to the requesting party similar to the following: “ERCOT cannot accommodate the request of <Company Name>for a unit test on <date and time> for the following reason(s) : <List reasons>”. __________________ (Shift Supervisor) |  |  |  |  |  |
| Approval |  | - As Resource tests are approved, update “Approved Unit Tests” spreadsheet located on the System Operations SharePoint. - All operators will be able to view the list to determine which resources are approved to be ONTEST. |  |  |  |  |  |
| Log |  | Log all actions. |  |  |  |  |  |

## 5.3	Notification of Protective Relay or Equipment Failures and Updates

Procedure Purpose:  Be aware and respond if needed to protective relay system failures when notified by a QSE or TO.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 6.2.3 | 6.2.4 |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 13 | Effective Date: January 1, 2020 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Protective Relay or Equipment Failure |  |
| NOTE | Protective relay systems include: relays, associated communications systems, voltage and current sensing devices, station batteries, and DC control circuitry |
| 1 | When notified by a QSE or TO that a protective relay or equipment failure reduces system reliability: - Ask the QSE or TO how it reduces ERCOT Grid system reliability and if any corrective actions have been taken, - Ask the QSE or TO if notifications have been made to any other affected TOs, - Notify the Operations Support Engineer to verify that system reliability has been affected. If so, a corrective action must be taken within 30 minutes, - Determine if other TOs are affected by this failure and make notification by phone. |
| 2 | - After notification from a TO or QSE, NOTIFY by e-mail: - OPS Support Engineering - Operations Analysis - TransRep - Shift Supervisors - The subject line of the e-mail should read “Protective Relay”, “Equipment Failure”, or “Equipment Updates”. - Include in the e-mail: - Entity Name - Brief description - Contact information - Any significant information |
| 3 | If a TO or QSE e-mails a – “Mis-Operation Relay report, forward to the above identified e-mail address. |
| 4 | Log all actions. |
| ### Protective Relay Outages |  |
| NOTE | Protective relay maintenance that ERCOT ISO has been made aware of can be found on the Outage Calendar located on the System Operations SharePoint. |
| Planned Outage | IF: - Notified that a relay is going to be removed from service (Planned); THEN: - Verify or enter information on the Outage Calendar located on the System Operations SharePoint Site, - The relay can’t be removed from service unless there are secondary/back up relays that will be functional and no system degradation will occur; IF: - Secondary/back up relays in place; THEN: - Notify the TO or QSE they can proceed with work. |
| Forced Outage | IF: - Notified that a primary relay has been removed from service (forced); THEN: - Ask if the secondary/back up relay is functional; IF: - There is no secondary/back up relay; THEN: - The equipment will need to be removed from service since it is no longer protected. |
| Log | Log all actions. |
| ### Protection System Setting Notifications |  |
|  | - WHEN: - Protection system setting notifications are received - FORWARD TO: - OPS Support Engineering - Operations Analysis - TransRep - Shift Supervisors |

## 5.6	Equipment Limitation and Rating Changes

Procedure Purpose:  To ensure line rating changes are documented and correct.

| Protocol Reference | 6.5.3(2) |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 7 | Effective Date: January 1, 2020 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Line Rating Changes |  |
| NOTE | Normally line rating changes can only be changed when a NOMCR is received. |
| 1 | IF: - Notified by a TO of an incorrect line rating; THEN: - Notify the Operations Support Engineer. |
| Log | Log all actions. |
| ### TO Temporary Equipment Limitation Notifications |  |
| 1 | IF: - Notified by a TO of any limitations on the Transmission Facilities that may affect Dispatch Instructions / Operating Instructions; THEN: - Notify the Operations Support Engineer. |
| 2 | IF: - The Operations Support Engineer confirmed the Temporary Equipment Limitation Notifications may affect Dispatch Instructions / Operating Instructions; THEN: - Notify the Director Control Room Operations and/or Designee to post on the MIS Secure Area the Transmission Facility limitations that may affect Dispatch Instructions / Operating Instructions. |
| Log | Log all actions. |

## 6.1	Reports

Procedure Purpose: Provide reporting criteria and instructions for the daily reports sent to the PUC, the process to report certain events to the Texas Reliability Entity, posting EEA notices to RCIS and the process for reporting system disturbances to NERC and DOE.

| Protocol Reference | 22 (B) | 6.5.1.2 (4) |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 3.2.3 | 4.7 |  |  |
| NERC Standard | EOP-004-4 R1, R2 | EOP-010-1 R1, R1.1, R2 | EOP-011-1 R2, R2.1, R2.2, R2.2.2, R2.2.3, R2.2.3.2, R2.2.3.3, R2.2.5 |  |

| Version: 1 | Revision: 41 | Effective Date: January 1, 2020 |
| --- | --- | --- |

| Step | Action |  |
| --- | --- | --- |
| ### PUCT Daily Report |  |  |
| NOTE | The PUCT Daily Report is automatically sent at 0530 and again at 1430 each day during the summer. During the Fall, Winter and Spring the PUCT Daily Report is automatically sent at 0230 and again at 1430 each day. Notify Grid Applications Development if the report fails to automatically send. |  |
| Prepare Report | During the Summer prepare the PUCT Daily Report between 0530 – 0600 and again between 1430 – 1500 each day. During the Fall, Winter and Spring prepare the PUCT Daily Report between 0230 – 0300 and again between 1430 – 1500 each day. Management will coordinate the transition of reports so that everyone knows the appropriate times that the report should be sent. |  |
| Review Report | Open up the PUCT Report site and review at any time. If required to send out the report manually, click on the camera to send yourself a PUCT Report. |  |
| E-Mail Report | E-mail the report to the distribution list entitled “PUC-Available Generating Resources.” Subject line example: 0600 PUCT Report June 1, 2019 |  |
| ### Unit Trip Posting |  |  |
| Report | Complete the Unit Trip posting for the previous day between 0000 – 0800 each day of the week. |  |
| Analyze | Review: - Any unit trips from the previous day, - Post an Operational Information message, low priority, on MIS Public |  |
| <450 MW | IF: - No trips are greater than 450 MW, - Post the following message example on MIS Public |  |
| Post | No sudden loss of generation greater than 450 MW occurred on <Date>. |  |
| ≥450 MW | IF: - A trip was 450 MW or more, - Post the following message example on MIS Public |  |
| Post | On <Date>, a sudden loss of generation occurred at <Time> totaling *** MW. Frequency declined to **.*** Hz, ERCOT load was **,*** MW. |  |
| Multiple Trip Example | On <Date>, a sudden loss of generation occurred at <Time> totaling *** MW. Frequency declined to **.*** Hz, ERCOT load was **,*** MW. Another sudden loss of generation occurred at <Time> totaling *** MW. Frequency declined to **.*** Hz, ERCOT load was **,*** MW. |  |
| ### Event Analysis Reporting |  |  |
| 1 | WHEN an event occurs that is listed on the “event list” below, before shift is over: - E-mail information to Director Control Room Operations and Designee - The subject line of the e-mail should read “TRE Event.” |  |
| Event List | For purposes of the event analysis program, brief reports must be completed with 10 days (Responsibility of Grid Analysis group). Most events listed are either OE-417 or EOP-004 reportable, those timelines and forms will be used in place of the EA brief report. Category 1 Events: - An unexpected outage, contrary to design, of three or more BES Facilities caused by a common disturbance: - The outage of a combination of three or more BES Facilities (excluding successful automatic reclosing) - The outage of an entire generation station of three or more generators (aggregate generation of 500 MW to 1,999 MW); each combined cycle unit is counted as one generator - Intended and controlled system separation by the proper operation of a RAS - Failure or misoperation of a BES RAS - System-wide voltage reduction of 3% or more that lasts more than 15 continuous minutes due to a BES emergency - Unintended BES system separation that results in an island of 100 MW to 999 MW. This excludes BES radial connections, and non-BES (distribution) level islanding - Retired on January 1, 2016 - The loss of generation of 1,400 MW to 1,999 MW - Loss of monitoring or control, at a Control Center, such that it significantly affects the entity’s ability to make operating decisions for 30 continuous minutes or more Examples include, but are not limited to the following: - Loss of operator ability to remotely monitor or control BES elements - Loss of communications from SCADA RTU - Unavailability of ICCP links reducing BES visibility - Loss of the ability to remotely monitor and control generating units via AGC - Unacceptable state estimator or contingency analysis solutions - A non-consequential interruption of inverter type resources aggregated to 500 MW or more not caused by a fault on its inverters, or its AC terminal equipment - A non-consequential interruption of a DC tie, between two separate asynchronous systems, loaded at 500 MW or more, when the outage is not caused by a fault on the DC tie, its inverters, or its AC terminal equipment. Category 2 Events: - Complete loss of Interpersonal Communication and Alternative Interpersonal Communication capability affecting its staffed BES control center for 30 continuous minutes or more - Retired on January 1, 2016 refer to Category 1h - BES Emergency resulting in a voltage deviation of equal to or greater than 10% difference of nominal voltage sustained for 15 continuous minutes - Complete loss of off-site power (LOOP) to a nuclear generating station per the Nuclear Plant Interface Requirement - Unintended system separation that results in an island of 1,000 MW to 4,999 MW - Unintended loss of 300 MW or more of firm load for more than 15 minutes - IROL Violation for time greater than Tv. Category 3 Events: - Unintended loss of load, generation (including inverter type resources), or DC tie to asynchronous resources of 2,000 MW or more - Unintended system separation that results in an island of 5,000 MW to 10,000 MW Category 4 Events: - Unintended loss of load, generation (including inverter type resource) from 5,001 MW to 9,999 MW - Unintended system separation that results in an island of more than 10,000 MW Category 5 Events: - Unintended loss of load of 10,000 MW or more - Loss of generation of 10,000 MW or more |  |
| ### NERC and DOE Reporting Operating Plan |  |  |
| NOTE | Send an email to “SysOpsMgrs” when a NERC or DOE reporting event occurs or if suspected to occur and verify it was received due to potential time constraints on report submissions. |  |
| OE-417 Reporting Events | DOE OE-417 forms can be downloaded at: https://www.oe.netl.doe.gov/docs/OE417_Form_05312021.pdf The events listed below must be reported within 1 hour of the incident: - Physical attack that causes major interruptions or impacts to critical infrastructure facilities or to operations - Cyber event that causes interruptions of electrical system operations - Complete operational failure or shut-down of the transmission and/or distribution electrical system - Electrical System separation (Islanding) where part or parts of a power grid remain(s) operational in an otherwise blacked out area or within the partial failure of an integrated electrical system - Uncontrolled loss of 300 MW or more of firm system loads for more than 15 minutes from a single incident - Firm Load shedding of 100 MW or more implemented under emergency operational policy - System-wide voltage reduction of 3% or more - Public appeal to reduce the use of electricity for purpose of maintaining the continuity of the electric power system The events listed below must be reported within 6 hours of the incident: - Physical attack that could potentially impact electric power system adequacy or reliability; or vandalism which target components of any security systems - Cyber event that could potentially impact electric power system adequacy or reliability - Loss of electric service to more than 50,000 customers for 1 hour or more - Fuel supply emergencies that could impact electric power system adequacy or reliability The events listed below must be reported by the later of 24 hours of recognition of meeting an event threshold for reporting or by the end of the next business day (4 p.m. local time will be considered the end of the business day): - Damage or destruction of a Facility that results in action(s) to avoid a Bulk Electric System Emergency - Damage or destruction of its Facility that results from actual or suspected intentional human action - Physical threat to its Facility excluding weather or natural disaster related threats, which has the potential to degrade the normal operation of the Facility. Or suspicious device or activity at its Facility - Physical threat to its Bulk Electric System control center, excluding weather or natural disaster related threats, which has the potential to degrade the normal operation of the control center. Or suspicious device or activity at its Bulk Electric System control center - Bulk Electric System Emergency resulting in voltage deviation on a Facility; A voltage deviation equal to or greater than 10% of nominal voltage sustained for greater than or equal to 15 continuous minutes - Uncontrolled loss of 200 Megawatts or more of firm system loads for 15 minutes or more from a single incident for entities with previous year’s peak demand less than or equal to 3,000 Megawatts - Total generation loss, within one minute of: greater than or equal to 1,400 Megawatts in the ERCOT Interconnection - Complete loss of off-site power (LOOP) affecting a nuclear generating station per the Nuclear Plant Interface Requirements - Unexpected Transmission loss within its area, contrary to design, of three or more Bulk Electric System Facilities caused by a common disturbance (excluding successful automatic reclosing) - Unplanned evacuation from its Bulk Electric System control center facility for 30 continuous minutes or more - Complete loss of Interpersonal Communication and Alternative Interpersonal Communication capability affecting its staffed Bulk Electric System control center for 30 continuous minutes or more - Complete loss of monitoring or control capability at its staffed Bulk Electric System control center for 30 continuous minutes or more |  |
| Event Reporting EOP-004-4 | If an EOP-004 reportable event is also a reportable event under the OE-417 requirements, the OE-417 form can be used to report to NERC and DOE. The events listed below must be reported by the later of 24 hours of recognition of meeting an event threshold for reporting or by the end of the next business day (4 p.m. local time will be considered the end of the business day). - Damage or destruction of a Facility that results in actions to avoid a BES Emergency - Damage or destruction of a Facility that results from actual or suspected intentional human action - Physical threats to a Facility excluding weather or natural disaster related threats, which has the potential to degrade the normal operation of the Facility or suspicious device or activity at a Facility - Physical threats to its BES control center, excluding weather or natural disaster related threats, which has the potential to degrade the normal operation of the control center or suspicious device or activity at its BES control center - Public appeal for load reduction to maintain continuity of the BES - System wide voltage reduction of 3% or more - Firm load shedding ≥ 100 MW (manual or automatic) - Voltage deviation of =/> 10% of nominal voltage sustained for ≥ 15 continuous minutes - Uncontrolled loss of firm load for greater than 15 minutes from a single incident: - ≥ 300 MW for entities with a previous year’s demand of ≥ 3,000 MW OR - ≥ 200 MW for all other entities - Each system separation resulting in an island ≥ 100 MW - Loss of generation of ≥ 1,400 MW - Complete loss of off-site power affecting a nuclear generating station per the Nuclear Plant Interface Requirement - Unexpected loss within its area, contrary to design, of three or more BES Elements caused by a common disturbance (excluding successful automatic reclosing) - Unplanned evacuation from BES control center facility for 30 continuous minutes or more - Complete loss of Interpersonal Communication and Alternative Interpersonal Communication capability affecting its staffed BES control center for 30 continuous minutes or more - Complete loss of monitoring or control capability at its staffed BES control center for 30 continuous minutes or more |  |
| Reporting To Entities | When required to file or forward a report from other entities, the Director Control Room Operations or the Designee will be responsible. File or forward the disturbance report to the following entities: - NERC System Awareness (systemawareness@nerc.net) - NERC (operations@eisac.com), requirement for cyber and courtesy copy for all other reports - Fax (404) 446-9770, if internet down - Phone (404) 446-9780 - DOE when required above (doehqeoc@oem.doe.gov) - Fax (202) 586-8485, if internet down - Phone (202) 586-8100 - NERC and DOE Disturbance Reporting distribution list In the body of the e-mail, type the following: - "Contains Privileged Information and/or Critical Energy Infrastructure Information - Do Not Release". |  |
| NOTE | - If adverse conditions prevent reporting the damage caused by an event and issuing a written Event Report within the timing of the Standard, notify NERC and Texas RE and provided as much information as is available at the time of the notification. - Please be aware that for phone calls to NERC, you will be prompted by a computerized auto-attendant to press 1 for operational issues or 2 for cyber-security issues. |  |
| ### RCIS Reporting |  |  |
| EEA Postings | There are four levels of Emergency Energy Alert (EEA). As ERCOT enters each level, postings must be made on the RCIS under “Energy Emergency Alert”: - “ERCOT is declaring EEA 1” - “ERCOT is declaring EEA 2” - “ERCOT is declaring EEA 3” - “ERCOT is in EEA 0 and back to normal operations.” |  |
| ### NXT Notification Requirements |  |  |
| Beginning of each Shift |  | Log into the NXT Communicator at the beginning of each shift in order to make the required notification quickly. - If issues arise and you are unable to log into the NXT Communicator with your user name, notify the helpdesk and request immediate assistance. |
| NOTE |  | NXT notification should be coordinated with the Shift Engineer. |
| Watch |  | IF: - A Watch for Physical Responsive Capability is initiated, THEN: - Select the “SO Watch PRC below 2500” Scenario and activate notification, WHEN: - A Watch for Physical Responsive Capability has been cancelled, THEN: - Select the “SO Watch for PRC Cancelled” Scenario and activate notification. |
| EEA Implementation Levels |  | IF: - ERCOT initiates EEA Level 1, THEN: - Select the “SO EEA Level 1” Scenario and activate notification, IF: - ERCOT initiates EEA Level 2, THEN: - Select the “SO EEA Level 2” Scenario and activate notification, IF: - ERCOT initiates EEA Level 3 without Load Shed, THEN: - Select the “SO EEA Level 3, NO Load Shed” Scenario and activate notification. IF: - ERCOT initiates EEA Level 3 with Load Shed, THEN: - Select the “SO EEA Level 3, WITH Load Shed” Scenario and activate notification. |
| EEA Termination Levels |  | WHEN: - EEA Level 3 is terminated, THEN: - Select the “SO EEA Level 3 to EEA Level 2” Scenario and activate notification, WHEN: - EEA Level 2 is terminated, THEN: - Select the “SO EEA Level 2 to EEA Level 1” Scenario and activate notification, WHEN: - EEA Level 1 is terminated, THEN: - Select the “SO EEA Level 1 Cancellation” Scenario and activate notification. |
| Loss of Firm Load |  | IF: - An Operator (ERCOT or TO) has issued a request for firm load shed of ≤ 100 MW, THEN: - Notify the Director Control Room Operations and/or Designee immediately. WHEN: - An Operator (ERCOT or TO) has issued a request for firm load shed of ≥ 100 MW, THEN: - Notify the Director Control Room Operations and/or Designee immediately, - Select the “SO Request Firm Load Shed” Scenario and activate notification. |
| NXT Testing |  | WHEN: - Performing Shift Supervisor Procedure 9.2 Monthly Testing of Non-Routinely used Telecommunications Facilities, THEN: - Select the “SO ENS Test” Scenario and activate notification. |
| ### ERCOT Morning Report |  |  |
| NOTE | - This report is currently only required Monday – Friday. - The Morning Report form is located on the _Operations Official Spreadsheets folder |  |
| 1 | Weather Information: - The temperatures are automatically pulled from the EMS, however please verify temperatures from a National or Local Weather Service for each city listed and adjust as necessary.. - Enter the current day forecast conditions for each city listed. |  |
| 2 | Load Data: - The All-Time Peak MW and Seasonal Peak MW will be provided as needed. - Verify the Projected Peak MW and peak hour for the current day. Use the most reasonable forecast, which may not be the highest. - Verify the Previous Day Actual MW. |  |
| 3 | Interchange: - Verify the net flow across the DC-Ties for the peak hour. This can be obtained from the MOI under “DC Tie Scheduling” or from the Excel MAI. |  |
| 4 | Transmission Line Outages: - Verify the number of 345 kV line segment outages for the peak hour. |  |
| 5 | Generation MW Totals: - Verify the Generation scheduled outage MW total. - Verify the Generation forced outage MW total. |  |
| 6 | Projected MW Reserves: - Verify the Responsive Reserve requirement at the Project Peak. - Verify the anticipated operating reserves available at time of peak. - The anticipated operating reserves can be found by adding the “Max Cap. Room” and Responsive Reserve requirement. |  |
| 7 | Recent ERCOT Congestion Activity: - No action needed |  |
| 8 | Comments: - List any active OCNs, Advisories, Watches or Emergency notices. |  |
| 9 | Select: Create Report |  |
| EMAIL | The file is transferred to P:\SYSTEM OPERATIONS drive in the NERC Morning Report Folder. This report should be sent as an attachment by 0700 using the e-mail distribution list entitled “ERCOT Morning Report.” The subject line of the e-mail should read “ERCOT Morning Report for <date>” |  |
| ### RMR Unexcused Misconduct Events |  |  |
| NOTE | - For a RMR unit, a “Misconduct Event” means any hour or hours during which Participant is requested to, but does not; deliver the energy at a level of at least 98% on each hour of the level shown in the Availability Plan. - For a Synchronous Condenser Unit, a “Misconduct Event” means any hour or hours during which Participant is requested to, but does not, synchronize the Unit to the ERCOT Transmission Grid during any hour in which the Unit is shown in the Availability Plan |  |
| 1 | IF: - An RMR or Synchronous Condenser fail to deliver the energy when requested to; THEN: - Notify the Director Control Room Operations and/or Designee. - The management will gather the detailed information and send an e-mail to “Nodal Settlements and Billing” with the subject line “Action Required – RMR Unexcused Misconduct Event”. |  |
| ### Shift Schedule |  |  |
| NOTE | - Shift Schedules will be posted to the MIS under GRID on the Transmission Page in the Transmission Supporting Information section. - The posting of the schedule will be current at all time to be compliant with the Protocols. |  |
| ### Geomagnetic Disturbance (GMD) |  |  |
| NOTE | Solar storms or Geomagnetic disturbances (GMDs) are caused by the interaction of coronal mass ejections (solar flares) with the Earth’s Ionosphere. This interaction produces ionospheric currents in the magnitude of millions of amperes which disturb Earth’s magnetic field. This disturbance induces voltage potential at Earth’s surface which results in geomagnetically induced currents (GICs) in conducting paths such as long transmission lines, pipelines, cables etc. GICs are low frequency or quasi-DC currents which enter and exit the power system at transformer groundings and grounded transmission lines. GICs of 100’s of amperes in magnitude have been recorded. Hence the GICs have the potential to disrupt the normal operation of power system and may damage transformers. GICs may also lead to the loss of reactive power support and hence may cause voltage instabilities. |  |
| Monitor | Monitor forecasted and current space weather: - Reliability Coordinator Information System (RCIS) at https://rcis.nerc.net - NOAA’s Space Weather Prediction Center http://www.swpc.noaa.gov/ |  |
| Warning (Forecasted) | WHEN: - A forecasted GMD Warning is issued for K-7 and greater or G3 and greater; THEN: - Post message on MIS Public - Notice Type: Operational Information - Notice Priority: Low Typical MIS Posting: The Space Weather Prediction Center has issued a GMD Warning of [state level] until [date and time]. Notify Operations Support to run power flow studies to identify 345kV transformers loaded above 70% and develop a mitigation plan if needed. |  |
| Extend | IF: - The Warning is extended or K level increases/decreases; THEN: - Post new message on MIS Public and - Cancel the older message Typical MIS Posting: The Space Weather Prediction Center has extended the GMD Warning of [state level] until [date and time]. |  |
| Cancel | WHEN: - The Warning is no longer valid; THEN: - Cancel the MIS posting. |  |
| Alert (Current) | WHEN: - An Alert for a GMD is issued for K-7 and greater or G3 and greater, or the K level increases/decreases; THEN: - Instruct the Transmission & Security and Real-Time Operators to implement their GMD procedures to make additional postings and Hotline calls. |  |
| Extend | IF: - The Alert is extended or the K level is increased/decreases; THEN: - Instruct the Operators to extend the Alert and/or make notifications regarding storm severity. |  |
| Cancel | WHEN: - K levels drop below K7 or when the Warning is no longer valid; THEN: - Instruct the Operators to cancel the Advisory for the Alert. |  |
| Issues | IF: - Any TO reports an issue due to the GMD event; THEN: - Send e-mail to the following with the details - Operations Analysis - Operations Support - Shiftsupv |  |
| ### Gas Restrictions |  |  |
| 1 | Once notified by a QSE of gas restrictions - Send an e-mail to “Gas Company Notifications”. This will notify all appropriate ERCOT staff. |  |
| 2 | Determine: - If the gas restriction could impact electric power system adequacy or reliability, THEN: - Proceed to “Reports” procedure for NERC/DOE reporting requirements, AND - Consider fuel switching for the generation that has this capability This data can be viewed at ERCOT SharePoint > System Operations – Control Center > Quick Links > Fuel Oil Capability |  |
| ### Remedial Action Schemes (RAS) |  |  |
|  | IF: - A Monthly RAS report is received by e-mail; THEN: - Forward reports to: - OPS Support Engineering - Operations Analysis - Shift Supervisors |  |

## 6.2	Requests for Public Appeal

Procedure Purpose: Provide instructions to initiate public appeals to conserve electricity when needed.

| Protocol Reference | 6.5.9.4(5) | 6.5.9.4.2 |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 3.2.3 |  |  |  |
| NERC Standard | EOP-011-1 R2, R2.1, R2.2, R2.2.4 | OE-417 |  |  |

| Version: 1 | Revision: 6 | Effective Date: January 1, 2020 |
| --- | --- | --- |

| Step | Action |  |
| --- | --- | --- |
| 1 | An ERCOT-wide appeal through the public news media for voluntary energy conservation can be made at any time. However, if ERCOT enters Level 2 of an EEA, an appeal must be issued. This can be coordinated with the Director Control Room Operations and/or Designee. |  |
| 2 | When notified by the Director Control Room Operations and/or Designee that an appeal through the public news media has been made, ensure the Transmission and Real-Time Operators make a Hotline call to notify TOs and QSEs. |  |
| 3 | The Director Control Room Operations and/or Designee will coordinate the recall of the media appeal with Manager of Communications. |  |
| 4 | This is an event that will trigger an OE-417 Report. Coordinate with Director Control Room Operations and/or Designee to verify the report will be submitted, see section 6.1 “NERC and DOE Reporting”. |  |

## 7.1	Abnormal Events

Procedure Purpose:  To provide guidance for those events outside normal operating parameters.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.2.4 |  |  |  |
| NERC Standard | EOP-011-1 R1, R1.1, R1.2, R1.2.2, R1.2.6, R2, R2.1, R2.2, R2.2.9 |  |  |  |

| Version: 1 | Revision: 7 | Effective Date: January 1, 2020 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - The ERCOT Shift Supervisor will act as the main contact and answer inquiries between the control room and other ERCOT operations groups during abnormal events - See Phone Book at Shift Supervisor’s Desk |
| ### System Disturbance |  |
| NERC | Following a Reportable Balancing Contingency Event, restore the Contingency Reserve to at least the Most Severe Single Contingency (1430 MW) before the end of the Contingency Reserve Restoration Period (90 minutes). |
| 1 | IF: - ERCOT is considered to be in an insecure state when the Transmission Grid status is such that a Credible Single Contingency event presents the threat of uncontrolled separation, cascading Outages and/or large-scale service disruption to Load and/or overload of a Transmission Facility, and no timely solution is obtainable from the market; THEN: - Verify that an Emergency Notice is issued - Verify the necessary actions are taken to return the system to normal operating conditions. |
| 2 | IF: - The system disturbance cannot be normalized with current on-shift staff; THEN: - Identify and Assign additional System Operators, Operations Support, Operations Analysis, or Market Operations staff to assist in normalizing the system condition. |
| 3 | The ERCOT Shift Supervisor will ISSUE Emergency Communications & Notifications to ERCOT staff and management in accordance with Desktop Guide Shift Supervisor Section 2.1. |
| ### Degraded Weather |  |
| 1 | WHEN degrading weather conditions are forecasted, verify that the System Operators on the Transmission & Security and Real-Time desks issued corresponding OCN, Advisories, and Watches. |
| 2 | Monitor reserves and Ancillary Services capacities during degraded weather periods such as extreme hot weather, extreme cold weather, and other significant weather events. Determine if additional A/S is needed. |
| 3 | IF: - Forecasted weather conditions are extreme, and it has been deemed necessary that additional staff is required; THEN: - Identify and Assign additional System Operators, Operations Support, Operations Analysis, or Market Operations staff to assist in operating the system during degraded weather conditions. |

## 7.2	EEA Implementation Checklist

shift Supervisor – EEA IMPLEMENTATION Check List

|  | Prior to entering EEA | To be considered when ERCOT anticipates entering into an EEA Event or one is imminent |
| --- | --- | --- |
| Time | Action | Comment |
|  | - Media Appeal for voluntary energy conservation. |  |
|  | - TCEQ exercising enforcement discretion for exceedance of generating plants environmental limits |  |
|  | - ERCOT and the TO agree to use a 15-minute Rating - Identify the appropriate double-circuit contingency and constrain on the single-circuit contingency to make more generation available |  |
|  | - ERCOT notifies MISO or SPP to request one or more SWGRs be switched into ERCOT |  |

| Time | Action | Comment |
| --- | --- | --- |
|  | Administrative tasks applicable to each step: |  |
|  | - Hotline calls made |  |
|  | - NXT System activated |  |
|  | - MIS message posted |  |
|  | - SPP RC Notified |  |
|  | - RCIS Posting |  |
|  | - Ensure 3-part communication is used |  |
|  | - Update EEA Dashboard |  |
|  | EEA Level 1 Implementation | PRC <2300 MW and is not projected to be recovered above 2300 MW within 30 minutes without the use of EEA Level 1 |
|  | - TCEQ exercising enforcement discretion for exceedance of generating plants environmental limits |  |
|  | - Non-Spin deployed |  |
|  | - 30 MIN ERS deployed, if deploying in Level 1. This includes Weather-Sensitive if available and Time Periods TP3 & TP4 |  |
|  | - Resource testing suspended |  |
|  | - Online RMRs loaded to full output |  |
|  | - Emergency Energy procedures implemented across CENACE DC-Ties |  |
|  | - EEA 1 Schedule requested across SPP DC-Ties |  |
|  | - RUC VDI/electronic Dispatch Instruction confirmation, as appropriate/including EMR |  |
|  | - OE-417 for public appeals |  |
|  | - PRC <2000, Manually Deploy RRS |  |

|  | EEA Level 2 Implementation Maintain steady state system frequency at a minimum of 59.91 Hz and maintain PRC above 1000 MW | PRC <1750MW or unable to maintain system frequency at a minimum of 59.91 Hz and is not projected to be recovered above 1750 MW within 30 minutes without the use of EEA Level 2 |
| --- | --- | --- |
|  | - Media Appeal for voluntary energy conservation. |  |
|  | - Load Resources deployed and/or ERS Resources - Block 1 (<1750MW) - Block 2 (as needed) - Both (<1430MW) |  |
|  | - 30 MIN ERS deployed, if not deployed in Level 1. This includes Weather-Sensitive |  |
|  | - 10 MIN ERS deployed, if deemed necessary |  |
|  | - ERCOT and the TO agree to use a 15-minute Rating - De-activate the appropriate double-circuit contingency and constrain on the single-circuit contingency to make more generation available |  |
|  | - TOs load management program deployed if deemed necessary if June - September |  |
|  | - Emergency Energy Procedures implemented across SPP DC-Ties |  |
|  | - TOs notified of Load Resource deployment |  |
|  | - Distribution voltage reduction, as appropriate |  |
|  | - RUC VDI/electronic Dispatch Instruction confirmation, as appropriate/including EMR |  |
|  | EEA Level 3 Implemention Without FIRM LOAD SHED | ERCOT will declare an EEA Level 3 when PRC cannot be maintained above 1,430 MW. |
|  | - PRC <1430 MW, see additional actions required |  |
|  | EEA Level 3 Implemention With FIRM LOAD SHED | PRC < 1000 MW and is not projected to be recovered above 1,000 MW within 30 minutes, or when the clock-minute average frequency falls below 59.91 Hz for 25 consecutive minutes |
|  | - Firm Load shed ordered (100 MW blocks) |  |
|  | - QSEs notified of Firm Load shed |  |
|  | - Load shed achieved |  |

## 7.3	EEA Restoration Checklist

Shift Supervisor – EEA Restoration Check List

| IMPORTANT: If the EEA event coincides with a severe weather event that resulted in the loss of residential load as well as the ERCOT instructed shedding of firm load, COORDINATE load restoration with the appropriate Transmission Operator to insure lost residential load is given priority over the shed load. |  |  |
| --- | --- | --- |
| Time | Action | Comment |
|  | Administrative tasks applicable to each step: |  |
|  | - Hotline calls made |  |
|  | - NXT System activated |  |
|  | - MIS message updated |  |
|  | - SPP RC Notified |  |
|  | - RCIS Posted |  |
|  | RESTORE FIRM LOAD | Sufficient Regulation exist to control to 60 Hz & PRC – Reg Up Resp. is >1430 MW |
|  | - Firm load restoration instructed |  |
|  | - QSEs notified of Firm load restoration |  |
|  | - Load shed recall achieved |  |
|  | EEA LEVEL 3 TO EEA LEVEL 2 | Sufficient Regulation exist to control to 60 Hz & PRC >1430 MW while Load Resources are being recalled |
|  | - Begin recalling Load Resources |  |
|  | - TOs notified of Load Resources |  |
|  | - May begin recalling 30/10 MIN ERS Resources |  |
|  | - TOs notified of Load Resource and ERS Resources recall |  |
|  | EEA Level 2 TO EEA LEVEL 1 | PRC > 1750 MW & all Load Resources and ERS have been instructed to be restored |
|  | - ERS Resources recalled if not already done |  |
|  | - Distribution voltage reductions measures recalled |  |
|  | - TOs notified of ERS Resources recall |  |
|  | - TOs load management program recalled |  |
|  | EEA Level 1 TO EEA 0 | PRC > 2300 MW & all Load Resources and ERS have been instructed to be restored |
|  | - End emergency energy across DC Ties |  |
|  | - Release any RUC committed Resources |  |
|  | - Manually deployed RRS recalled |  |
|  | - Restore control to the post-contingency flow to within the Emergency Rating for those constraints that utilized the 15-Minute Rating - Enforce double-circuit contingencies |  |
|  | - See administrative tasks |  |

## 7.4	Hurricane/Tropical Storm

Procedure Purpose: To ensure ERCOT ISO, TOs and QSEs are prepared for an approaching Hurricane / Tropical Storm.

| Protocol Reference | 6.3.2(3)(a)(ii) | 6.5.9.3.1 | 6.5.9.3.2 | 6.5.9.3.3 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.3.4 |  |  |  |
| Guide Reference | 4.2.1 | 4.2.2 | 4.2.3 | 4.2.4 |
| NERC Standard | EOP-011-1 R1, R1.1, R1.2, R1.2.2, R1.2.6, R2, R2.1, R2.2, R2.2.9 |  |  |  |

| Version: 1 | Revision: 5 | Effective Date: January 1, 2020 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | Hurricane / Tropical Storm notifications are called when there is a probability of landfall in the ERCOT Region (http://www.nhc.noaa.gov) |
| Reporting | As system conditions warrant, complete the following tasks: - Refer to the “Abnormal Events” procedure (7.1) and take appropriate actions for “Gas Restrictions” - Refer to the “Reports” procedure (6.1) and complete the appropriate reporting forms for the conditions that exist. |
| OCN | When an approaching Hurricane / Tropical Storm is approximately 5 days away. - Ensure OCN is issued. - Review the expected path of the hurricane/tropical storm and consult with the Operations Support Engineer to determine if multiple contingencies should be studied due to the possibility of transmission outages or loss of load. - Coordinate with Outage Coordination for the review of planned and existing transmission outages to be withdrawn, rejected, or restored. - Coordinate with Outage Coordination for the review of planned and existing Resource outages that could be asked to be delayed or returned early. - Report any fuel restrictions as per section 6.1 of this procedure. - Review emergency operating procedures. Outages that could be critical are: - Getaways from power plants, in the affected areas, that need to remain on during the storm for reliability. - 345 KV transmission paths in the affected areas, OR - 345 KV transmission paths that will significantly impact the flow of power to and from the affected area. |
| Advisory | When an approaching Hurricane / Tropical Storm is approximately 3 days away. - Ensure Advisory is issued. - If STP is in the path of the hurricane/tropical storm and the QSE is planning to take the unit offline, - Contact Operations Support to run studies to determine the impact and evaluate system conditions. - If necessary determine the generation needed to replace the loss of capacity from STP. - Continue to coordinate with Outage Coordination for the review of planned and existing transmission outages to be withdrawn, rejected, or restored. - Continue to coordinate with Outage Coordination for the review of planned and existing Resource outages that could be asked to be delayed or returned early. - Report any fuel restrictions as per section 6.1 of this procedure. - Review emergency operating procedures. |
| Watch | When approaching Hurricane / Tropical Storm is 1 day away. - Ensure Watch is issued - If necessary, instruct the RUC Operator to commit additional Resources as per Operations Support recommendations. - Determine if the need to have a conference call bridge open with the most affected TOs. - Determine if the need for additional support staff from EMMS Production, ANA, Operations Support, and Operators. - Report any fuel restrictions as per section 6.1 of this procedure. |
| Emergency Notice | When Hurricane/Tropical Storm is in the ERCOT Region and is beginning to have an adverse impact on the ERCOT System. - Ensure Emergency Notice is issued - Implement emergency procedures as needed |
| Issues | Notify the ERCOT Director Control Room Operations or Designee of any issues. |
| Log | Log all actions. |

## 7.6	Extreme Hot Weather

Procedure Purpose: To ensure ERCOT ISO, TOs and QSEs are prepared for extreme hot weather operations.

| Protocol Reference | 6.3.2(3)(a)(ii) | 6.5.9.3.1 | 6.5.9.3.2 | 6.5.9.3.3 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.3.4 |  |  |  |
| Guide Reference | 4.2.1 | 4.2.2 | 4.2.3 | 4.2.4 |
| NERC Standard | EOP-011-1 R1, R1.1, R1.2, R1.2.2, R1.2.6, R2, R2.1, R2.2, R2.2.9 |  |  |  |

| Version: 1 | Revision: 8 | Effective Date: January 1, 2020 |
| --- | --- | --- |

| Step |  | Action |
| --- | --- | --- |
| NOTE |  | Extreme Hot weather notifications are issued when: Temperatures are forecasted to be 103°F or above in the North Central and South Central weather zones. – OR – Temperatures are forecasted to be 94°F or above in the North Central and South Central weather zones during the following months (October – May). |
| OCN |  | When extreme hot weather is forecasted approximately 5 days away: - Ensure OCN is issued - Continue to monitor the weather - Coordinate with Outage Coordination for the review of Planned and existing outages for the possibility of withdrawing or restoring equipment |
| Advisory |  | When extreme hot weather is forecasted approximately 3 days away: - Ensure Advisory is issued - Continue to monitor the weather - Continue to coordinate with Outage Coordination for the review of Planned and existing outages to be withdrawn, rejected, or restored |
| Watch |  | When extreme hot weather is forecasted approximately 1 day away: - Ensure Watch is issued - Continue to monitor the weather - Continue to coordinate with Outage Coordination for the review of Planned and existing outages to be withdrawn, rejected, or restored - Contact Operations Support to run studies to determine the impact of current and future outages - Review emergency operating procedures |
| Emergency Notice |  | When extreme hot weather has arrived and is beginning to have an adverse impact on the ERCOT System: - Ensure Emergency Notice is issued - Implement emergency procedures as needed |
| Issues |  | Notify the ERCOT Director Control Room Operations or Designee of any issues. |
| Log | Log all actions. |  |

## 8.3	Possible Protocol or Operating Guide Violations

Procedure Purpose: Provide instructions for reporting that a QSE or TO may have violated an ERCOT Protocol or Operating Guides requirement.

| Protocol Reference | 6.5.7.9 |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 3.1.2 |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 5 | Effective Date: January 1, 2020 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| 1 | IF: - It appears that a QSE or TO is in violation of the ERCOT Protocols or Operating Guides, THEN: - Confirm the ERCOT System Operator’s finding of a possible violation and that an attempt was made to resolve issue with the QSE or TO personnel. - Attempt to resolve the issue. - Obtain information from Market Operations Support and/or Operations Support personnel, as needed. IF resolution is reached, then LOG the event and this procedure is complete. |
| 2 | IF: - No agreement can be reached; THEN: - Review the incident to establish confidence that there has been a possible violation. Submit information to Director Control Room Operations and/or Designee |
| 3 | Log all actions. |

## 8.6	Root Cause Analysis

Procedure Purpose:  To investigate and recommend corrective action on procedure violations.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 5 | Effective Date: January 1, 2020 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | The following events will trigger an investigation: - Possible violation of the Contingency Event Recovery Period - Possible violation of the Contingency Reserve Restoration Period - Frequency deviation of +/- .05 from scheduled frequency for greater than 30 minutes - High frequency events greater than 60.175 Hz. - Incorrect procurement/deployment of NSRS - Operating actions outside of the ERCOT Protocols, Guides, Operating Procedures or NERC Reliability Standards - Over constraining - A constraint that remains active with no corresponding congestion The Director Control Room Operations and/or Designee may direct the investigation of other events not listed above. |
| NOTE | The “rule of thumb” is to ask why until the most basic cause of the problem is revealed. |
| 1 | When an event occurs, notify the Director Control Room Operations and/or Designee via e-mail that an investigation has been initiated. Include the event, time, duration, and a summary of what occurred. |
| 2 | Preserve all data relevant to the event: - EMMS data - Operational logs - Applicable graphs and charts |
| 3 | Evaluate the following conditions: - Resources - Software performance - Man – Machine interface - Procedures - Management instructions - Training - Computer (hardware) performance - External Distracters - Control Room conditions - Market conditions - System conditions - Human Performance - QSE input and communication - TO input and communication - ERCOT internal support and communication - Shift communication and team work |
| 4 | A preliminary report is due within three days. The report should include: - A summary - The chain of events and/or decisions that produced the outcome - The most basic root cause - Recommended steps to prevent future events from occurring. |
| 5 | Forward the report and related information to the Director Control Room Operations and/or Designee; keep one for the later discussion. |
| 6 | The Director Control Room Operations and/or Designee will review the report with the appropriate ERCOT staff and Shift Supervisor to identify the cause and recommend corrective action. |

## 9.3	Testing of Alternative Interpersonal Communications

Procedure Purpose: To test the multiple Alternative Interpersonal Communication capabilities at least once each calendar month.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | COM-001-3 R9 |  |  |  |

| Version: 1 | Revision: 16 | Effective Date: January 1, 2020 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Primary Control Center |  |
| 1st Weekend Of Every Month | On the first weekend of each month, between the hours of 0000 Saturday and 0500 Monday, test each Alternative Interpersonal Communication device as listed in the steps below. Reference Desktop Guide Shift Supervisor 2.7 Monthly Communication Testing Checklist |
| PBX | - Using the Nortel phone, make a call to an OPX extension - Make a log entry listing the device tested, who the test call was made to, and if it was successful or not successful. |
| PBX By-Pass | - Using the PBX By-Pass phone, make a long distance call - Make a log entry listing the device tested, who the test call was made to, and if it was successful or not successful. |
| Cell Phone | - Using the Control Room cell phone, make a call to the ERCOT Helpdesk. - Make a log entry listing the device tested, who the test call was made to, and if it was successful or not successful. |
| Stand Alone Satellite | - Using the Standalone Satellite phone, make a call (not necessary to call a satellite number). Refer to Desktop Guide Common to Multiple Desks Section 2.7.5. - Make a log entry listing the device tested, who the test call was made to, and if it was successful or not successful. |
| Satellite Modem | Coordinate the following test with the ERCOT DC Tie Operator at the alternate control center. - Using the turret, call each programmed Satellite desk phone at the alternate control center. - Make a log entry listing the device tested, who the test call was made to, and if it was successful or not successful. |
| All Alternative device failures | IF: - All Alternative Interpersonal Communication phones at the Primary Control Center and the same devices from the Alternate Control Center are inoperable. THEN: - Open a helpdesk ticket and cc: “shiftsupv”, AND - Ensure the Help Desk knows this event is a high priority ticket and that one of the Alternative devices must be restored within 2 hours. |
| Unsuccessful Test | IF: - Any of the above devices proved to be unsuccessful; THEN: - Designate a replacement device from one of the five Alternative Interpersonal Communication devices above within 2 hours, - Open a helpdesk ticket and cc: “shiftsupv”, AND - Make a log entry in the applicable log type (see example below). |
| Example Log Entry | The [PBX] phone on the [Supervisor] Desk at the Primary Control Center will be used if needed until the [PBX] phone on the [Supervisor] Desk is repaired. |
| NXT Test | The NXT is not an Alternative Interpersonal Communication device; however it will be tested monthly. - Using the NXT Communicator, activate the “SO ENS Test” scenario between the hours of 0800-2200. - If any issues are found, open help ticket and cc: “shiftsupv”. |
| Form | Complete the Testing of Alternative Interpersonal Communications form located the in P:\ SYSTEM OPERATIONS/ Alternative Interpersonal Communication Testing Forms folder. |
| Email | Send the results of the Testing of Alternative Interpersonal Communications spreadsheet by e-mail to: 1 ERCOT Shift Supervisors |
| Log | Log all actions. |
| Alternate Control Center |  |
| Once a Month | - When working out of the alternate Control Room during the monthly scheduled dates, test each Alternative Interpersonal Communication devices as listed in steps below. |
| PBX | - Using the Nortel phone, make a call to an OPX extension - Make a log entry listing the device tested, who the test call was made to, and if it was successful or not successful. |
| PBX By-Pass | - Using the PBX By-Pass phone, make a long distance call - Make a log entry listing the device tested, who the test call was made to, and if it was successful or not successful. |
| Cell Phone | - Using the Control Room cell phone, make a call to the ERCOT Helpdesk. - Make a log entry listing the device tested, who the test call was made to, and if it was successful or not successful. |
| Stand Alone Satellite | - Using the Standalone Satellite phone, make a call (not necessary to call a satellite number). Refer to Desktop Guide Common to Multiple Desks Section 2.7.5. - Make a log entry listing the device tested, who the test call was made to, and if it was successful or not successful. |
| Satellite Modem | Coordinate the following test with the DC Tie Operator at the other control center. - Using the turret, call each programmed Satellite desk phone at the other control center - Make a log entry listing the device tested, who the test call was made to, and if it was successful or not successful. |
| ALL Alternative device failures | IF: - All Alternative Interpersonal Communication phones at the Alternate Control Center and the same devices from the Primary Control Center are inoperable. THEN: - Open a helpdesk ticket and cc: “shiftsupv”, AND - Ensure the Help Desk knows this event is a high priority ticket and that one of the Alternative devices must be restored within 2 hours. |
| Unsuccessful Test | IF: - Any of the above devices proved to be unsuccessful; THEN: - Designate a replacement device from one of the five Alternative Interpersonal Communication devices above within 2 hours, - Open a helpdesk ticket and cc: “shiftsupv”, AND - Make a log entry in the applicable log type (see example below). |
| Example Log Entry | The [PBX By-Pass] phone on the [Supervisor] Desk at the Alternate Control Center will be used if needed until the [PBX] phone on the [Supervisor] Desk is repaired. |
| NXT Test | The NXT is not an Alternative Interpersonal Communication device; however it will be tested monthly. - Log into the Bastrop ENS link when working out of the alternate Control Room in Bastrop, - Using the NXT Communicator, activate the “SO ENS Test” scenario between the hours of 0800-2200. - If any issues are found, open help ticket and cc: “shiftsupv”. |
| Form | Complete the Testing of Alternative Interpersonal Communications form located the in P:\ SYSTEM OPERATIONS/Alternative Interpersonal Communication Testing Forms folder. |
| Email | Send the results of the Testing of Alternative Interpersonal Communications spreadsheet by e-mail to: - 1 ERCOT Shift Supervisors |
| Log | Log all actions. |

## 9.4	Monthly Testing of Satellite Phone

Procedure Purpose: To test the satellite phone system between ERCOT and the Transmission Operators to ensure communication capability via the Satellite Phone System.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | COM-001-3 R9 |  |  |  |

| Version: 1 | Revision: 6 | Effective Date: January 1, 2020 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - This test is to be conducted on the first weekend of each month, between the hours of 0000 Saturday and 0500 Monday. - Refer to Desktop Guide Common to Multiple Desks Section 2.7. - When a participant dials into the conference bridge before the moderator dials in, they will hear music and be placed on hold. |
| Test | - Call each ERCOT TO using the preprogrammed number on the Turret Phone. - If there is no answer: - Call the ERCOT TO directly using the Satellite Phone number provided in Desktop Guide Common to Multiple Desks Section 2.7.1 and inform them of the time of their respective Satellite Conference Bridge Call. |
| Forms | - Complete the Monthly Satellite Testing forms located the in P:\ SYSTEM OPERATIONS/Satellite Phone Testing Forms folder. |
| Email | Send the compiled results of the Satellite phone test by e-mail to: - 1 ERCOT Shift Supervisors |
| Issues | For any issues identified during testing, day support Management will follow up with the TO or helpdesk and make an entry on the testing form as to the resolution. |
| File | File a hard copy in the control room daily file. |
| Log | Log all actions. |

## 10.1		Loss of Primary Control Center Functionality

Procedure Purpose: Provide instructions for responding to conditions that cause the primary control center to become inoperable or uninhabitable and ensuring the safety of control room personnel.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Stanard | EOP-008-2 R1, R1.4, R1.6, R1.6.2, R1.6.3 |  |  |  |

| Version: 1 | Revision: 6 | Effective Date: January 1, 2020 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| 1 | It will be the responsibility of the Shift Supervisor to determine the risk and ensure the safety of Control Center personnel when deciding to evacuate the Control Center. |
| 2 | Upon confirmation of imminent danger to Control Center personnel, immediately evacuate the Control Center to a secure area, taking the Control Center cell phone. Notify the DC Tie Desk Operator before leaving or immediately after. |
| NOTE | - After the Control Center has been evacuated the Shift Supervisor may: - Re-locate the entire shift to the Alternate Control Center (ACC). - Send a partial shift or contact extra personnel to report to the ACC. - Remain in the secure area in anticipation of a quick return to the Primary Control Center (PCC). - The Shift Supervisor may choose another course of action that will best maintain grid security depending on the circumstances causing the evacuation. |
| 3 | - The Shift Supervisor is responsible for the following notifications in the event of a Control Center evacuation. Information and instructions conveyed will be based on the Shift Supervisors decision regarding relocation to the ACC. - ERCOT Security TCC1 – Ext. 3000 - ERCOT Security ACC (Bastrop) – Ext. 5000 - Help Desk (to notify EMMS Support, Telecommunications) - Director Control Room Operations and/or Designee - Engineering Support These phone numbers have been programmed into the control room cell phone. |

## 10.2		EMMS and Interface System Failures

Procedure Purpose: Provide guidance for coordinating with the ERCOT Help Desk and making notification for unplanned outages of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between the affected TOs and QSEs.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 7.3.3(4) |  |  |  |
| NERC Standard | IRO-018-1(i) R1, R1.2, R2, R2.2, R3 | TOP-001-4 R9 | TOP-010-1(i) R1, R1.2, R2, R2.2, R3, R3.2, R4 |  |

| Version: 1 | Revision: 16 | Effective Date: January 1, 2020 |
| --- | --- | --- |

| Step |  | Action |  |
| --- | --- | --- | --- |
| 1 |  | If any Control Room computer systems fails, such as ICCP links, Web Portal, MIS, or Outage Scheduler that affect normal operations, - Contact the ERCOT Help Desk immediately from the Supervisor Help Desk button on the Turret Phone or extension 6804 - Continue with situational awareness If necessary, contact the on-call IT person first then contact the Help Desk. |  |
| NOTE |  | For a complete EMMS failure, see Real-Time Procedure Section 3.1 Frequency Control Operating Procedure and 3.3 System Failures. |  |
| 2 |  | IF: - Any of the systems fail and are effecting ERCOT systems or TOs and/or QSEs and will be unavailable for longer than 30 minutes; THEN: - Notify TOs and QSEs of the problem and expected duration via Hotline, - Request additional assistance from other support staff, if needed. |  |
| 3 |  | When the problem is resolved, Notify all TOs and QSEs via Hotline of the problem resolution. |  |
| 4 |  | RECORD the following information: - Date - Time of event - Description of system alarms, events, failures, or incident - Actions taken and resolution - Time of system or function restoration |  |
| Log |  | Log all actions. |  |
| ## Data and/or Voice Communication Failures |  |  |  |
| 1 |  | Notify the Help Desk of the loss and REQUEST assistance to re-establish voice and/or data communications. - Telecommunications group will be responsible for voice communications. - EMMS Production group will be responsible for data communications |  |
| 2 |  | Use back-up communications if needed such as the Control Room cell phone, Standalone Satellite phone or the PBX Bypass phones to maintain communications with the other control room, TOs, QSEs, SPP and any other entities as needed. The list of phone numbers is located on the System Operations SharePoint site. |  |
| 3 |  | IF: - The criticality and impact of events or failures is such that TOs and/or QSEs are, or will be affected before the problem can be resolved, THEN: - Instruct ERCOT System Operator to NOTIFY the other ERCOT Control Room and all TOs and QSEs via Hotline of the problem and expected duration. If Hotline is unavailable utilize any of the following methods: - Control Room cell phone, PBX Bypass phones, or Standalone Satellite phone. - REQUEST additional assistance from other support staff, as needed. |  |
| NOTE |  | Steps 4 & 5 may be performed in any order. |  |
| 4 |  | RECORD the following: - Date - Time of event - Description of events, failures, or incident - Actions taken and resolution - Time of system or function restoration |  |
| 5 |  | When the problem is resolved, NOTIFY all participants via Hotline of the problem resolution. |  |
| Log |  | Log all actions. |  |
| ## EMS Alarm Heartbeat, Dynamic Rating, SCED Status, EMBP, SE, RTCA or RLC Alarms |  |  |  |
| NOTE |  | - Normal status for the EMS Alarm Heartbeat/Dynamic Rating, SCED Status, EMBP, SE, RTCA and RLC Status is indicated by each status box constant green on the “ERCOT & QSE Summary Page” in the PI system. - Failure of the PI server is indicated by abnormal status of Dynamic Rating, SE and RLC, accompanied by the PI system “flat-lining” - Indication of PI server failure has been moved to the update time for all wallboard displays. - Dynamic Rating, SE and RLC status boxes flashing red AND PI flat-lining may indicate failure of the EMS. - Verify Shift Engineer has contacted on-call EMMS Production person via xmatters for any EMS tool failure that impacts Grid Reliability. |  |
| Monitor |  | PERFORM the following as applicable to the indicated conditions: - IF only the EMS Alarm Heartbeat status box is yellow, orange or red, CONTACT the ERCOT Help Desk - Tell them the Alarm status in Processbook is not green - Greater than 1 minute but less than 3 minutes turns - Yellow - Greater than 3 minutes but less than 5 minutes turns - Orange - Greater than 5 minutes – Red - REQUEST they notify the on-call EMMS Production person of the situation. - IF only the Dynamic Ratings status box red, CONTACT the ERCOT Help Desk - TELL them the Dynamic Rating Alarm status in Processbook is red and the dynamic ratings are not being sent to the SCADA in the EMS. - REQUEST they notify the on-call EMMS Production person of the situation. - IF only the RLC status box is yellow/red, CONTACT the ERCOT Help Desk - TELL them the RLC Alarm status in Processbook is not green - Greater than 5 minutes but less than 7 minutes turns - Yellow - Greater than or equal to 7 minutes turns - Red - Instruct them to notify the on-call EMMS Production person of the situation. - IF only the SCED Status box is Yellow or red, - The alarm turns yellow when the update duration is greater than 5 minutes and less than 7 minutes. - The alarm turns red when the update duration is greater than or equal to 7 minutes - Follow the Managing SCED Failures in the Real Time Desk Procedure. - If SCED failure can’t be resolved CONTACT the ERCOT Help Desk and instruct them to notify the on-call EMMS Production person of the situation. - IF only the EMBP box is red, - Determine the reason Emergency Base Point are being issued, - Remove the Emergency Base Point flag when condition allow, - If EMBP can’t be resolved CONTACT the ERCOT Help Desk and instruct them to notify the on-call EMMS Production person of the situation. - IF only the SE status box is red, CONTACT the Operations Support Engineer - TELL them the SE Alarm status in Processbook is red - IF only the RTCA status box is yellow or red, CONTACT the Operations Support Engineer - RTCA executes every 5 minutes, if RTCA doesn’t complete within the desired threshold the display changes colors - Greater than 5 minutes but less than 10 minutes turns – Yellow - Greater than 10 minutes but less than 15 minutes turns – Orange - Greater than 15 minutes turns - Red - TELL them the RTCA Alarm status in Processbook is yellow/red - Greater than 15 minutes, inform QSEs for STP and CPSES. |  |
| ## Building Security and Fire Alarms |  |  |  |
| NOTE | The Shift Supervisor or designee will ensure staff members adhere to emergency evacuation procedures and evacuate all team members from the Control Room if an emergency evacuation is required. |  |  |
| 1 | IF: - Building security or fire alarm sounds, THEN: - Contact Security’s Emergency Number if Security has not already made communications with the Control Room. |  |  |
| 2 | IF: - Control Room personnel are in danger or ordered to be evacuated, THEN: - Transfer control of the Grid to the Alternate Control Center (see “Loss of Primary Control Center Functionality” procedure Section 4.4 in the DC Tie Desk Procedure), - Request additional assistance from other support staff, - Evacuate the Control Room to a safe area for Zone #1, - Report to the Alternate Control Center if necessary. |  |  |
| 3 | Notify the Director Control Room Operations and/or Designee as soon as practical. |  |  |
| ## Failure of the Emergency Generator |  |  |  |
| 1 | If the Facilities emergency generator fails to start, you will be notified by the Facilities Staff. |  |  |
| 2 | If the Facilities Staff or the Shift Supervisor determines that it will be more than 20 minutes before the emergency generator can be started, the Shift Supervisor may consider initiating the “Loss of Primary Control Center Functionality” procedure. |  |  |
| 3 | The Shift Supervisor or his/her delegated representative should notify the Director Control Room Operations and/or Designee that the controls have been transferred to the other control center. |  |  |
| 4 | REQUEST additional assistance from other support staff as needed. |  |  |
| NOTE | See Desktop Guide Shift Supervisor Section 2.1. |  |  |
| ## Telemetering, Control Equipment and Communication Outages |  |  |  |
| NOTE | TOs are required to inform ERCOT of all planned outages, and unplanned outages of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between the affected entities. Telemetering, Control Equipment and Communication outages that ERCOT ISO has been made aware of can be found on the Outage Calendar located on the System Operations SharePoint. |  |  |
| Planned Outage | WHEN: - Notified of a planned outage by email; THEN: - Record the information on the Outage Calendar located on the System Operations SharePoint Site for coordination; IF: - The outage(s) cause State Estimator or Contingency Analysis solution issues; NOTIFY: - Shift Engineer as manual updates may be needed to correct any reliability issue; |  |  |
| Forced Outage | WHEN: - Notified of a forced outage; THEN: - Ask if the secondary/back up redundancy is available and functional; IF: - There is no redundancy available and functional; NOTIFY: - Shift Engineer as manual updates may be needed to correct issues with the State Estimator or Contingency Analysis solution. |  |  |
| Log | Log all actions. |  |  |

# 11.	Supervisory Responsibilities

Procedure Purpose:  To keep current on all activities.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 3 | Effective Date: January 1, 2020 |
| --- | --- | --- |

| Step | Action |  |
| --- | --- | --- |
| ## Review Shift Logs |  |  |
| 1 | REVIEW shift logs entries using the following guidelines: - Review multiple days’ worth of shift logs when returning from multiple rest days or vacation periods. - Review previous two shifts logs when accepting a shift in mid-rotation. |  |
| ## Review New Communications from Director Control Room Operations and/or Designee |  |  |
| NOTE |  | Periodically, the ERCOT Director Control Room Operations and/or Designee will issue new operating instructions, operating memos, and other relevant communications to all System Operators. These types of communications are used to clarify or temporarily modify existing procedures. The Shift Supervisor is required to review these communications to ensure that the new instructions are known and understood by all desks in the shift. This task is especially crucial when returning from vacation periods, or several rest days. This review of Director Control Room Operations and/or Designee issued communications includes verification of e-mail and hardcopy communications or instructions. Clarification of new instructions, if needed, must be addressed directly to the Director Control Room Operations and/or Designee. |
| 1 |  | REVIEW all communications received from the Director Control Room Operations and/or Designee including e-mails, letters, and memorandums. |
| 2 |  | DETERMINE if new or revised operating instructions and operating memos were issued since the last verification of communications was made. |
| 3 |  | IF new or revised operating instructions and operating memos were issued, VERIFY which system operator positions and operating procedures may be affected. |
| ## Deliver Oral Shift Report to Entering Shift Supervisor |  |  |
| 1 | OUTLINE comments on the following areas: - Forced Outages - System Reserves - System Conditions - Market Conditions - Forecasted Congestion - System Disturbances, if any occurred - New or modified operating procedures - Shift Staffing information including staff assigned to alternate control center |  |
| 2 | REQUEST understanding and acknowledgement from entering Shift Supervisor. |  |
| ## Coordinate Adjustments to Shift Personnel Schedules |  |  |
| 1 | ADJUST system operator’s shift schedules for: - Scheduled vacation leave periods - Schedule or unscheduled sick periods - Training needs - Special assignments - Other unscheduled leaves of absence |  |
| 2 | COORDINATE system operator replacements for any coordinated leave. |  |
| ## Implement ERCOT Personnel and Company Standards |  |  |
| 1 | IMPLEMENT the policies described in the ERCOT Employee Corporate Standard Manual as needed. |  |
| 2 | ASSIST system operators in observing the standards described in the ERCOT Employee Corporate Standard Manual as needed. |  |
| 3 | DISCUSS any violations of the standards described in the ERCOT Employee Corporate Standard Manual with the system operators as needed. |  |
| 4 | DISCUSS any continuous and persistent non-compliance of a system operator with the standards described in the ERCOT Employee Corporate Standard Manual with the Director Control Room Operations and/or Designee as needed. |  |
| 5 | EXECUTE any remedial actions recommended or instructed by the Director Control Room Operations and/or Designee. |  |

| ## Communicate Procedure Changes |  |
| --- | --- |
| 1 | When changes to operating procedures are approved, INFORM the System Operators and have them review the change(s). |
| 2 | VERIFY that each affected System Operator understands the new or revised procedures. |
| 3 | VERIFY that each affected System Operator has signed the log sheet (located on the Shift Supervisor desk) that states that each Operator is aware and understands the new or revised operating instructions. |
| ## Identify Training Needs of System Operators |  |
| NOTE | - Under performance by a system operator is generally remedied by additional training. Clear indications of underperformance obtained from periodic performance reviews, and on the job-performance observations should indicate to the Shift Supervisor the need to consider training options. |
| 1 | - REVIEW performance review results and periodic job performance observation notes at least once every three months. |
| 2 | IDENTIFY training needs of a system operator or group of system operators in any of the following areas: - System Operations - Employee standards - General skills required in performing assigned system operator duties - New or modified operating procedures or instructions - Other areas not covered by Operating Procedures, Operating Guidelines, or established system operator training |
| 3 | - REVIEW record of training needs of each system operator in the crew. |
| 4 | - SCHEDULE required training for each system operator with ERCOT Training Department. |
| 5 | - FOLLOW progress of system operators training. |
| 6 | - DISCUSS effectiveness of training program related to system operator job performance with Director Control Room Operations and/or Designee and ERCOT Training Department at least once every six months. |
| 7 | - MAKE recommendations on system operator training program as needed. |
| ## Official Copies of Manuals and Guides |  |
| NOTE | Employees who want their own personal copies are responsible for making them themselves. |
| 1 | Ensure that only the official updated copy of the Protocols Manual, Operating Guide, and Operating Procedures Manual is kept at each Operating Desk. |
| 2 | Personal copies of Protocols Manual, Operating Guide, and Operating Procedures Manual ARE NOT allowed at the duty desk. |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Frosch, Hartmann, Stone, and Barcalow | Preparers | November 10, 2010 |
| Frosch and Hartmann | Procedure writers and editors | November 29, 2010 |
| Frosch, Hartmann, and Moore | Procedure writers and editors | January 26, 2011 |
| Frosch and Hartmann | Procedure writers and editors | March 23, 2011 |
| Frosch and Hartmann | Procedure writers and editors | April 20, 2011 |
| Frosch and Hartmann | Procedure writers and editors | June 6, 2011 |
| Frosch and Hartmann | Procedure writers and editors | July 18, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 30, 2011 |
| Frosch and Hartmann | Procedure writers and editors | September 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | October 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 16, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | April 25, 2012 |
| Frosch and Hartmann | Procedure writers and editors | May 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | May 30, 2012 |
| Frosch and Hartmann | Procedure writers and editors | July 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | August 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | October 26, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 26, 2013 |
| Frosch and Hartmann | Procedure writers and editors | May 28, 2013 |
| Frosch and Hartmann | Procedure writers and editors | July 10, 2013 |
| Frosch and Hartmann | Procedure writers and editors | August 7, 2013 |
| Frosch and Hartmann | Procedure writers and editors | August 28, 2013 |
| Frosch and Hartmann | Procedure writers and editors | December 11, 2013 |
| Frosch and Hartmann | Procedure writers and editors | January 27, 2014 |
| Frosch, Gaddy, and Hartmann | Procedure writers and editors | April 1, 2014 |
| Frosch and Hartmann | Procedure writers and editors | May 27, 2014 |
| Frosch and Hartmann | Procedure writers and editors | July 29, 2014 |
| Frosch and Hartmann | Procedure writers and editors | September 29, 2014 |
| Frosch and Hartmann | Procedure writers and editors | December 10, 2014 |
| Frosch and Hartmann | Procedure writers and editors | February 25, 2015 |
| Frosch and Hartmann | Procedure writers and editors | March 25, 2015 |
| Frosch and Hartmann | Procedure writers and editors | April 29, 2015 |
| Frosch and Hartmann | Procedure writers and editors | July 13, 2015 |
| Frosch, Hartmann and Gaddy | Procedure writers and editors | September 25, 2015 |
| Frosch, Hartmann and Gaddy | Procedure writers and editors | December 22, 2015 |
| Frosch, Hartmann and Gaddy | Procedure writers and editors | February 23, 2016 |
| Hartmann and Gaddy | Procedure writers and editors | April 22, 2016 |
| Frosch, Hartmann and Gaddy | Procedure writers and editors | June 24, 2016 |
| Frosch, Hartmann and Gaddy | Procedure writers and editors | September 26, 2016 |
| Hartmann, Gaddy and Frosch | Procedure writers and editors | December 23, 2016 |
| Hartmann, Gaddy and Frosch | Procedure writers and editors | March 27, 2017 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | May 26, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | June 23, 2017 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | September 27, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | October 27, 2017 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | December 22, 2017 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | February 22, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | March 26, 2018 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | April 27, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | May 25, 2018 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | August 28, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | September 26, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | October 29, 2018 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | December 21, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | January 25, 2019 |
| Hartmann, Gaddy, Luker and Frosch | Procedure writers and editors | March 25, 2019 |
| Hartmann, Gaddy, and Luker | Procedure writers and editors | April 26, 2019 |
| Hartmann, Gaddy, and Pence | Procedure writers and editors | May 13, 2019 |
| Hartmann, Gaddy, and Pence | Procedure writers and editors | May 28, 2019 |
| Hartmann, Gaddy, Pence and Frosch | Procedure writers and editors | July 29, 2019 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | October 29, 2019 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | December 20, 2019 |

Manual Change History

| Procedure | Ver/Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All Sections | 1.0 / 0 | New procedures for all sections for Nodal implementation | November 28, 2010 |
| 3.1 4.2 6.1 10.2 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Updated steps 1 and 5, deleted steps 6, 7 and 8 Updated VDI, Testing Rules and Retest Updated PUCT Daily Report step “Update Report”. Updated all steps of Texas RE Event Reporting. Updated Title (Dynamic Rating, SCED Status, EMBP, SE, RTCA or RLC Alarms), 1st Note and Monitor | December 1, 2010 |
| 3.2 3.3 3.7 4.2 6.1 10.2 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 2 1.0 / 2 - / 2 | Updated step 1,3 and added step 4 in “Capacity Monitoring” Updated step 4 Updated step No SCED Solution Updated VDI, Retest, and Notify, added Completion Updated step OE-417 Reporting Events in NERC, DOE Reporting and step 2 on GEO-Magnetic Disturbance (GMD) Updated step Monitor on “Dynamic Rating, SCED Status, EMBP, SE, RTCA or RLC Alarms” | January 31, 2011 |
| 3.2 5.3 5.5 6.1 7.2 7.3 9.2 | 1.0 / 2 1.0 / 1 1.0 / 1 1.0 / 3 1.0 / 1 1.0 / 1 1.0 / 1 | Updated step 3 “Capacity Monitoring” Updated step 1 & 3 Updated 1st note & step 2 Updated PUCT Daily Report, Texas RE Event Reporting & NXT Notification Updated EEA Checklist Updated EEA Restoration Checklist Added new steps “SAT modem testing” & updated NXT Tests | March 25, 2011 |
| 4.2 5.1 7.1 7.3 | 1.0 / 3 1.0 / 1 1.0 / 1 1.0 / 1 | Updated “Unannounced Resource Testing” 1st note Updated 2nd & 6th paragraphs Updated “System Disturbance” NERC, step 2 and “Degraded Weather” step 3 Updated Table | April 22, 2011 |
| 5.3 5.7 6.1 7.1 7.4 7.5 7.6 8.3 | 1.0 / 2 1.0 / 1 1.0 / 4 1.0 / 2 1.0 / 1 1.0 / 0 1.0 / 1 1.0 / 1 | Updated step 2 Updated all steps Updated all steps in Texas RE Event Reporting and NERC and DOE Reporting Updated steps in Degraded Weather Updated all steps Added new procedure Updated all steps Updated step 2 and deleted step 3 | June 8, 2011 |
| 3.6 4.1 4.2 6.1 7.2 7.3 9.2 | 1.0 / 1 1.0 / 1 1.0 / 4 1.0 / 5 1.0 / 1 1.0 / 1 1.0 / 2 | Updated step 3 Removed Initial Synchronization of New Resource Updated Testing Rules Updated step Event List Updated EEA Implementation Checklist Updated EEA Restoration Checklist Added Notice Builder test in Primary Control Center section | July 20, 2011 |
| 4.2 5.5 6.1 7.2 7.3 7.7 9.2 10.1 | 1.0 / 5 1.0 / 2 1.0 / 6 1.0 / 2 1.0 / 3 1.0 / 0 1.0 / 3 1.0 / 1 | Updated step Caution Updated 1st Note Updated step 1 in Texas RE Event Reporting and NXT Testing in NXT Notification Requirements Updated EEA Implementation checklist Updated EEA Restoration checklist Added Extreme Hot Weather Updated NXT Test in Alternate Control Center Updated step 3 | September 1, 2011 |
| 3.4 6.1 7.2 7.3 9.2 | 1.0 / 1 1.0 / 7 1.0 / 2 1.0 / 3 1.0 / 4 | Grammar changes Combined EEA 2A & B per NPRR 379 Updated to implement NPRR 379 Updated to implement NPRR 379 Updated Phone Test in Alternate Control Center | October 1, 2011 |
| 3.7 7.2 10.2 | 1.0 / 2 1.0 / 3 1.0 / 3 | Changed title & all steps Updated EEA checklist Updated 1st Note | November 1, 2011 |
| 3.3 6.2 6.3 | 1.0 / 2 1.0 / 1 1.0 / 1 | Updated all steps Updated step 2 Updated step 1 & 2 All procedures in this manual have been reviewed. | December 15, 2011 |
| 1.2 4.2 5.7 | - / 1 - / 6 - / 2 | Updated Scope Updated all steps of procedure Updated Market Participant Backup Control Center Transfer | January 19, 2012 |
| 2.1 3.3 3.4 3.7 3.8 4.1 4.2 5.3 5.6 5.8 6.1 7.1 9.1 9.2 10.2 | 1.0 / 1 1.0 / 3 1.0 / 2 1.0 / 3 1.0 / 1 1.0 / 2 1.0 / 7 1.0 / 3 1.0 / 1 1.0 / 1 1.0 / 8 1.0 / 3 1.0 / 1 1.0 / 5 1.0 / 4 | Updated paragraph 4 Updated Step 3 Updated Threat & Emergency Classifications & Desktop Guide reference Changed Shift Engineer to Operations Support Corrected grammar on step 1 Changed Shift Engineer to Operations Support Updated procedure Changed Shift Engineer to Operations Support Corrected grammar on step 2 Updated step 2 Updated Texas RE Event Reporting, OE-417 reporting & Desktop Guide reference Updated Desktop Guide reference Updated Desktop Guide reference Updated Desktop Guide reference Changed Shift Engineer to Operations Support and updated Desktop Guide reference | March 1, 2012 |
| 2.1 3.3 3.6 5.6 6.1 7.1 7.4 7.5 7.6 | 1.0 / 2 1.0 / 4 1.0 / 2 1.0 / 2 1.0 / 9 1.0 / 4 1.0 / 2 1.0 / 2 1.0 / 2 | Changed TSP/DSP to TO Updated 3rd Note Updated purpose Changed TSP to TO and Transmission Facility Updated step Update Report & changed ARR to PRC and ERCOT Morning Report Updated step NERC and Degraded Weather Updated OCN, Advisory, & Watch steps Deleted Cold Weather, not Extreme Cold Weather Section number changed, Added OCN, Advisory and Emergency Notice | May 1, 2012 |
| 3.2 | 1.0 / 3 | Updated to reflect changes in the TAC approved Non-Spin document | May 14, 2012 |
| 7.2 7.3 | 1.0 / 3 1.0 / 4 | Updated EILS to ERS per NPRR 451 & added TO load management program Updated EILS to ERS per NPRR 451 & added TO load management program | June 1, 2012 |
| 3.3 4.2 6.1 | 1.0 / 5 1.0 / 8 1.0 / 10 | Updated step 3 Added Desktop Guide to VDI reference Updated PUCT Daily Report, NERC and DOE Reporting and RCIS Posting | July 16, 2012 |
| 3.4 4.2 5.9 6.1 7.2 | 1.0 / 3 1.0 / 9 1.0 / 1 1.0 / 11 1.0 / 4 | Added CPT to procedure and Typical Subject line for e-mail Added Log to procedure Deleted Procedure Updated NERC and DOE Reporting Added 30 MIN ERS deployed to EEA 1 | August 29, 2012 |
| 2.2 3.1 5.3 6.1 7.6 9.1 | 1.0 / 1 1.0 / 2 1.0 / 4 1.0 / 12 1.0 / 3 1.0 / 2 | Added Hotline Call Communication Updated step 5 Updated and added Planned and Forced Outage sections. Added Weather Information section to PUCT Daily Report. Updated step 1 in NERC and DOE Reporting and ERCOT Morning Report section. Updated OCN, Advisory, & Watch Updated step E-mail All procedures in this manual have been reviewed. | November 1, 2012 |
| 3.2 3.3 3.4 3.5 3.6 3.7 3.8 4.1 5.2 5.3 5.5 5.6 5.8 6.1 6.2 6.3 7.4 7.5 7.6 8.3 8.6 9.2 10.1 10.2 11.0 | 1.0 / 4 1.0 / 6 1.0 / 4 1.0 / 1 1.0 / 3 1.0 / 4 1.0 / 2 1.0 / 3 1.0 / 1 1.0 / 5 1.0 / 3 1.0 / 3 1.0 / 2 1.0 / 13 1.0 / 2 1.0 / 2 1.0 / 3 1.0 / 3 1.0 / 4 1.0 / 2 1.0 / 1 1.0 / 6 1.0 / 2 1.0 / 5 1.0 / 1 | Updated step 1, Capacity Monitoring and deleted Reserve Monitoring Updated step 3 Updated notes and Management Notifications Updated purpose and step 1 Updated step 2 Updated step TCM & renamed LMP Map Delete procedure for large wind ramp events Updated step 1 Grammatical correction Updated step 3 Protective Relay or Equipment Failure Added MISO Reliability Coordinator Updated step 2 TO Temporary Equipment Limitation Notifications Updated purpose Updated step 1 Texas RE Event Reporting, Note and step 1 NERC and DOE Reporting, Loss of Firm Load NXT Notification Requirements, step 1 Weather Information section to ERCOT Morning Report, step 1 RMR Unexcused Misconduct Events, GMD, step 2 Gas Restrictions and added Special Protection Systems (SPSs) Deleted procedure Renamed to 6.2 and updated procedure Updated step Reporting Updated step Reporting Updated Log Updated step 2 Updated procedure Deleted Notice Builder Updated step 3 Updated step monitor, step 4 Building Security and Fire Alarms and step 3 Failure of the Emergency Generator Updated procedure Review New Communications from Manager and/or Control Room Operations Manager and step 4 Implement ERCOT Personnel and Company Standards | March 1, 2013 |
| 3.3 3.4 6.1 | 1.0 / 7 1.0 / 5 1.0 / 14 | Updated all steps Added 1st Note, deleted 2nd & 3rd Notes, Management Notification, updated QSE Notification, TO Notification Updated step Update Report | June 1, 2013 |
| 4.1 5.1 6.1 10.2 | 1.0 / 4 1.0 / 2 1.0 / 15 1.0 / 6 | Updated Ancillary Service Testing Coordination and added Coordinated Reactive Tests Added MISO Updated PUCT Daily Report & step 1 on NERC and DOE Reporting and added Note to NXT Notification Requirements Updated 1st Note and step #3 on Building Security and Fire Alarms | July 15, 2013 |
| 3.4 4.1 6.1 7.3 | 1.0 / 6 1.0 / 5 1.0 / 16 1.0 / 5 | Updated QSE Notification, TO Notification & Send E-mail Updated Coordinated Reactive Tests Added 7-Day Outlook, updated Event List on Texas RE Event Reporting & step 2 on GEO-Magnetic Disturbance (GMD) Updated table | August 9, 2013 |
| 3.3 | 1.0 / 8 | Removed HHGT TO reference | August 30, 2013 |
| 3.3 3.4 4.1 4.2 5.3 5.4 5.6 5.7 6.1 7.6 8.1 8.2 8.3 9.1 9.2 10.2 | 1.0 / 9 1.0 / 7 1.0 / 6 1.0 / 10 1.0 / 6 1.0 / 1 1.0 / 4 1.0 / 3 1.0 / 17 1.0 / 5 1.0 / 1 1.0 / 1 1.0 / 3 1.0 / 3 1.0 / 7 1.0 / 7 | Updated step 1 and Log Updated step Log Updated step Log Updated step Log Updated step 4, Planned Outage, Forced Outage and added Log Updated step Log Updated step Log Updated step 1 and added Log Updated step Update Report, TRE Event Reporting changed to Event Analysis Report and event list updated, and NERC and DOE Reporting updated Added step Issues and updated Log Updated step 3 and added Log Updated step 3, 5 and added Log Updated step 3 Updated step Log Updated steps Log Added step 4 and updated Log All procedures in this manual have been reviewed. | December 13, 2013 |
| 4.1 6.1 7.2 7.3 | 1.0 / 7 1.0 / 18 1.0 / 5 1.0 / 6 | Updated for NOGRR125 & OK to test on Coordinated Reactive Tests Updated NERC and DOE Reporting Updated EEA Implementation Checklist Updated EEA Restoration Checklist | January 29, 2014 |
| 3.2 4.2 5.5 6.1 6.2 | 1.0 / 5 1.0 / 11 1.0 / 4 1.0 / 19 1.0 / 3 | Updated VDI information Updated VDI information Updated Note Updated Update Report on PUCT Daily Report and step 1 on NERC and DOE Reporting Updated step 1 | April 4, 2014 |
| 2.2 7.1 | 1.0 / 2 1.0 / 5 | Added VDIs to Master QSEs Updated step 1 | June 1, 2014 |
| 4.2 6.1 6.2 7.2 | 1.0 / 12 1.0 / 20 1.0 / 4 1.0 / 6 | Updated 1st Note, Retest and added Demonstration Test Updated step Update Report Updated steps 1 & 4 Updated checklist | August 1, 2014 |
| 3.3 3.4 4.1 4.2 9.2 | 1.0 / 10 1.0 / 8 1.0 / 8 1.0 / 13 1.0 / 8 | Added step 2 Corrected spelling on Send E-mail Updated script for Unit Testing Added new reference Updated new section on Phone Tests | October 1, 2014 |
| 3.6 3.7 4.2 6.1 | 1.0 / 4 1.0 / 5 1.0 / 14 1.0 / 21 | Changed title and removed references to W-N Added step RTMONI Updated Testing Rules and Scripts Added 2nd note to NERC and DOE Reporting & updated GMD procedure All procedures in this manual have been reviewed | December 15, 2014 |
| 2.2 3.2 3.3 4.2 5.3 5.5 6.1 7.2 7.5 | 1.0 / 3 1.0 / 6 1.0 / 11 1.0 / 14 1.0 / 7 1.0 / 5 1.0 / 22 1.0 / 7 1.0 / 4 | Added Dispatch and VDI definitions Updated step 4 Updated step 1 in Suspected Sabotage or Sabotage Events Moved procedure to Resource desk Updated title and added Protection System Setting Notifications Added Switchable Generation Resource Added Unit Trip Posting Updated checklist Updated Note | March 1, 2015 |
| 5.3 6.1 | 1.0 / 8 1.0 / 23 | Clarification to step 2 Clarifications to GMD procedure | March 30, 2015 |
| 3.3 3.4 3.6 3.7 4.1 5.6 6.1 6.2 7.6 8.3 8.6 10.1 10.2 11 | 1.0 / 12 1.0 / 9 1.0 / 5 1.0 / 6 1.0 / 9 1.0 / 5 1.0 / 24 1.0 / 5 1.0 / 6 1.0 / 4 1.0 / 2 1.0 / 3 1.0 / 8 1.0 / 2 | Updated contact information Updated contact information Updated contact information Updated contact information Updated contact information Updated contact information Updated contact information Updated contact information Updated contact information Updated contact information Updated contact information Updated contact information Updated contact information Updated contact information | May 1, 2015 |
| 6.1 10.2 | 1.0 / 25 1.0 / 9 | Updated GMD procedure Added new Telemetering, Control Equipment and Communication Outages process | July 15, 2015 |
| 9.1 9.2 9.3 9.4 | 1.0 / 0 1.0 / 0 1.0 / 9 1.0 / 4 | New procedure for COM-001-2 New procedure for COM-001-2 Updated procedure for COM-001-2 Updated section number | October 1, 2015 |
| 6.1 7.2 9.3 | 1.0 / 26 1.0 / 8 1.0 / 10 | Updated Event Analysis Reporting step Event List Implement NPRR708 for EEA Added Primary Control Center step Replacement/Alternative Device Examples Added Alternate Control System step Replacement/Alternative Device Examples All procedures in this manual have been reviewed | December 31, 2015 |
| 2.1 6.1 | 1.0 / 3 1.0 / 27 | Updated System Operator Responsibility and Authority Updated Guidelines for Determining EEA Potential | March 1, 2016 |
| 5.3 10.2 | 1.0 / 9 1.0 / 10 | Updated Protective Relay or Equipment Failure step 2 Deleted step 2 and updated step 3 | April 29, 2016 |
| 2.1 2.2 3.2 4.1 5.37.2 7.3 8.2 8.6 10.2 | 1.0 / 4 1.0 / 4 1.0 / 7 1.0 / 10 1.0 / 10 1.0 / 9 1.0 / 7 1.0 / 2 1.0 / 3 1.0 / 11 | Updated steps for COM-002-4 Updated steps for COM-002-4 Updated steps for COM-002-4 Updated steps for COM-002-4 Updated Protection System Setting Notification Updated steps for COM-002-4 Updated steps for COM-002-4 Updated steps for COM-002-4 Updated steps for COM-002-4 Updated steps for COM-002-4 | June 30, 2016 |
| 3.3 6.1 7.2 10.1 | 1.0 / 13 1.0 / 28 1.0 / 9 1.0 / 4 | Updated step Updated Step 1 of NERC and DOE Reporting Updated checklist Updated step 2 | September 30, 2016 |
| 3.3 4.1 5.5 6.1 | 1.0 / 14 1.0 / 11 1.0 / 6 1.0 / 29 | Updated Note Added Unit Testing Note Updated Approved Resources to be ONTEST Step Approval Deleted Turbine Governor Updated Note, renamed SPS to RAS & updated RAS Updated Event Analysis Reporting Step Event List, Event Reporting EOP-004-2 & Step 1 Renamed Special Protection Systems (SPS) to Remedial Action Schemes (RAS) & updated Remedial Action Schemes (RAS) All procedures in this manual have been reviewed | December 30, 2016 |
| 2.1 3.4 4.1 5.1 5.3 5.4 5.5 5.6 5.7 5.9 6.1 7.2 7.6 9.1 9.2 9.3 10.2 | 1.0 / 5 1.0 / 10 1.0 / 12 1.0 / 3 1.0 / 11 1.0 / 2 1.0 / 7 1.0 / 6 1.0 / 4 1.0 / 0 1.0 / 30 1.0 / 10 1.0 / 7 1.0 / 1 1.0 / 1 1.0 / 11 1.0 / 12 | Updated for IRO-001-4 Updated Threat & Emergency Classifications step Updated In Service Approval step 1 Deleted paragraph to create new procedure in 5.9 Updated CFE to CENACE Updated Protective Relay Outages step Updated second note, step 5 & 6 Updated CFE to CENACE Updated TO Temporary Equipment Limitation Notifications step 2 Updated Heading title and step 1 New procedure for IRO-002-4 R2 Updated with Event Analysis v3.1 changes and EOP-004-3 and EOP-011 Updated checklist Updated title Updated step 1 Updated step 2 Updated Satellite Modem Updated TOs, QSEs along with Telemetering, Control Equipment and Communication Outages | March 31, 2017 |
| 1.1 3.2 5.3 7.2 9.1 | 1.0 / 1 1.0 / 8 1.0 / 12 1.0 / 11 1.0 / 2 | Updated Purpose to add Reliability Risk desk Updated Capacity Monitoring step 3 & 4 Updated step 3 and Protective Relay Outages Updated EEA 3 checklist Updated Interpersonal Communication | June 1, 2017 |
| 7.2 | 1.0 / 12 | Updated checklist | June 30, 2017 |
| 9.1 | 1.0 / 3 | Updated steps & deleted Note | September 29, 2017 |
| 9.3 | 1.0 / 12 | Updated 1st Weekend of Every Month | October 31, 2017 |
| 6.1 7.1 8.6 | 1.0 / 31 1.0 / 6 1.0 / 4 | All procedures in this manual have been reviewed Updated PUCT Daily Report step Update Report Updated System Disturbance step NERC Updated Root Cause Analysis step NOTE | December 28, 2017 |
| 6.1 7.2 9.3 10.2 | 1.0 / 32 1.0 / 13 1.0 / 13 1.0 / 13 | Updated NERC and DOE Reporting OE-417 Reporting Events Updated Checklist Added Form an Email steps Updated step 1 & 2 | February 28, 2018 |
| 6.1 10.2 | 1.0 / 33 1.0 / 14 | Updated NERC and DOE Reporting step OE-417 Reporting Events Updated Title & EMS Alarm Heartbeat, Dynamic Rating, SCED Status, EMBP, SE, RTCA or RLC Alarms steps note and Monitor | March 30, 2018 |
| 2.2 7.2 7.3 | 1.0 / 5 1.0 / 14 1.0 / 8 | Updated procedure purpose Updated Checklist Updated Checklist | May 1, 2018 |
| 5.5 | 1.0 / 8 | Update EEA and Switchable Generation Resource | May 31, 2018 |
| 3.2 6.1 7.2 9.3 9.4 | 1.0 / 9 1.0 / 34 1.0 / 15 1.0 / 14 1.0 / 5 | Added step 2 & Log, updated step 3 and renumbered 2, 3 &4 Deleted 7-Day Outlook Report Updated Checklist Multiple changes to clarify the roles and responsibilities Updated forms | August 31, 2018 |
| 5.5 6.1 | 1.0 / 9 1.0 / 35 | Removed Monticello RAS Removed Reportable Balancing Contingency Event from the PUCT Daily Report update and updated step 1 on the ERCOT Morning Report | October 1, 2018 |
| 6.1 | 1.0 / 36 | Updated PUCT Daily Report | November 1, 2018 |
| 9.1 9.2 9.3 | 1.0 / 4 1.0 / 2 1.0 / 15 | Updated Alternative Interpersonal Communication Updated step 1 & 2 Clarified notification times All procedures in this manual have been reviewed | December 28, 2018 |
| 7.2 | 1.0 / 16 | Updated Checklist | January 31, 2019 |
| 6.1 7.4 10.1 | 1.0 / 37 1.0 / 4 1.0 / 5 | Updated NERC and DOE Reporting Operating Plan Updated step Emergency Notice and added steps Issues and Log Updated steps and deleted note | March 29, 2019 |
| 3.7 4.1 | 1.0 / 7 1.0 / 13 | Added Note Updated Coordinated Reactive Tests step 2 | May 01, 2019 |
| 5.5 | - / 10 | Updated Sharyland to ONCOR DC Tie Desk Added step 3 and Typical Scripts to Switchable Generation Resource | May 16, 2019 |
| 5.5 6.1 7.2 | 1.0 / 11 1.0 / 38 1.0 / 17 | Updated Switchable Generation Resource steps Updated process Moved TOs load management from EEA1 to EEA2 | May 31, 2019 |
| 4.1 6.1 10.2 | 1.0 / 14 1.0 / 39 1.0 / 15 | Updated Coordinated Reactive Tests step 1 Added Note to PUCT Daily Report Updated NERC and DOE Reporting Operating Plan steps Updated Building Security and Fire Alarms step 2 | August 1, 2019 |
| 6.1 7.2 | 1.0 / 40 1.0 / 18 | Updated Remedial Action Schemes (RAS) step Updated Checklist | November 1, 2019 |
| 3.3 3.4 3.6 3.7 4.1 5.3 5.6 6.1 6.2 7.1 7.2 7.3 7.4 7.6 8.3 8.6 9.3 9.4 10.1 10.2 11 | 1.0 / 15 1.0 / 11 1.0 / 6 1.0 / 8 1.0 / 15 1.0 / 13 1.0 / 7 1.0 / 41 1.0 / 6 1.0 / 7 1.0 / 19 1.0 / 9 1.0 / 5 1.0 / 8 1.0 / 5 1.0 / 5 1.0 / 16 1.0 / 6 1.0 / 6 1.0 / 16 1.0 / 3 | Updated Suspected Sabotage or Sabotage Events Updated Note Updated step 2 Updated step LMP Map Updated Unit Testing step 1 Deleted step NERC Updated TO Temporary Equipment Limitation Notifications step 2 Updated steps Updated steps Updated NERC step Updated checklist Updated checklist Updated step Issues Updated step Issues Updated step 2 Updated steps Updated step Cell Phone Update Note and added issues step Updated step 3 Updated steps Updated Title and steps All procedures in this manual have been reviewed | January 1, 2020 |