- Power Operations Bulletin # 924

ERCOT has posted/revised the Transmission and Security manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

- http://www.ercot.com/mktrules/guides/procedures/index.html

## 3.1	System Overview

Procedure Purpose: Review, monitor and analyze data to maintain system security.

| Protocol Reference | 6.3.2(3)(a)(i) |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | IRO-002-5 R5 | NUC-001-3 R4, R4.1, R4.2, R9, R9.2, R9.2.1, R9.2.2, R9.4, R9.4.1, R9.4.2 | TOP-001-4 R10, R10.1, R10.2, R10.4, R10.5, R10.6 | VAR-001-5 R2 |

| Version: 1 | Revision: 10 | Effective Date: January 1, 2020 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Review | REVIEW each of the following as necessary to confirm system reliability status: - Alarms - State Estimator (SE) - Real Time Contingency Analysis (RTCA) - Transmission Constraint Manager (TCM) - Approved and Forced Outages - Load Forecast - Voltage and Stability Limits - Real Time Monitoring (RTMONI) - Security Constrained Economic Dispatch (SCED) - Real Time Reserve Monitoring |
| Gap Study | Run a gap study for the next day’s peak hour to ensure all contingencies can be solved. If necessary: - Request the Operations Support Engineer to review results and create CMPs as needed - Coordinate with TOs - If both CPSES units are offline, the Auxiliary load will need to be manually adjusted to 45 MW at both units - Refer to Desktop Guide Transmission Desk Section 2.5 Conducting Future Security Analysis - Save study - Log the following: - Study name - Any issues that could not be resolved and actions taken. |
| STP Lines | A minimum of two transmission lines should be in service at all times. The in-service lines should be from at least two of the groups in the table below: Independent Groups of STP Transmission Lines Group 1; Group 2; Group 3. STPZWP39; STPELM18; JCKSTP18. STPELM27; REFSTP27. STPWAP39. Note: Transmission lines, STP – Blessing (BLESSING), STP – HILLJE (HLJSTP64), and STP – HILLJE (CKT_3124) (EMS naming convention) are not included in this table because these circuits are not part of STP’s credited offsite sources. IF: - A minimum of two lines are not in service; THEN: - Notify the Nuclear Plant’s QSE. - Give an explanation of the event, if known and an estimate of when expected to return to normal |
| Dynamic Transmission Limits | IF: - Any changes in the system that could affect the security and dynamic transmission limits; THEN: - Post message on MIS Public. |

## 4.1	Transmission Congestion Management

Procedure Purpose:  To verify and take corrective action for post-contingency overloads for various conditions.

| Protocol Reference | 3.10.4(2) | 6.1(4) | 6.5.5.2(1) | 6.5.7.1.10 |
| --- | --- | --- | --- | --- |
|  | 6.5.7.1.11 | 6.5.7.8 | 6.5.9(2) | 6.5.9.2(3) |
|  | 6.5.9.3.3 | 6.5.9.3.4 |  |  |
| Guide Reference | 2.2.2 |  |  |  |
| NERC Standard | IRO-001-4 R1 | IRO-002-5 R5 | IRO-008-2 R4, R5, R6 | TOP-001-4 R1, R10, R10.1, R10.3, R10.4, R10.6, R14, R18 |
|  | VAR-001-5 R2, R3 |  |  |  |

| Version: 1 | Revision: 53 | Effective Date: January 1, 2020 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | Although the steps within the procedure are numbered, the numbering is for indexing purposes and are not sequential in nature. The system operator will determine the sequence of steps, exclude steps, or take any additional actions required to ensure system security based on the information and situational awareness available during both normal and emergency conditions. Refer to Section 2.6 of the Transmission & Security Desktop Guide for the contingency solution results legend. |
| Authority | ERCOT System Operators have the authority to take or direct timely and appropriate real-time action, up to and including shedding firm load to alleviate System Operating Limit (SOL) violations. Following a separation from the Interconnection, and following automatic under-frequency load shedding, System Operators will also instruct TOs to shed additional load manually when there is insufficient capacity to restore system frequency. To include directing physical operation of the ERCOT Transmission Grid, including circuit breakers, switches, voltage control equipment, and Load-shedding equipment. |
| CAUTION | IF: - At any time, the prescribed measures within this procedure fail to resolve the congestion, AND - The transmission system is in an unreliable state (see Section 4.2 if a DC-Tie has a shift factor) THEN: - Issue an Emergency Notice - See Generic Script in Section 7.1 - Notify Real-Time operator to make hotline call to QSEs. |
| Critical Facilities | Critical facilities are the ERCOT defined contingencies that show up after running Real Time Contingency Analysis (RTCA) as a post-contingency overload. This list is located in the EMS and an electronic copy is located on the MIS Secure site: Select: Grid>Generation>Reliability Unit Commitment>Standard Contingency List’ Select “Standard Contingency List” Open the zip file>Open the CIM file>Select the Standard_Contingency_List tab and view the contingencies. A potential critical facility becomes a critical facility when the contingency appears in RTCA as a post-contingency overload. |
| NOTE | Congestion Management techniques consist of: - SCED - Phase Shifters (shift factors are on the TCM display) - Remedial Action Plan (RAP) - Pre-Contingency Action Plan (PCAP) - Mitigation Plan (MP) – enacted Post-Contingency - Temporary Outage Action Plans (TOAP) - Building a manual constraint - Non-Spin The electronic and hard copy for the RAPs, PCAPs, and MPs are to be considered current. Should a conflict exist between the electronic and hard copy, the electronic version is to be used. - This data can be viewed at ERCOT SharePoint > System Operations – Control Center > Quick Links > Remedial Action Schemes (RAS) and/or MP/PCAP/RAP , - OCTOAPs are located in the daily Outage Notes. |
| Constraint Shift Factor Cut Off | Basecase and post-contingency constraints which do not have generator shift factors for units greater than or equal to 2% as indicated in EMS or indicate NOSCED are not activated in SCED. See Section 4.6 Mitigation Plan for additional details. |
| ### Review Planned Outage Notes |  |
| Non-Cascading Condition | Review daily outage notes: IF: - Studies indicate a high post-contingency overload (125% of Emergency rating or greater) due to a Planned outage AND it is not a cascading condition; THEN: - Allow the outage - Activate the constraint and step the constraint down by adjusting the %Rating (increments of 5%) |
| Cascading Condition | IF: - Studies indicate a high post-contingency overload (125% of Emergency rating or greater), AND it is a cascading condition, OR - An unsolved contingency, OR - A Basecase overload; THEN: - Take pre-posturing measures to reduce the flow before the outage is taken - Use RTMONI if available on a GTC, OR - Have a manual constraint created if needed IF: - Constraint is ineffective THEN: - Use HDL/LDL overrides as required to pre-posture for an expected Outage as last resort - Post message on MIS Public anytime manual action is taken Typical MIS Posting Script: ERCOT is taking manual actions to pre-posture for XXXX outage ONCE: - Studies show that the post-contingency is below 125% of Emergency rating, unsolved contingency, or Basecase overload is resolved - Give approval for the outage, - Activate constraint, and - Release manual override after SCED runs - Cancel MIS posting. |
| Log | Log all actions. |
| ### Evaluate Real Time Contingency Analysis (RTCA) Results |  |
| 1 | IF: - A major topology change has occurred; THEN: - Re-run RTCA and VSAT. IF: - A constraint needs to be controlled before the next SCED run THEN: - Manually run RTCA after activating the constraint, AND - Manually execute the SCED process |
| Log | Log all actions. |
| ### Post-Contingency Overloads |  |
| 1 | IF: - A post-contingency overload is approaching 98% of its Emergency Rating; THEN: - Verify the contingency definition associated with the constraint is accurate and appropriate given the current state of the grid - Verify SCADA is of similar magnitude to the pre-contingency value (MW and MVAR flows) - Review the limits in DYNRTG static table in order to ensure that the telemetry of the lines is within the acceptable range. |
| 2 | IF: - Inaccurate, - Indicate NOSCED, OR - There is not a unit with at least a 2% shift factor; THEN: - DO NOT employ congestion management techniques, - Notify the Shift Supervisor and Operations Support Engineer to investigate or create a CMP. - Acknowledge the constraint and list a reason using the drop down box, - The comment field should be used for additional information |
| 3 | IF: - Accurate, AND - There is a unit with at least a 2% shift factor; THEN: - Verify no RAS (identified as RAS in EMS), or RAP exist - Activate constraint - Lower the value in the % Rating column in TCM to tighten the constraint as needed (minimum of 95%, excluding GTCs) IF: - A PST can help solve the congestion; THEN: - Activate the constraint until the PST is studied and moved. |
| 4 | IF: - A post-contingency overload of 98% or greater of the Load Shed Rating exist with a RAP in place; THEN: - Activate the constraint to reduce the predicted post-contingency loading to no more than 98% of the Load Shed Rating; IF: - Constraint needs to be controlled within the next 5 minutes; THEN: - Manually run RTCA after activating the constraint, - Manually execute the SCED process, - Refer to “Managing Constraints in SCED”. |
| ### Monitoring Sub Synchronous Resonance (SSR) with Capacitor switching action |  |
| CAUTION | - There are two series Capacitors at Gauss substation. One should remain bypassed all of the time. The ERCOT outage monitoring tool will verify these conditions. - Only one set of series capacitors at either Edison or Oersted will be in service at any time. The ERCOT outage monitoring tool will verify these conditions. - Prior to energizing or bypassing any series capacitors from service, ERCOT System Operators should run an STNET power flow study and contingency analysis. |
| Capacitors With SSR issues | Name EMS ID Transmission Operator. Edison EDISON AEP TO. Orsted OERSTED AEP TO. Gauss GAUSS AEP TO. Kirchhoff KIRCHHOF AEP TO. Ctt_Cros CTT_CROS CROSS TEXAS TO. |
| NOTE | - SSR Studies identify the conditions for SSR. These outages are programmed into the EMS monitoring tool. - TO(s) should contact ERCOT System Operations prior to energizing or bypassing any Series Capacitor. - WARNING: If the generator plant is three contingencies away from SSR vulnerability, a notification will inform a system operator to review the procedural plan. - ALARM: If the generator plant is two or fewer contingencies away from SSR vulnerability, an alarm will inform a system operator to implement the procedural action plan. A Generator is allowed to reside in this condition for 8 hours. - The ERCOT EMS system will be utilized to monitor transmission outages. A double circuit transmission outage is considered as one contingency in Operations. |
| Output Displays | REVIEW REFERENCE DISPLAY: ERCOT EMS Applications>OLNETSEQ – Real-Time Network On-line Sequence Contingency Violation Display SSR Summary Display IF: - You receive an SSR alarm but the impacted Resource is offline. THEN: - Take action accordingly because the SSR tool does not take into account if the unit is planned ON/OFF |
| Warning | IF: - EMS SSR Notification (Warning) Three Contingencies away from SSR vulnerability THEN: - Notify Shift Supervisor - Instruct Operations Support Engineer to review Action Plan - Consider restoring planned outages with less than 8 hours restoration times |
| Alarm | IF: - EMS SSR Notification (Alarm) Two Contingencies away from SSR vulnerability THEN: - Notify Shift Supervisor and Operations Support Engineer - Assess system with series Capacitors bypassed IF: - Congestion is identified during the assessment THEN: - Activate the Manual Constraint - Bypass Series Capacitors promptly Typical Script for TO: This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing [TO] an Operating Instruction to bypass the [Edison and Oersted], [Cross and Gauss], or [Kirchhoff] Series Capacitor for SSR mitigation and update the Outage Scheduler. Notify ERCOT when this task is complete. Please repeat this back to me. That is correct, thank you.” - Post message on MIS Public Typical MIS Posting of the SSR Mitigation: “ERCOT is bypassing the [Series Capacitor] for SSR mitigation.” - Activate Constraint (if any) - Contact affected TOs, Inquire if planned/forced outages can be restored within 8 hours |
| 1 | IF: - There are two Contingencies away from SSR vulnerability Series Capacitor cannot be opened or the planned/forced outages cannot be restored within 8 hours THEN: - Notify Shift Supervisor and Operations Support Engineer - Assess system with [Kendall – Big Hill 345 kV line], [Edith Clarke – Clear Crossing 345 kV line] and/or [Tule Canyon – Tesla 345 kV line], or [Dermott Switch – Clear Crossing 345 kV line] opened IF: - Congestion is identified during the assessment THEN: - Activate the Manual Constraint - Instruct TO to open [Kendall – Big Hill 345 kV line], [Edith Clarke – Clear Crossing 345 kV line] and/or [Tule Canyon – Tesla 345 kV line], or [Dermott Switch – Clear Crossing 345 kV line] - Consider RUC De-Commit of a Resource if this action is less restrictive and additional capacity is needed. Refer to Desktop Guide Transmission Desk 2.18 Sub-Synchronous Resonance |
| 2 | The MIS posting of the SSR Mitigation MUST be posted prior to SSR Notification (Alarm) One Contingency away from SSR vulnerability. IF: - EMS SSR Notification (Alarm) identifies one Contingency away from SSR vulnerability THEN: - Confirm previous steps have been completed; and - Notify QSE with impacted resource |
| Normal Operations | WHEN: - Back to normal operations and there is no SSR vulnerability. CANCEL: - SSR mitigation message on MIS Public. THEN: - Assess system with series Capacitors in service - Insert Series Capacitors Typical Script for TO: This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing [TO] an Operating Instruction to close the [Edison and Oersted], [Cross and Gauss], or [Kirchhoff] Series Capacitor as conditions have improved and there is no reportable SSR condition at this time. Notify ERCOT when this task is complete. Please repeat this back to me. That is correct, thank you.” |
| Log | Log all actions. |
| ### Monitoring Sub Synchronous Resonance (SSR) without Capacitor switching action |  |
| Capacitors With SSR issues | Name EMS ID Transmission Operator. North Edinburg NEDIN AEP TO. Rio Hondo RIOHONDO AEP TO. |
| NOTE | - SSR Studies identify the conditions for SSR. These outages are programmed into the EMS monitoring tool. - TO(s) should contact ERCOT System Operations prior to energizing or bypassing any Series Capacitor. - WARNING: If the generator plant is three contingencies away from SSR vulnerability, a notification will inform a system operator to review the procedural plan. - ALARM: If the generator plant is two or fewer contingencies away from SSR vulnerability, an alarm will inform a system operator to implement the procedural action plan. A Generator is allowed to reside in this condition for 8 hours. - The ERCOT EMS system will be utilized to monitor transmission outages. A double circuit transmission outage is considered as one contingency in Operations. |
| Output Displays | REVIEW REFERENCE DISPLAY: ERCOT EMS Applications>OLNETSEQ – Real-Time Network On-line Sequence Contingency Violation Display SSR Summary Display IF: - You receive an SSR alarm but the impacted Resource is offline. THEN: - Take action accordingly because the SSR tool does not take into account if the unit is planned ON/OFF |
| Warning | IF: - EMS SSR Notification (Warning) Three Contingencies away from a SSR vulnerability THEN: - Notify Shift Supervisor - Inform QSE resource may be requested offline for Valley SSR mitigation |
| Alarm | IF: - EMS SSR Notification (Alarm) Two Contingencies away from a SSR vulnerability THEN: - Notify Shift Supervisor - Issue QSE operating instruction to order the resource offline Typical Script for TO: This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing [QSE] an Operating Instruction to take [resource] offline for SSR mitigation. Notify ERCOT when this task is complete. Please repeat this back to me. That is correct, thank you.” - Post message on MIS Public Typical MIS Posting of the SSR Mitigation: “ERCOT is taking manual actions for SSR mitigation.” |
| 1 | Refer to Desktop Guide Transmission Desk 2.18 Sub-Synchronous Resonance |
| 2 | The MIS posting of the SSR Mitigation MUST be posted prior to SSR Notification (Alarm) One Contingency away from SSR vulnerability. IF: - EMS SSR Notification (Alarm) identifies one Contingency away from SSR vulnerability THEN: - Confirm previous steps have been completed; and - Notify QSE with impacted resource |
| Normal Operations | WHEN: - Back to normal operations and there is no SSR vulnerability. CANCEL: - SSR mitigation message on MIS Public. THEN: - Notify QSE resource is released to come online Typical Script for TO: This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is notifying [QSE] [resource] is released to come online. Please repeat this back to me. That is correct, thank you.” |
| Log | Log all actions. |
| ### Post-Contingency Overloads on the South DC Ties |  |
| NOTE | Ensure all available generation has been committed and the constraint binding before curtailing any South DC-Ties. Curtail only enough to maximize the flow across the South DC-Ties at all times. |
| 1 | IF: - A post-contingency overload is approaching 98% of the Emergency Rating with shift factors for a DC-Tie export; THEN: - Activate the constraint if a 2% or more shift factor exists. IF: - Shift factors exists for a DC-Tie export only or if activating the constraint does not fully resolve the congestion; THEN: - Ensure appropriate Resources have been committed, - Request DC-Tie Operator to curtail the appropriate South DC-Tie to a specific MW amount to resolve the overload - Ensure a Mitigation Plan exists for the contingency and review with TO, - If no Mitigation Plan exists, notify Operations Engineer to create one. |
| ### Basecase Overloads |  |
| 1 | IF: - A Basecase exists THEN: - Verify SCADA is of similar magnitude to the Actual Basecase value (MW and MVAR flows) - Example: Review the SCADA value with Actual (state estimation value) |
| 2 | IF: - Inaccurate, - Indicate NOSCED, OR - There is not a unit with at least a 2% shift factor; THEN: - DO NOT employ congestion management techniques, - Notify the Shift Supervisor and Operations Support Engineer to investigate or create a CMP. - Acknowledge the constraint and list a reason using the drop down box, - The comment field should be used for additional information |
| 3 | IF: - Accurate, AND - There is a unit with at least a 2% shift factor; THEN: - Activate constraint - Lower the value in the % Rating column in TCM to tighten the constraint as needed (minimum of 95%, excluding GTCs) IF: - A PST can help solve the congestion; THEN: - Activate the constraint until the PST is studied and moved. |
| ONTEST | Resources with a Resource Status of ONTEST, may not be issued dispatch instructions / Operating Instructions except: - For Dispatch Instructions / Operating Instructions that are a part of the testing; or - During conditions when the Resource is the only alternative for solving a transmission constraint (would need QSE to change Resource Status); or - During Force Majeure Events that threaten the reliability of the ERCOT System. |
| QSGR | Market Operation>Real-Time Market>SCED Displays>DSI Displays>DSI Data Processes>DSI Operator Manual Overide HDL And LDL IF: - A QSGR is needed for voltage support or an unsolved contingency; THEN: - Override LDL to a level greater than or equal to the COP LSL - DO NOT override while SCED is running, - Notify QSE as time permits - Post message on MIS Typical MIS Posting Script: ERCOT is taking manual actions for XXXX constraint. - These Resources can be viewed at ERCOT SharePoint > System Operations – Control Center > Quick Links > Approved Quick Start (QSGR) Resources |
| Not Dispatchable to SCED | REVIEW REFERENCE DISPLAY: EMS Applications>Generation Control>Resource Limit Calculation>RLC Unit Input Data and RLC Unit Output Data IF: - A QSE has telemetered more A/S on a specific Resource that is greater than their HSL, OR - A Resource is generating more than their telemetered HSL; THEN: - SCED will set the HDL=LDL=MW making the Resource un-dispatchable, - Request the QSE to make corrections to telemetry (Resource status, Resource limits, A/S responsibilities, etc.) - Disregard IRRs unless transmission constraint is active. |
| Qualifying Facilities | A list of Qualifying Facilities can be found in Desktop Guide Common to Multiple Desk section 2.20 IF: - A Qualifying Facility (QF) is needed to operate below its LSL, or be ordered off-line to solve congestion; THEN: - An Emergency must be declared - Issue an electronic Dispatch Instruction confirmation to the appropriate QSE, - Choose “DECOMMIT or ERCOT REQUESTED QF OPERATE BELOW LSL” as the Instruction Type from Resource level - Enter contingency name in “other information” When issuing a VDI or confirmation, ensure the use of three-part communication: - Issue the Operating Instruction - Receive a correct repeat back - Give an acknowledgement - Issue an Emergency Notification via Hotline call to TOs, - Instruct the Real-Time Operator to make Hotline call to QSEs, - Post message to MIS Public. T#28 - Typical Hotline Script for Emergency Notice for instructing Qualifying Facility to operate offline/below LSL |
| Log | Log all actions. If known, log the outage that is causing the congestion. |
| ### Basecase / Post-Contingency Exceedance of Phase Angle |  |
| 1 | IF: - A Phase Angle exceedance exists, THEN: - Verify SCADA is of similar magnitude to the Actual value (MW and MVAR flows) Example: Review the SCADA value with Actual (state estimation value) |
| 2 | IF: - Phase Angle exceedance is valid; THEN: - Notify the appropriate TO and make them aware of the potential that reclosure of breakers could be affected, IF: - The TO needs assistance from ERCOT to get Phase Angle exceedance adjusted; THEN: - This could be transmission switching, creation of a manual constraint, bringing on an additional Resource, returning a planned outage, or development of a CMP. |
| Log | Log all actions. |
| ### Post-Contingency Overloads on Private Use Networks (PUNs) or Customer Owned Equipment behind the Meter |  |
| 1 | IF: - A post-contingency overload is 100% of its Emergency Rating on a PUN or customer owned equipment; THEN: - Contact the appropriate QSE/PUN to alert them of the post-contingency overload, VERIFY: - There is a plan to mitigate the overload if the contingency were to occur. |
| 2 | IF: - It is determined that the QSE/PUN has no way to mitigate or correct the congestion; THEN: - Instruct the QSE/PUN to take action such as lower/raise generation or load (verbal Operating Instruction only, do not override HDL/LDL or activate constraint in SCED) and - Acknowledge the post-contingency overload in TCM. |
| 3 | IF: - The contingency occurs; THEN: - Notify the QSE/PUN to ensure action is being taken on the plan. |
| 4 | IF: - A post-contingency overload of 98% or greater of its Emergency Rating on transmission equipment (non-PUN or customer owned equipment), and the only shift factor of 2% or more is a PUN unit; THEN: - Activate the constraint. |
| Log | Log all actions. |
| ### Managing Constraints in SCED |  |
| NOTE | One of the key tasks is to properly monitor and manage transmission constraints. Keep track of non-binding constraints that have flows approaching their limits and be prepared to take action as the constraint approaches its rating. |
| Output Displays | REVIEW REFERENCE DISPLAY: Market Operation>Real-Time Market>SCED Displays>DSP Displays>DSP Constraint Summary Once SCED has completed its run, check the validity of the binding/exceeded constraints, limits, shadow price, and current real-time flows. |
| In Series | It is common for series elements to have nearly identical shift factors for a given contingency. If post-contingency loading of 98% or greater occurs for multiple elements which have been identified as being in series with each other, only the most limiting constraints should be activated to mitigate all the series element congestion. Example: Contingency A overloads X, Contingency A overloads Y |
| Same Element | If post-contingency loading of 98% or greater occurs on the same element for multiple contingencies and they have nearly identical shift factors, only one of the most limiting constraints should be activated to mitigate the congestion. Example: Contingency A overloads X, Contingency B overloads X |
| 1 | Verify that the SCED executions are reducing the flows on each constraint that is binding. |
| 2 | When a constraint becomes violated in SCED, which is when it has reached its max shadow price and is exceeding its Emergency rating, review the following bullets to take the appropriate action(s): - Confirm that pre-determined relevant RAPs are properly modeled in the EMS, - Ensure base points are being followed , - Remove Resource from ONTEST , - Remove A/S to increase capacity available to SCED (see procedure below), - Determine if a unit carrying Off-line Non-Spin could be used, - Ask Resource Operator to deploy Non-Spin for the specific unit - The telemetered Non-Spin schedule must be changed to 0 for SCED to dispatch the Resource - Determine if additional units could be committed/decommitted, - Confirm SCED is balancing conflicting constraints - Ensure reactive devices are being utilized |
| 3 | IF: - All applicable steps above have been completed, AND constraint is still exceeding its Emergency Rating; THEN: - Seek to determine what unforeseen change in system condition has arisen and where possible, seek to reverse the action, - Instruct Operations Support Engineer to develop a mitigation plan, AND - Notify Shift Supervisor to contact the Director Control Room Operations and/or Designee to investigate further - Refer to Section 4.3, Closely Monitored SOLs |
| NOTE | EMP Applications>TCM-Transmission Constraint Manager>Related Displays>Message Log for CAM IF: - No shift factors are passed for the constraint; THEN: - Contact Help Desk to issue a ticket to EMMS Production to fix immediately. |
| Log | Log all action taken including the following: - Reason for doing a manual override - Any security violations that were ≥ 125% of the Emergency Rating |
| ### Remove A/S to Increase Capacity available to SCED |  |
| 1 | RLC Unit Input Data display IF: - A/S needs to be removed from a specific unit in order to increase capacity to SCED; THEN: - Instruct the QSE to remove the A/S by updating their telemetry to ON to free that capacity to SCED - Notify Resource Operator with undeliverable A/S type, amount and approximate hours. |
| LOG | Log all actions. |
| ### Unsolved Contingencies |  |
| 1 | Periodically check the “Contingency Solution Results” display: IF: - An unsolved contingency exist; THEN: - Run the State Estimator again, - If unsolved contingency remains, notify the Operations Support Engineer to investigate IF: - Generation needs to be re-dispatched to solve the contingency THEN: - Use HDL/LDL override - Post message on MIS Public anytime manual action is taken - Log all actions IF: - EMR Generation needs to be committed such as Hydro THEN: - Issue an Emergency Notice - Notify the RUC Operator to commit the resource(s) - Log all actions IF: - It has been determined that a Resource is needed in real-time for a transmission condition after the close of the Adjustment Period (Typically will be short start); THEN: - Notify the RUC Operator to issue a VDI and an a electronic Dispatch Instruction - Refer to RUC Procedure 3.7 Manual Dispatch of Resources “Manual Commit of a Resource” - Post message on MIS Public anytime manual action is taken Typical MIS Posting Script: ERCOT is taking manual actions for an unsolved contingency. WHEN: - Constraint solves and the contingency comes into RTCA - Activate constraint, and - Release manual override after SCED runs - Cancel MIS posting. |
| LOG | Log all action taken including the following: - Reason for unsolved contingency - Actions taken to resolve |
| ### Unresolvable Congestion with EMR Generation available |  |
| 1 | IF: - Post-contingent rating exceedance in excess of 115% of the Emergency Rating, - An unsolved contingency, - Real-time exceedance, OR - A CMP that does not maintain Reliability; THEN: - Verify the contingency definition associated with the constraint is accurate and appropriate given the current state of the grid IF: - EMR Generation is available to be dispatched to resolve the Reliability issue, THEN: - Issue a Transmission Emergency Notice - Post message on MIS Public - Notify Real-Time Desk to make Hotline call to QSEs - Notify the RUC Operator to commit the appropriate EMR resource(s) Typical MIS Posting Script: Transmission Emergency Notice has been issued for the [Specific Area] due to [state issue used in hotline call]. Edit script as needed to fit situation. WHEN: - Contingency or Constraint solves and is no longer a Reliability concern - Release the EMR Generation - Cancel the Transmission Emergency Notice - Cancel MIS posting. |
| LOG | Log all action taken including the following: - Reason for Transmission Emergency Notice - Actions taken to resolve |
| ### Model Inconsistencies/Updates |  |
| 1 | IF: - Any inconsistencies in ratings, impedance changes, etc. are found; THEN: - Notify Operations Support Engineer so that they can work with the TO to confirm the correct information and if required, correct it through the NOMCR process. |
| 2 | IF: - There is a difference in a Facility rating or system voltage limit between ERCOT and a TO; THEN: - The most limiting rating will be used until the correct rating can be determined, - Notify Operations Support Engineer so that they can work with the TO to confirm the correct information and if required correct it through the NOMCR process. |
| LOG | Log all actions. |
| ### QSE Requests to Decommit a Resource |  |
| 1 | IF: - Notified by the Resource/RUC Operator of a request to decommit a self-scheduled Resource; THEN: - Perform a real-time study (if necessary) to determine that no violation of security criteria exist with the Resource off-line and no additional active constraints for SCED will occur, - Notify the Resource/RUC Operator with determination. |
| ### Phase Shifters |  |
| 1 | IF: - A TO calls to requests that a Phase Shifter position be adjusted and there is no longer any known Reliability issues in the area; THEN: - As time permits, run a study to re-evaluate the phase shifter position; - Coordinate with the TO and adjust the phase shifter as needed to an agreed upon position (preferably as close to neutral as possible). |
| LOG | Log all actions. |

## 4.5	GTC Stability Limits

Procedure Purpose: Maintain transmission stability within the ERCOT region when there is a Generic Transmission Constraint (GTC).

| Protocol Reference | 6.5.9.1(1)(e) |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 2.2.2 | 4.5.2(2)(b) |  |  |
| NERC Standard | IRO-001-4 R1 | IRO-002-5 R5 | IRO-008-2 R5, R6 | TOP-001-4 R1, R10, R10.1, R10.3, R10.6, R14 |

| Version: 1 | Revision: 24 | Effective Date: January 1, 2020 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ## Panhandle Stability |  |
| NOTE | The most limiting of the Weighted Short Circuit Ratio (WSCR) limit, the real-time VSAT steady-state voltage stability limit, and the dynamic voltage stability limit, is used when determining limits in real-time. |
| 1 | WHEN: - VSAT runs and provides an updated limit for the Panhandle Stability; THEN: - Update RTMONI. If: - VSAT results indicates a lower matrix limit; THEN: - Verify dynamic voltage stability limit from table identified in Desktop Guide Transmission Desk 2.12 - Update RTMONI WHEN: - The BASECASE PNHNDL is approaching 85% of the limit; THEN: - Activate the BASECASE PNHNDL constraint in TCM, AND; - Raise the BASECASE PNHNDL to 95% as the flow stabilizes. |
| NOTE | For an unsolved contingency scenario, activate the BASECASE PNHNDL constraint to get the contingency to solve. This may require setting the %Rating lower than 85%. |
| Topology Change | IF: - A topology change occurs; THEN: - Re-run RTCA and VSAT. IF: - A constraint needs to be controlled before the next SCED run THEN: - Manually run RTCA after activating the constraint, AND Manually execute the SCED process |
| Log | Log all actions. |
| ## Nelson Sharpe – Rio Hondo 345kV Stability |  |
| Note | All lines are in-service, Rio Hondo 345 kV Series Cap in-service and improved reactive controls (capacitor switching scheme at Texas Gulf Wind is available) there is no local voltage stability issue in South Texas near Ajo. |
| 1 | IF: - An outage has occurred on any of the identified elements in the table; THEN: - Refer to the constraint limit, WHEN: - The BASECASE NELRIO is approaching 85% of the limit; THEN: - Activate the BASECASE NELRIO constraint in TCM - The constraint activates AND; - Raise the BASECASE NELRIO to 98% as the flow stabilizes. |
| 2 | If there is more than one line out of service or AEP is unable to manage the reactors at Ajo to control voltages, use the most restrictive limit in RTMONI. With more than one line out of service, this becomes more of a thermal issue and RTCA will most likely be more binding than the GTC. |
| Log | Log all actions. |
| ## Red Tap Stability |  |
| NOTE | When all lines are in-service, there is no local voltage stability issue. |
| 1 | IF: - An outage has occurred on the identified element in the table (identified in Desktop Guide Transmission Desk 2.12); THEN: - Refer to the constraint limit from table to set the value (identified in Desktop Guide Transmission Desk 2.12); - Update RTMONI from table; WHEN: - The BASECASE REDTAP flow is approaching 85% of the limit in TCM; THEN: - Activate the BASECASE REDTAP constraint in TCM - The constraint activates AND; - Raise the BASECASE REDTAP to 98% as the flow stabilizes. |
| Log | Log all actions. |
| ## North Edinburg – Lobo Stability |  |
| 1 | IF: - An outage has occurred on the identified element in the table (identified in Desktop Guide Transmission Desk 2.12); THEN: - Refer to the constraint limit from table to set the value (identified in Desktop Guide Transmission Desk 2.12); - Update RTMONI from table; WHEN: - The BASECASE NE_LOB flow is approaching 85% of the limit in TCM THEN: - Activate the BASECASE NE_LOB constraint in TCM - The constraint activates AND; - Raise the BASECASE NE_LOB to 98% as the flow stabilizes. |
| Log | Log all actions. |
| ## East Texas Stability |  |
| NOTE | When all lines are in-service, there is no local voltage stability issue. |
| 1 | IF: - An outage has occurred on the identified element in the table (identified in Desktop Guide Transmission Desk 2.12); THEN: - Refer to the constraint limit from table to set the value (identified in Desktop Guide Transmission Desk 2.12); - Update RTMONI from table; WHEN: - The BASECASE EASTEX flow is approaching 85% of the limit in TCM THEN: - Activate the BASECASE EASTEX constraint in TCM - The constraint activates AND; - Raise the BASECASE EASTEX to 98% as the flow stabilizes. |
| Log | Log all actions. |
| ## McCamey Stability |  |
| 1 | IF: - An outage has occurred on the identified element in the table (identified in Desktop Guide Transmission Desk 2.12); THEN: - Refer to the constraint limit from table to set the value (identified in Desktop Guide Transmission Desk 2.12); - Update RTMONI from table; WHEN: - The BASECASE MCCAMY flow is approaching 85% of the limit in TCM THEN: - Activate the BASECASE MCCAMY constraint in TCM - The constraint activates AND; - Raise the BASECASE MCCAMY to 98% as the flow stabilizes. |
| Log | Log all actions. |
| ## Treadwell Stability |  |
| NOTE | When all lines are in-service, there is no local voltage stability issue. |
| 1 | IF: - An outage has occurred on the identified element in the table (identified in Desktop Guide Transmission Desk 2.12); THEN: - Refer to the constraint limit from table to set the value (identified in Desktop Guide Transmission Desk 2.12); - Update RTMONI from table; WHEN: - The BASECASE TRDWEL flow is approaching 85% of the limit in TCM THEN: - Activate the BASECASE TRDWEL constraint in TCM - The constraint activates AND; - Raise the BASECASE Treadwell to 98% as the flow stabilizes. |
| Log | Log all actions. |
| ## Raymondville – Rio Hondo Stability |  |
| NOTE | When all lines are in-service, there is no local voltage stability issue. |
| 1 | IF: - An outage has occurred on the identified element in the table (identified in Desktop Guide Transmission Desk 2.12); THEN: - Refer to the constraint limit from table to set the value (identified in Desktop Guide Transmission Desk 2.12); - Update RTMONI from table; WHEN: - The BASECASE RV_RH flow is approaching 85% of the limit in TCM THEN: - Activate the BASECASE constraint in TCM - The constraint activates AND; - Raise the BASECASE RV_RH to 98% as the flow stabilizes |
| Log | Log all actions. |
| ## Bearkat Stability |  |
| NOTE | When all lines are in-service, there is no local voltage stability issue. |
| 1 | IF: - An outage has occurred on the identified element in the table (identified in Desktop Guide Transmission Desk 2.12); THEN: - Refer to the constraint limit from table to set the value (identified in Desktop Guide Transmission Desk 2.12); - Update RTMONI from table; WHEN: - The BASECASE BEARKT flow is approaching 85% of the limit in TCM THEN: - Activate the BASECASE constraint in TCM - The constraint activates AND; - Raise the BASECASE BEARKT to 98% as the flow stabilizes |
| Log | Log all actions. |

## 7.3	Implement EEA Levels

Procedure Purpose:  To provide for maximum possible continuity of service while maintaining the integrity of the ERCOT system to reduce the chance of cascading outages.

| Protocol Reference | 6.5.9.3.4(6) | 6.5.9.4 | 6.5.9.4.2 |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.5.3 | 4.5.3.1 | 4.5.3.2 | 4.5.3.3 |
|  | 4.5.3.4 |  |  |  |
| NERC Standard | EOP-011-1 R2, R2.1, R2.2, R2.2.2, R2.2.4, R2.2.7, R2.2.8 | IRO-001-4 R1 | TOP-001-4 R1, R8 |  |

| Version: 1 | Revision: 29 | Effective Date: January 1, 2020 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - IF steady state system frequency falls below 59.91 Hz, ERCOT CAN immediately implement EEA 3. - IF steady state system frequency falls below 59.5 Hz, ERCOT SHALL immediately implement EEA 3. |
| NOTE | Confidentiality requirements regarding transmission operations and system capacity information will be lifted, as needed to restore reliability. |
| Media Appeal | When an ERCOT-wide appeal through the public news media for voluntary energy conservation is made. Notify the TOs by hotline. T#39 - Typical Hotline Script for Media Appeal |
| ### Implement EEA Level 1 |  |
| 1 | IF: - PRC < 2300 MW and is not projected to be recovered above 2300 MW within 30 minutes without the use of EEA Level 1; THEN: - Using the Hotline, notify all TOs to implement EEA 1. T#5 - Typical Hotline Script for EEA1 After the repeat, give TOs an update of system conditions, including chances of proceeding into an EEA 2. |
| LOG | Log all actions. |
| ### Implement EEA Level 2 |  |
| Note | ERCOT may declare an EEA Level 2 when the clock-minute average system frequency falls below 59.91 Hz for 15 consecutive minutes. |
| 1 | IF: - PRC < 1750 MW or unable to maintain system frequency at 59.91 Hz and is not projected to be recovered above 1750 MW within 30 minutes without the use of EEA Level 2; THEN: - Using the Hotline, notify all TOs to implement EEA 2 and any measures associated with EEA 1, if not already implemented. - If the energy conservation call has not been made previously, it can be combined with this call. - Reduce Customer Load by using distribution voltage reduction measures, if deemed beneficial. - Implement any available Load management plans to reduce Customer Load. T#7 - Typical Hotline Script for EEA2 Media Appeal and Voltage Reduction After the repeat, give TOs an update of system conditions, including chances of proceeding into an EEA 3. |
| NOTE | The Load Management Program step below is only to be considered on weekdays (except holidays) during the summer months (June to September) between 1330 and 1900 hours due to restrictions in TO Load Management Program contracts. |
| Load Management Program | Monitor predicted load increase over the next hour and into the peak hours as indicated in the prevailing ERCOT Load Forecast. * Only applies June through September IF: - The current time is AT LEAST 13:30 BUT NOT AFTER 16:00; THEN: - Using the Hotline, contact all TOs with Load Management Programs, requesting implementation of their Load Management Programs. T#6 - Typical Hotline Script to Deploy Load Management Program |
| LOG | Log all actions. |

| ### Implement EEA Level 3 |  |
| --- | --- |
| Note | ERCOT may declare an EEA Level 3 when the clock-minute average system frequency falls below 59.91 Hz for 20 consecutive minutes. |
| 1 | ERCOT will declare an EEA Level 3 when PRC cannot be maintained above 1,430 MW. Using the Hotline, notify all TOs to implement EEA 3 Without Firm Load Shed and any measures associated with EEA 1 and 2, if not already implemented. T#88 - Typical Hotline Script for EEA3 PRC <1430 MW Without Firm Load Shed After the repeat, give TOs an update of system conditions, including chances of proceeding into an EEA 3 Firm Load Shed. |
| 2 | IF: - PRC < 1000 MW and is not projected to be recovered above 1,000 MW within 30 minutes, or when the clock-minute average frequency falls below 59.91 Hz for 25 consecutive minutes; THEN: - Using the Hotline, notify all TOs to implement EEA 3 Firm Load Shed and any measures associated with EEA 1 and 2, if not already implemented - *Request deployment of Load Management Programs * Only applies June through September in EEA 2 if not already deployed, EEA 2 and EEA3 implements any available Load management plan to reduce Customer Load. T#8 - Typical Hotline Script for EEA3 Firm Load Shed |
| LOG | Log all actions. |

## 7.4	Restore EEA Levels

Procedure Purpose:  To restore the ERCOT grid to normal state as system conditions warrant while recovering from an EEA event.

| Protocol Reference | 6.5.9.4.1 | 6.5.9.4(3)(g) | 6.5.9.4.3 |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.5.3.5 |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 20 | Effective Date: January 1, 2020 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Restore Firm Load |  |
| RESERVES | 1430 MW of PRC must be restored within 90 minutes. |
| 1 | IF: - Sufficient Regulation Service exist to control to 60 Hz, AND - PRC – Regulation Up Responsibility is ≥ 1430 MW for the last 15 minutes; THEN: - Using the Hotline, notify all TOs of firm load restoration. T#9 - Typical Hotline Script EEA3 Restore a Portion of the Firm Load OR T#10 - Typical Hotline Script EEA3/BAAL Restore All Firm Load |
| LOG | Log all actions. |
| ### Move from EEA Level 3 to EEA Level 2 |  |
| 1 | IF: - Sufficient Regulation Service exist to control to 60 Hz, AND - PRC is ≥ 1750 MW, AND - All firm load has been instructed to be restored; THEN: - Using the Hotline, notify all TOs of the reduction from EEA 3 to EEA 2: - Notify the TOs that Load Resources are being restored T#11 - Typical Hotline Script to move from EEA3 to EEA2 |
| LOG | Log all actions. |
| ### Move from EEA Level 2 to EEA Level 1 |  |
| 1 | IF: - The System can maintain PRC ≥ 2300 MW AND - All Load Resources have been instructed to be restored; THEN: - Using the Hotline, notify all TOs of the reduction from EEA 2 to EEA 1 and ERS Resources have been instructed to restore, - If distribution voltage reduction measures were used, restore - If BLTs were implemented, restore - *If Load Management Programs were deployed, restore T#12 - Typical Hotline Script to move from EEA2 to EEA1 |
| ### Move from EEA Level 1 to EEA 0 |  |
| 1 | IF: - The System can maintain PRC ≥ 2300 MW, AND - All committed units secured in EEA can be released, AND - Emergency energy from the DC Ties is no longer needed; THEN: - Using the hotline, notify all TOs of the termination of EEA. T#13 - Typical Hotline Script Terminate EEA1 |
| ### Cancel Watch |  |
| 1 | WHEN: - Requested by the Real-Time Operator; THEN: - Cancel Watch T#14 - Typical Hotline Script to cancel Watch for PRC <2500 MW |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Frosch, Hartmann, Stone, and Barcalow | Preparers | November 10, 2010 |
| Frosch and Hartmann | Procedure writers and editors | November 29, 2010 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2010 |
| Frosch and Hartmann | Procedure writers and editors | January 4, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 26, 2011 |
| Frosch and Hartmann | Procedure writers and editors | March 23, 2011 |
| Frosch and Hartmann | Procedure writers and editors | April 20, 2011 |
| Frosch and Hartmann | Procedure writers and editors | June 10, 2011 |
| Frosch and Hartmann | Procedure writers and editors | July 18, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 1, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 30, 2011 |
| Frosch and Hartmann | Procedure writers and editors | September 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | October 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 16, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | April 25, 2012 |
| Frosch and Hartmann | Procedure writers and editors | May 30, 2012 |
| Frosch and Hartmann | Procedure writers and editors | July 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | August 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | September 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | October 26, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 26, 2013 |
| Frosch and Hartmann | Procedure writers and editors | May 28, 2013 |
| Frosch, Hartmann & Weldon | Procedure writers and editors | July 8, 2013 |
| Frosch and Hartmann | Procedure writers and editors | August 7, 2013 |
| Frosch and Hartmann | Procedure writers and editors | August 28, 2013 |
| Frosch and Hartmann | Procedure writers and editors | September 25, 2013 |
| Frosch and Hartmann | Procedure writers and editors | December 11, 2013 |
| Frosch, Solis and Hartmann | Procedure writers and editors | December 20, 2013 |
| Frosch and Hartmann | Procedure writers and editors | February 18, 2014 |
| Frosch, Gaddy, and Hartmann | Procedure writers and editors | April 1, 2014 |
| Frosch, Gaddy, Hartmann and Solis | Procedure writers and editors | May 27, 2014 |
| Frosch and Hartmann | Procedure writers and editors | July 27, 2014 |
| Frosch and Hartmann | Procedure writers and editors | September 29, 2014 |
| Frosch, Hartmann, Lopez and Solis | Procedure writers and editors | December 10, 2014 |
| Frosch and Hartmann | Procedure writers and editors | February 25, 2015 |
| Frosch and Hartmann | Procedure writers and editors | March 25, 2015 |
| Frosch and Hartmann | Procedure writers and editors | April 29, 2015 |
| Frosch, Hartmann and Gaddy | Procedure writers and editors | July 13, 2015 |
| Hartmann and Gaddy | Procedure writers and editors | September 4, 2015 |
| Hartmann and Gaddy | Procedure writers and editors | September 25, 2015 |
| Hartmann and Gaddy | Procedure writers and editors | December 22, 2015 |
| Hartmann, Gaddy and Frosch | Procedure writers and editors | January 22, 2016 |
| Hartmann and Gaddy | Procedure writers and editors | February 23, 2016 |
| Hartmann, Gaddy and Frosch | Procedure writers and editors | April 22, 2016 |
| Hartmann, Gaddy and Frosch | Procedure writers and editors | June 24, 2016 |
| Hartmann and Gaddy | Procedure writers and editors | September 26, 2016 |
| Hartmann and Gaddy | Procedure writers and editors | October 31, 2016 |
| Hartmann, Gaddy, Frosch and Solis | Procedure writers and editors | December 23, 2016 |
| Hartmann, Gaddy and Frosch | Procedure writers and editors | March 27, 2017 |
| Hartmann, Gaddy and Frosch | Procedure writers and editors | April 5, 2017 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | May 26, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | June 23, 2017 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | July 24, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | August 30, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | September 27, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | October 27, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | December 28, 2017 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | December 22, 2018 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | March 26, 2018 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | April 27, 2018 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | May 25, 2018 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | August 24, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | September 27, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | October 29, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | December 21, 2018 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | January 25, 2019 |
| Hartmann, Gaddy and Frosch | Procedure writers and editors | March 26, 2019 |
| Hartmann, Gaddy and Luker | Procedure writers and editors | April 26, 2019 |
| Hartmann, Gaddy and Pence | Procedure writers and editors | May 28, 2019 |
| Hartmann, Gaddy and Pence | Procedure writers and editors | July 29, 2019 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | October 29, 2019 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | December 20, 2019 |

Manual Change History

| Procedure | Ver/ Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All Sections | 1.0 / 0 | New procedures for all sections for Nodal implementation | November 28, 2010 |
| 3.2 4.1 4.2 4.3 4.4 4.5 4.6 6.1 7.4 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Updated Categories and Priorities In section “Post-Contingency Overloads”, updated step 5 and QSGR, “Managing Binding and Violated Constraints” step 1, “Reaching Shadow Price Cap” step 1, and ” Managing Congestion during SCED Failure” step 1 Updated steps 1 and 2 Updated steps 2 and 3 Updated step ≤200MW In section “Special Protection Systems (SPS) (Identified as RAS in EMS)” changed 3rd Note to “Monitor”, changed “Operation” to step 4, changed “Runback” to step 5 and updated In section “Manual Dispatch Instruction to take a Unit Off-Line” and “Taking One CT of a Combined Cycle Off-line”, Updated step 1 and deleted Manual Dispatch Instruction In section “Voltage Issues”, Updated 1st Note and Exceed URL, deleted 3rd Note and added QSE Performance In section “ERCOT picks up Load for Non-ERCOT System” and “Non-ERCOT System picks up Load for ERCOT”, updated step 1 | December 1, 2010 |
| 4.1 4.2 4.3 5.1 | 1.0 / 2 1.0 / 2 1.0 / 2 1.0 / 1 | Deleted 1st Note, updated step Critical Facilities & 2nd Note, step 1 in Evaluate Real-Time Contingency Analysis Results, steps 3-6, 8 & QSGR in Post-contingency Overload, step 2 in Transmission Issues in the Areas of the CFE Ties, changed title & updated all steps in Managing Binding and Violated Constraints, step 1 in Reaching Shadow Price Cap, all steps in QSE Requests to Decommit a Resource, deleted Deploy/Termination of Non-Spin for Congestion, updated step 1 in Managing Congestion during SCED failure Updated step 1 & 2 Updated step 3 Added Remedial Switching Action section | December 15, 2010 |
| 4.1 4.2 4.3 7.1 | 1.0 / 3 1.0 / 3 1.0 / 3 1.0 / 1 | Updated step 1 in Reaching Shadow Price Cap Updated step 1 & 2 Updated step 2 & 3 and added step 4 & 5 Updated step 1 in Watch and step Hotline in Scripts | January 5, 2011 |
| 2.3 2.4 3.3 4.1 4.3 4.4 4.5 4.6 4.7 6.1 7.1 7.2 7.3 7.5 8.1 8.2 8.3 9.3 | 1.0 / 0 1.0 / 0 1.0 / 1 1.0 / 4 1.0 / 4 1.0 / 2 1.0 / 2 1.0 / 2 1.0 / 1 1.0 / 2 1.0 / 2 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Added “Site failovers and Database Loads” as new procedure Added “Switching Control Center” as new procedure Updated step 5 Updated scripts, step 1 in “Managing Binding and Exceeding Constraints”, “Reaching Shadow Price Cap” and “Managing Congestion during SCED Failure” Updated step 2, 3 & 4 Updated scripts Updated scripts Added “Manual Commit of a Resource” as new procedure Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts Deleted procedure | January 31, 2011 |
| 2.3 4.1 4.6 7.1 7.2 | 1.0 / 1 1.0 / 5 1.0 / 3 1.0 / 3 1.0 / 2 | Updated Site Failovers & added W-N Active step Added Review Planned Outage Notes, Updated all steps in Transmission Issues in the Areas of the CFE DC-Ties and step 1 of SCED not able to Solve Congestion (Reached Max Shadow Price) Added Posting Manual Actions Updated Watch and Emergency Notice Updated step 2 in Implementation of EEA Level 2A | March 25, 2011 |
| 2.3 3.3 4.1 4.3 4.4 4.5 5.1 6.1 7.1 7.3 | 1.0 / 2 1.0 / 2 1.0 / 6 1.0 / 5 1.0 / 3 1.0 / 3 1.0 / 2 1.0 / 3 1.0 / 4 1.0 / 2 | Added steps and updated whole procedure Updated step 8 Updated Review Planned Outage Notes Added 1st Note Updated 1st Note and step VSAT Updated step Status Change in SPS Updated Definition in Remedial Switching Action Updated “PSS & AVR” 2nd note Updated step 1 in Watch and Emergency Notice and step Post Updated “Restore Firm Load” and “Move From EEA Level 3 to EEA Level 2B” step 1 | April 22, 2011 |
| 2.3 3.3 4.1 6.1 7.1 7.2 7.3 7.4 8.1 8.2 8.3 8.4 9.1 | 1.0 / 3 1.0 / 3 1.0 / 7 1.0 / 4 1.0 / 5 1.0 / 3 1.0 / 3 1.0 / 2 1.0 / 2 1.0 / 0 1.0 / 2 1.0 / 2 1.0 / 1 | Added step Site Failover Complete Updated step 2 Updated Critical Facilities and step 5 in Post-Contingency Overloads, changed Managing Binding and Exceeded Constraints procedure to Managing Constraints in SCED & updated procedure, deleted SCED not able to Solve Congestion procedure Updated 2nd Note and step 2 in Voltage Issues Updated all step 1’s Updated all step 1’s and deleted Note in Implement EEA Level 2A Updated all step 1’s Updated all steps Updated all steps Added new procedure Changed section number and updated all steps Changed section name and updated all steps Updated 1st Note and steps 2 & 3 | June 14, 2011 |
| 4.1 4.5 6.1 7.2 7.3 7.4 7.5 7.6 10.1 | 1.0 / 8 1.0 / 4 1.0 / 5 1.0 / 4 1.0 / 4 1.0 / 1 1.0 / 3 1.0 / 2 1.0 / 1 | Updated 2nd note & step Phase Shifters in Transmission Congestion Management, steps 3, 5 & 7 in Post-Contingency Overloads, Moved Transmission Issues in the Areas of the CFE DC Ties to 7.4 Updated 1st note, steps SPS Posting and Status Change in Special Protection Systems (SPS) (Identified as RAS in EMS) and Updated all steps in Mitigation Plan (MP) Updated 2nd note in Power System Stabilizers (PSS) & Automatic Voltage Regulators (AVR) Updated step 1 in Implement EEA Level 1 and 2A Updated step 1 in Move from EEA Level 1 to EEA 0 Moved procedure from section 4.1 Changed section number from 7.4 to 7.5 Changed section number from 7.5 to 7.6 Added Market Participant Backup Control Center Transfer procedure | July 20, 2011 |
| 4.1 4.4 4.6 6.1 8.4 8.5 | 1.0 / 9 1.0 / 4 1.0 / 4 1.0 / 6 1.0 / 0 1.0 / 3 | Updated step 5 in Post-Contingency Overloads and step Log in Managing Constraints in SCED Updated monitor section Updated step 1’s Updated step 2 and deleted For HHGT_G-O in Voltage Security Assessment Tool Added new procedure “Extreme Hot Weather” Changed section number | August 3, 2011 |
| 2.4 4.1 4.3 4.4 7.1 7.2 7.3 8.4 9.2 | 1.0 / 1 1.0 / 10 1.0 / 6 1.0 / 5 1.0 / 6 1.0 / 5 1.0 / 5 1.0 / 1 1.0 / 1 | Updated step Hotline Call Updated step 2 in Managing Constraints in SCED Updated step 2, 4 & 5, added step 3 Added 2nd note Updated step 1 in Watch Updated step 2 in Implement EEA Level 1, steps 1 & 2 in Implement EEA Level 2A Updated the step 1’s Updated temperature from 102 to 103 Updated 4th Note | September 1, 2011 |
| 3.3 4.2 7.2 7.3 7.4 7.5 9.1 | 1.0 / 4 1.0 / 4 1.0 / 6 1.0 / 6 1.0 / 2 1.0 / 4 1.0 / 2 | Updated Note to ensure compliance with IRO-008-1R2 Added 1st Note, added step 5, updated steps 4 & 6 Combined EEA 2 A and B per NPRR 379 Combined EEA 2 A and B per NPRR 379 Updated step 2 in Transmission Issues within CFE Updated step 1 in ERCOT picks up Load for Non-ERCOT System and step 1 in Non-ERCOT System picks up Load for ERCOT Updated step 2 | October 1, 2011 |
| 3.3 4.1 4.3 4.6 9.1 | 1.0 / 5 1.0 / 11 1.0 / 7 1.0 / 5 1.0 / 3 | Updated scripts Updated step 4 in Post Contingency Overloads & step 3 in Managing Constraints in SCED Updated step 3 Added Canceling RUC Commitments Added 3rd Note | November 1, 2011 |
| 2.3 3.1 4.1 4.4 4.5 4.6 6.1 7.1 8.1 8.3 | 1.0 / 4 1.0 / 1 1.0 / 12 1.0 / 6 1.0 / 5 1.0 / 6 1.0 / 7 1.0 / 7 1.0 / 3 1.0 / 3 | Updated step “Site Failover” Updated step “Review” Updated step 4 in Post-Contingency Overloads & added new procedure Post-Contingency Overloads on PUNs Updated 1st Note Updated step Status Change in SPS, step 1 in Remedial Action Plan (RAP) & Mitigation Plan (MP) Deleted 1st Note, changed titles to Manual Dispatch to take a Unit Off-line, Manual Dispatch to take a Unit of a CC Off-line, & updated procedure, changed title to Manual Dispatch to bring a Unit of a CC On-Line, & updated procedure Updated 2nd note and step 1 in Voltage Security Assessment Tool (VSAT)Updated Post in “Scripts” Added 2nd NOTE Updated OCN All procedures in this manual have been reviewed. | December 15, 2011 |
| 1.2 2.1 2.3 3.4 4.1 4.2 7.4 10.1 | 1.0 / 1 1.0 / 1 1.0 / 5 1.0 / 1 1.0 / 13 1.0 / 5 1.0 / 3 1.0 / 2 | Updated Scope Changed TSP to TO Updated database load script Changed insecure state to emergency condition Updated 1st Note, steps 6 & 8 in Post Contingency Overloads, steps 2 & 3 in Managing Constraints in SCED, added Model Inconsistencies/Updates procedure Updated Notes 1 & 2, Steps 1 & 2 Changed insecure state to emergency condition Updated Market Participant Backup Control Center Transfer | January 19, 2012 |
| 2.1 3.1 3.3 4.1 4.2 4.3 4.4 4.5 4.6 4.7 5.1 6.1 7.1 7.2 7.3 7.4 7.5 9.2 10.1 | 1.0 / 2 1.0 / 2 1.0 / 6 1.0 / 14 1.0 / 6 1.0 / 8 1.0 / 7 1.0 / 6 1.0 / 7 1.0 / 2 1.0 / 3 1.0 / 8 1.0 / 8 1.0 / 7 1.0 / 7 1.0 / 4 1.0 / 5 1.0 / 2 1.0 / 3 | Updated paragraph 4 Updated Operations Support Engineer Updated Operations Support Engineer & Desktop Guide reference Updated Operations Support Engineer, added 3rd Note, updated step 1 in Review Planned Outage Notes, steps 1, 2, 3, 4, 6, 7, 8, 9 & QSGR in Post Contingency Overloads, step 2, 4 & Log in Managing Constraints in SCED Updated Operations Support Engineer Updated Operations Support Engineer & step 1, 2 & 3 Updated Operations Support Engineer Updated Desktop Guide reference, 2nd Note, step 5 & SPS Posting & deleted step 4 in SPS, all steps in Mitigation Plan & Temporary Outage Action Plan Updated Desktop Guide reference Updated step 1 in Watch Updated TSP to TO, Operations Support Engineer & Desktop Guide reference Updated Operations Support Engineer, changed TSP to TO, Desktop Guide reference & step 1 of Power System Stabilizers (PSS) & Automatic Voltage Regulators (AVR) Updated step 1 in Watch Updated step 1 in Implement EEA Level 1 & step 1 in Implement EEA Level 3 Updated script in step 1 in Restore Firm Load Updated Operations Support Engineer & Desktop Guide reference Updated Operations Support Engineer & Desktop Guide reference Updated Desktop Guide reference Updated all steps in Telemetry Issues that could affect SCED and/or LMPs, step 1 in Backup/Alternate Control Center Transfer & Operations Support Engineer | March1, 2012 |
| 3.1 3.3 4.1 4.3 4.4 4.5 5.1 6.1 7.1 7.2 7.3 7.4 8.1 8.2 8.2 8.3 8.4 | 1.0 / 3 1.0 / 7 1.0 / 15 1.0 / 9 1.0 / 8 1.0 / 7 1.0 / 4 1.0 / 9 1.0 / 9 - / 8 1.0 / 8 1.0 / 5 1.0 / 4 1.0 / 0 1.0 / 4 1.0 / 2 1.0 / 4 | Updated step Gap Study Added TSAT Updated step 4 & deleted step 9 in Post-Contingency Overloads, clarified step 2 & 3 in Managing Constraints in SCED, Added Unsolved Contingencies Updated for TSAT tool, added Managing W-N during System Failures Updated step IROL and ‘instructing’ to ‘directing’ Updated step Status Change & ‘instructing’ to ‘directing’, updated step 3, 4 & log in RAP, added step 3 and log in PCAP, update Note, added TO Issue in MP Updated Opportunity Outage procedure Added Valley Import to VSAT procedure, deleted step 2 in PSS/AVR section Updated OCN, Advisory, Watch and Emergency Notice for Cold Weather and Extreme Cold Weather Added Load Management Programs in Implement EEA Added Load Management Programs in Restore EEA Updated for NPRR405 Changed ‘TDSP’ to ‘TO’ & T/S Operator to Real-Time Deleted Cold Weather Revised to 8.2 and changed Severe Cold Weather to Extreme Cold Weather Revised to 8.3, added OCN & Emergency Notice Revised to 8.4 and changed T/S Operator to Real-Time Operator | May 1, 2012 |
| 2.3 4.1 4.5 6.1 7.2 7.3 7.5 | 1.0 / 6 1.0 / 16 1.0 / 8 1.0 / 10 1.0 / 9 1.0 / 9 1.0 / 6 | Updated Database load with W-N active and Site Failover with W-N steps Added Constraint SF Cut Off step, updated step 2 & 3 in Managing Constraints in SCED Updated 2nd Note, added Basecase continuous SPS triggering step in SPS, updated step 1 in RAP, step Note, SCED unable to fully resolve constraint, & < 2% Absolute Shift Factors in MP, 1st Note in TOAP Updated step Valley Import Updated EILS to ERS per NPRR 451 Updated EILS to ERS per NPRR 451 Updated step 1 in ERCOT picks up Load for Non-ERCOT System and step 1 in Non-ERCOT System picks up Load for ERCOT | June 1, 2012 |
| 1.3 3.3 4.1 4.4 5.1 6.1 7.1 7.2 7.3 8.3 9.2 | 1.0 / 1 1.0 / 8 1.0 / 17 1.0 / 9 1.0 / 5 1.0 / 11 1.0 / 10 1.0 / 10 1.0 / 10 1.0 / 3 1.0 / 3 | Removed ERCOT Shift Supervisor paragraph Updated step 2 Updated step Constraint SF Cut Off, Managing Congestion during SCED Failure Updated step ≤300MW Updated Maintenance Level 2 and 3 outages Updated STP Voltage Tables Updated all step 1’s Updated Load Management Program Updated step 1 Updated scripts Updated 4th note | July 16, 2012 |
| 2.3 4.4 | 1.0 / 7 1.0 / 10 | Added Note to step Database Load Updated step IROL | August 29, 2012 |
| 2.3 2.4 3.3 4.1 4.3 4.4 4.5 4.7 6.1 7.1 7.2 7.3 7.4 7.6 8.1 8.2 8.3 8.4 | 1.0 / 8 1.0 / 2 1.0 / 9 1.0 / 18 1.0 / 10 1.0 / 11 1.0 / 9 1.0 / 3 1.0 / 12 1.0 / 11 1.0 / 11 1.0 / 11 1.0 / 6 1.0 / 3 1.0 / 5 1.0 / 6 1.0 / 4 1.0 / 5 | Added to make call to HHGT Added to make call to HHGT Added to make call to HHGT Updated PUN section and added to make call to HHGT Added Hotline script and to make call to HHGT Added Hotline script and to make call to HHGT Added to make call to HHGT Added to make call to HHGT Added to make call to HHGT Added to make call to HHGT Added to make call to HHGT Added to make call to HHGT Updated step 1 and added to make call to HHGT Added to make call to HHGT Added to make call to HHGT Added to make call to HHGT Added to make call to HHGT Added to make call to HHGT | September 12, 2012 |
| 2.2 3.1 3.2 3.3 3.4 4.1 4.3 4.4 4.5 5.1 5.2 6.1 7.4 8.3 9.1 | 1.0 / 1 1.0 / 4 1.0 / 2 1.0 / 10 1.0 / 2 1.0 / 19 1.0 / 11 1.0 / 12 1.0 / 10 1.0 / 6 1.0 / 1 1.0 / 13 1.0 / 7 1.0 / 5 1.0 / 4 | Added Hotline Call Communication Moved protective relay section to 5.2 Updated step 3 Split VSAT/TSAT and SE/RTCA out into separate procedures Updated steps Immediate Action Updated step Unknown Operating State, all steps in Evaluate Real-Time Contingency Analysis Results, steps 1, 4 & 6 in Post-Contingency Overloads Added 1st Note Added 1st Note, Updated 2nd NOTE & step 0 MW Updated 2nd Note Updated Returning from Planned Outage Early Added new procedure Updated Exceed URL, Reduce MW, added NOTE & moved step 1 to section 3.3 and renumbered Added Note Word smith OCN, Advisory, & Watch Updated step 1, 2 & 3. Added step 4 and Log All procedures in this manual have been reviewed. | November 1, 2012 |
| 3.2 3.5 4.1 4.4 4.5 6.1 7.2 7.5 | 1.0 / 3 1.0 / 0 1.0 / 20 1.0 / 13 1.0 / 11 1.0 / 14 1.0 / 12 1.0 / 7 | Updated step 3 Added procedure Updated Note, Constraint Shift Factor Cut Off, Post-Contingency Overloads steps 4-9 , QSGR & Managing Constraints in SCED step 2 & 4 Updated step VSAT Updated Special Protection Systems (SPS) (Identified as RAS in EMS) step 2, Remedial Action Plan (RAP) steps 1-5, & step 3 Pre-Contingency Action Plan (PCAP) Updated 2nd Note and steps 1-3 Voltage Issues Deleted step 2 per NPRR 480 Updated all step 1’s & added step 3 to clarify 6.5.9.5.2(1) | March1, 2013 |
| 2.3 2.4 3.1 3.3 3.5 4.1 4.2 4.3 4.4 4.5 4.6 4.7 5.1 6.1 7.1 7.2 7.3 7.4 7.6 8.1 8.2 8.3 8.4 | 1.0 / 9 1.0 / 3 1.0 / 5 1.0 / 11 1.0 / 1 1.0 / 21 1.0 / 7 1.0 / 12 1.0 / 14 1.0 / 12 1.0 / 8 1.0 / 4 1.0 / 7 1.0 / 15 1.0 / 12 1.0 / 13 1.0 / 12 1.0 / 8 1.0 / 4 1.0 / 6 1.0 / 6 1.0 / 6 1.0 / 6 | Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts and steps in Caution, Phase Shifters, Constraint Shift Factor Cut Off, Post Contingency Overloads, deleted Input Displays, added step In Series & Same Element in Managing Constraints in SCED & deleted Managing Congestion during SCED Failure Updated step 2 Deleted 2nd Note, added GTL and updated scripts Deleted 2nd Note, added GTL and updated scripts Deleted Directives, 1st Note in Mitigation Plan, 1st Note in Temporary Outage Action Plan and updated scripts Updated scripts Updated all steps and deleted Cancelation Updated script Updated script Added Generic script and Specific scripts Updated scripts Updated scripts Updated scripts Updated script Updated scripts Updated script Updated script Correct spelling and updated script | June 1, 2013 |
| 2.3 4.1 4.2 4.3 4.4 4.5 4.6 4.7 4.8 7.1 7.2 7.4 7.5 | 1.0 / 10 1.0 / 22 1.0 / 9 1.0 / 8 1.0 / 13 1.0 / 15 1.0 / 13 1.0 / 9 1.0 / 5 1.0 / 13 1.0 / 14 1.0 / 8 1.0 / 5 | Updated step EMS Changes and added MMS Changes Updated step Caution Updated and moved section 7.4 and renamed to 4.2 Changed section # Updated and changed section # Changed section #, IROL & updated step 0MW Changed section # & updated step 4 in RAPs Changed section # Changed section # Updated step 1 in Watch, Emergency Notice & DRUC Timeline not Met Updated 2nd Note Changed section # & step 2 Changed section # | July 15, 2013 |
| 2.3 4.1 4.2 4.5 6.1 7.1 | 1.0 / 11 1.0 / 23 1.0 / 10 1.0 / 16 1.0 / 16 - / 14 | Spelling correction to step MMS Changes Updated Caution, Constraint Shift Factor Cut Off, step 8 of Post-Contingency Overloads & PUN procedure Removed the word “load” Updated step VSAT Updated 2nd note & step 1 on Voltage Security Assessment Tool (VSAT) Updated Specific Scripts EMMS (LFC and RLC/SCED) Failure | August 9, 2013 |
| 2.3 2.4 3.3 3.5 4.1 4.2 4.4 4.5 4.6 4.8 7.1 7.2 7.3 7.5 8.1 8.2 8.3 8.4 | - / 12 - / 4 - / 12 - / 2 - / 24 1.0 / 11 1.0 / 14 1.0 / 17 1.0 / 14 1.0 / 6 1.0 / 15 1.0 / 15 1.0 / 13 1.0 / 6 1.0 / 7 1.0 / 7 1.0 / 7 1.0 / 7 | Removed HHGT TO reference Removed HHGT TO reference Removed HHGT TO reference Removed HHGT TO reference Removed HHGT TO reference Removed HHGT TO reference Removed HHGT TO reference Removed HHGT TO reference Removed HHGT TO reference Removed HHGT TO reference Removed HHGT TO reference Removed HHGT TO reference Removed HHGT TO reference Removed HHGT TO reference Removed HHGT TO reference Removed HHGT TO reference Removed HHGT TO reference Removed HHGT TO reference | August 30, 2013 |
| 4.1 5.1 6.1 | 1.0 / 25 1.0 / 8 1.0 / 17 | Updated step 5 in Post-Contingency Overloads Updated to reflect SCR770 changes Updated script and added new script for Power System Stabilizers (PSS) & Automatic Voltage Regulators (AVR) | September 27, 2013 |
| 3.3 3.4 3.5 4.1 4.2 4.4 4.5 4.6 4.7 4.8 4.9 5.1 5.2 6.1 7.1 7.2 7.3 7.5 8.1 8.2 8.3 8.4 9.2 10.1 | 1.0 / 13 1.0 / 3 1.0/ 3 1.0 / 26 1.0 / 12 1.0 / 15 1.0 / 18 1.0 / 15 1.0 / 10 1.0 / 7 1.0 / 0 1.0 / 9 1.0 / 1 1.0 / 18 1.0 / 16 1.0 / 16 1.0 / 14 1.0 / 7 1.0 / 8 1.0 / 8 1.0 / 8 1.0 / 8 1.0 / 4 1.0 / 4 | Updated Log steps Updated Log steps Updated Log step Updated step 1 on Review Planned Outage Notes, step 1 for PUNs, Managing Constraints in SCED and Logs Updated Title, added step 2 and Log steps Deleted step GTL, updated step 1 and Log Updated step VSAT, Log and deleted GTL Updated Log steps Updated Log steps Updated Log steps Added new procedure Updated steps Definition, Approve Maintenance Outage, Coordinate Maintenance, Coordinate Maintenance Level 2 and 3, Log and step 1 in Simple Transmission Outage Updated Log steps Updated VSAT section Updated Log steps Updated Log steps Added step Reserves and Log steps Updated Log steps Updated note, OCN, Advisory and Log step Added note, updated OCN, Advisory, Watch and Log step Added note, updated OCN, Advisory, Watch and Log step Updated note and Log step Updated Log steps Updated Log steps All procedures in this manual have been reviewed | December 13, 2013 |
| 4.2 4.4 4.5 4.6 4.7 4.8 4.9 4.10 7.1 | 1.0 / 13 1.0 / 16 1.0 / 19 1.0 / 0 1.0 / 16 1.0 / 11 1.0 / 8 1.0 / 1 1.0 / 17 | Updated 1st Note, step 3, added step 4 & deleted step 5 in Transmission Issues within ERCOT. Added Note to Transmission/Capacity Issues within the CFE Area Removed posting requirement Removed posting requirement New procedure for new GTL Updated section number Updated section number Updated section number Updated section number & changed Watch to OCN Updated to incorporate NPRR542 and update scripts | January 1, 2014 |
| 4.1 4.2 4.6 7.3 8.4 | 1.0 / 27 1.0 / 14 1.0 / 1 1.0 / 15 1.0 / 9 | Updated step 3 in Post-Contingency Overloads Updated step 3, 4 in Transmission Issues within ERCOT and step 1, 2 & 3 in Transmission/Capacity Issues within the CFE Area Updated step 1 & 2 Updated steps Reserves and 1 in Restore Firm Load Updated 1st Note | February 25, 2014 |
| 4.1 4.2 4.4 4.5 4.8 6.1 7.2 7.4 9.1 | 1.0 / 28 1.0 / 15 1.0 / 17 1.0 / 20 1.0 / 12 1.0 / 19 1.0 / 17 1.0 / 9 1.0 / 5 | Updated VDI information Updated steps in Transmission Issues within ERCOT Updated VDI information Updated VDI information Updated Manual commitment process Updated VDI information Updated media appeal language & LM Program Updated VDI information Updated step 1 & 3, added step 5 | April 4, 2014 |
| 2.2 4.1 4.2 4.4 4.6 4.7 4.9 6.1 7.1 8.1 | 1.0 / 2 1.0 / 29 1.0 / 16 1.0 / 18 1.0 / 2 1.0 / 17 1.0 / 9 1.0 / 20 1.0 / 18 1.0 / 9 | Added VDI to Master QSEs Updated step 1 in Review Planned Outage Notes, QSGR & Log in Post-Contingency Overloads & PUN steps Updated section title & step 5, deleted step 3 Updated step 2 Updated step 1 & 2 Updated step 1 in RAP Deleted Note Updated Note & Step 1 in Voltage Issues Added Note, updated Market Notices Advisory & Watch Updated scripts | June 1, 2014 |
| 4.1 4.2 4.7 7.2 | 1.0 / 30 1.0 / 17 1.0 / 18 1.0 / 18 | Changed WGR to IRR & updated desktop reference Updated step 4 & 6 Updated 1st Note Added Media Appeal & updated step 1 script | August 1, 2014 |
| 4.1 5.1 6.1 7.1 | 1.0 / 31 1.0 / 10 1.0 / 21 1.0 / 19 | Updated desktop reference number & step 3 in Post-Contingency Overloads, added step 4 to PUN section Updated desktop reference number Updated step 1, 2 & 3 in Real-Time Voltage Issues, added Future Voltage Issues Updated Generic Script | October 1, 2014 |
| 2.3 2.4 3.3 3.5 4.1 4.2 4.4 4.5 4.6 4.7 4.8 4.9 5.1 6.1 7.1 7.2 10.1 | 1.0 / 13 1.0 / 5 1.0 / 14 1.0 / 4 1.0 / 32 1.0 / 18 1.0 / 21 1.0 / 3 1.0 / 19 1.0 / 13 1.0 / 10 1.0 / 2 1.0 / 11 1.0 / 22 1.0 / 20 1.0 / 19 1.0 / 5 | Removed references to W-N Updated scripts Removed references to W-N/TSAT, combined SE/RTCA Updated for Operating Guide 4.7 Updated Phase Shifters & removed references to TSAT Removed references to TSAT & added Future Studies Deleted West to North procedure and re-numbered Re-numbered Re-numbered Re-numbered Re-numbered Re-numbered Updated step 1 Updated step 2 & 3 in Real-Time Voltage Issues, Future Voltage Issues & Requesting Resource to operate beyond URL Updated Specific Scripts Updated EEA2 script Deleted Requests to decommit in Operating Period All procedures in this manual have been reviewed | December 15, 2014 |
| 2.2 4.1 4.2 4.3 4.4 4.7 4.8 6.1 7.4 8.2 | 1.0 / 3 1.0 / 33 1.0 / 19 1.0 / 9 1.0 / 22 1.0 / 14 1.0 / 11 1.0 / 23 1.0 / 10 1.0 / 9 | Added definitions for Dispatch and VDIs Updated “Review Planned Outage Notes” and provided a better flow, deleted redundant steps & added Basecase Overloads, Added step Topology Change Updated to reflect SOL Methodology and provide a better flow Updated step <200MW Updated step 1 Updated script Updated step Exceeding URL or Reducing Output Updated all steps for better flow Updated scripts | March 1, 2015 |
| 3.5 4.2 4.5 4.9 9.1 | 1.0 / 5 1.0 / 20 1.0 / 4 1.0 / 3 1.0 / 6 | Updated GMD process Updated step 2 of Rio Grande Valley Renamed to GTC Stability and added Ajo – Zorrillo Updated to new name Generic Transmission Constraint Updated scripts | March 30, 2015 |
| 2.3 2.4 3.3 3.5 4.1 4.2 4.3 4.4 4.5 4.6 4.8 4.9 7.1 7.2 7.3 7.4 7.5 7.6 8.1 8.2 8.3 8.4 9.1 | 1.0 / 14 1.0 / 6 1.0 / 15 1.0 / 6 1.0 / 34 1.0 / 21 1.0 / 10 1.0 / 23 1.0 / 5 1.0 / 20 1.0 / 12 1.0 / 4 1.0 / 21 1.0 / 0 - / 20 - / 16 1.0 / 11 1.0 / 8 - / 10 - / 10 - / 9 - / 10 1.0 / 7 | Moved scripts to script procedure Moved scripts to script procedure Moved scripts to script procedure & updated GTL to GTC Moved scripts to script procedure Updated step 1 QSE Requests to Decommit a Resource, updated GTL to GTC, and moved scripts to script procedure Moved scripts to script procedure Moved scripts to script procedure Moved scripts to script procedure & updated GTL to GTC Renamed and updated Zorrillo – Ajo table Moved scripts to script procedure Updated for implementation of NOGRR135/NPRR642 and moved scripts to script procedure Moved scripts to script procedure & updated GTL to GTC Updated 50% Probability Of Down Ramp to 30%, removed 70% Probability Of Up Ramp, added note and moved scripts to script procedure New process for implementation of NOGRR135/NPRR642 Updated section number and moved scripts to script procedure Updated section number and moved scripts to script procedure Updated section number Updated section number and moved scripts to script procedure Moved scripts to script procedure Moved scripts to script procedure Moved scripts to script procedure Moved scripts to script procedure Moved scripts to script procedure | May 1, 2015 |
| All Sections 2.3 3.1 3.5 4.4 | 1.0 / 1 1.0 / 15 1.0 / 6 1.0 / 7 1.0 / 24 | Added a “T” for TO scripts Renamed section to Site Failovers and Database Loads Updated Gap Study Updated Procedure Purpose. Updated GMD MIS Posting Scripts to include “until time” Updated procedure purpose and step ≤500MW | July 15, 2015 |
| 4.1 4.5 | 1.0 / 35 1.0 / 6 | Updated step 1 Post-Contingency Overloads Replaced East Texas Stability with Panhandle Stability Added Laredo Import Stability Removed Zorillo – Ajo Table | September 9, 2015 |
| 4.5 7.2 | 1.0 / 7 1.0 / 1 | Removed Panhandle Stability Step 1, updated Step 2 and Laredo Area Stability Updated Double-Circuit Contingency actions | October 1, 2015 |
| 2.3 3.3 3.5 4.1 4.2 4.3 4.4 4.5 4.6 4.8 4.9 7.1 7.3 7.4 7.6 8.1 8.2 8.3 8.4 9.1 | 1.0 / 16 1.0 / 16 1.0 / 8 1.0 / 36 1.0 / 22 1.0 / 11 1.0 / 25 - / 8 1.0 / 21 1.0 / 13 1.0 / 5 1.0 / 22 1.0 / 21 1.0 / 17 1.0 / 9 1.0 / 11 1.0 / 11 1.0 / 10 1.0 / 11 1.0 / 8 | Updated step Site Failover T#17 Updated step Site Failover Complete T#18 Updated State Estimator/RTCA step 3 T#21 & step 7 T#22 Updated Voltage Security Assessment Tool (VSAT) step 2 T#23 & step 6 T#24 Updated step 1 T#25 Updated step K Level Increases/Decreases T#26 Updated step Cancel T#27 Updated Review Planned Outage notes step Cascading Condition Updated Basecase Overloads step Qualifying Facilities T#28 Updated Rio Grande Valley step 2 Added Rio Grande Valley step Reliability Margin <100 MW Updated Rio Grande Valley step 3 T#29 Updated step Cascading Condition Updated Pre-Contingency Load Shedding to avoid Post-Contingency cascading step 3 T#30 Updated step ≤300 T#31 Updated step ≤100 T#32 Updated step 0MW T#33 Updated Laredo Area Stability step 4 T#29 Updated Zorrillo – Ajo 345kV Stability step 1 & step 2 Added Liston Stability Added Molina Stability Updated Special Protective Systems (SPS) step SPS Posting Updated Mitigation Plan (MP) step Issue Watch T#34 Updated Mitigation Plan (MP) step Cancel Watch T#35 Updated Advisory step Cancel Advisory T#2 Updated Watch step Issue Watch T#3 Updated Watch step Cancel Watch T#4 Updated step GTC T#36 Updated Title Operating Condition Scripts Updated Operating Condition Scripts step Hotline T#37 Updated Operating Condition Scripts step Hotline Cancellation T#38 Updated Title Specific Scripts for QSE’s Updated Specific Scripts for QSE’s step 30% Probability Of Down Ramp T#39 & T#40 Updated Specific Scripts for QSE’s step Failure T#41 & T#42 Updated Specific Scripts for QSE’s step EMMS (LFC and RLC/SCED) Failure T#43 & T#44 Updated Specific Scripts for QSE’s step Increasing Amount of Ancillary Services T#45 & T#46 Updated Specific Scripts for QSE’s step A/S Insufficiency Offers in DAM T#47 & T#48 Updated Specific Scripts for QSE’s step REG/RRS – RUC Committed Shortages T#51 & T#52 Updated Specific Scripts for QSE’s step DAM Timeline Deviation T#53 & T#54 Updated Specific Scripts for QSE’s step DAM Failure T#55 & T#56 Updated Specific Scripts for QSE’s step DRUC Delay or Timeline Deviation T#57 & T#58 Updated Specific Scripts for QSE’s step DRUC Timeline not Met T#59 & T#60 Updated Specific Scripts for QSE’s step HRUC Failure or Timeline Deviation T#61 & T#62 Updated Specific Scripts for QSE’s step DRUC Committed for Capacity Shortage T#63 & T#64 Updated Specific Scripts for QSE’s step Excess Generation T#65 & T#66 Updated Specific Scripts for QSE’s step Projected Reserve Capacity Shortage with no market solution T#67 & T#68 Updated Specific Scripts for QSE’s step RMR Projected Reserve Capacity Shortage T#69 & T#70 Update first note, Updated Implement EEA Level 1 step Load Management title T#6 Updated Implement EEA Level 2 step 1 T#7 Updated Implement EEA Level 3 step 1 T#8, and Implement NPRR708 for EEA Updated Restore Firm Load step 1 T#9 & T#10 Updated Move from EEA Level 1 to EEA 0 step 1 T#13 Updated step Return to Normal TO Notification T#71 Updated step OCN T#72 Updated step Advisory T#73 Updated step Watch T#74 Updated step Emergency T#75 Updated step OCN T#76 Updated step Advisory T#77 Updated step Watch T#78 Updated step Emergency Notice T#79 Updated step OCN T#80 Updated step Advisory T#81 Updated step Watch T#82 Updated step Emergency Notice T#83 Updated step OCN/Advisory/Watch T#84 Updated step 2 T#85 All procedures in this manual have been reviewed | December 31, 2015 |
| 2.1 4.1 4.3 4.5 4.6 5.1 6.1 7.1 9.1 | 1.0 / 3 1.0 / 37 1.0 / 12 1.0 / 9 1.0 / 22 1.0 / 12 1.0 / 24 1.0 / 23 1.0 / 9 | Updated System Operator Responsibilities and Authority Updated NERC Standard Reference Updated NERC Standard Reference Updated Molina Stability Updated NERC Standard Reference Updated NERC Standard Reference Updated NERC standard Reference Updated Voltage Security Assessment Tool step 1 table Updated PSS & AVR step Note Added Specific Scripts for QSE’s T#86 Updated Specific Scripts for QSE’s T#51 Updated Alert Levels | February 1, 2016 February 10, 2016 |
| 1.3 6.1 7.1 | 1.0 / 2 1.0 / 25 1.0 / 24 | Removed Interchange Coordinator Updated STP Voltage Table Updated Execute a SASM script title T#86 |  |
| 3.1 4.1 4.2 4.4 4.5 6.1 | 1.0 / 11 1.0 / 38 1.0 / 23 1.0 / 26 1.0 / 10 1.0 / 26 | Updated step STP Lines Updated Review Planned Outages Cascading Condition Updated Reliability Margin Updated ≤300MW Updated Zorrillo – Ajo 345kV Stability step 1 Updated step STP Voltage Table, 1 and 2 | April 29, 2016 |
| 2.1 2.2 4.1 4.2 4.3 4.4 4.5 4.6 6.1 7.1 7.4 7.5 | 1.0 / 4 1.0 / 4 1.0 / 39 1.0 / 24 1.0 / 13 1.0 / 27 1.0 / 11 1.0 / 23 1.0 / 27 1.0 / 25 1.0 / 18 1.0 / 12 | Updated for COM-002-4 Updated steps for COM-002-4 Updated steps for NPRR748, NOSCED and COM-002-4 Updated Reliability Margin Updated steps for COM-002-4 Updated steps for COM-002-4 Updated step for COM-002-4 Updated steps for COM-002-4 Updated steps for COM-002-4 Updated steps for COM-002-4 & added Typical Script T#87 BAAL Firm Load Shed Updated Restore Firm Load step 1 Updated steps for COM-002-4 | June 30, 2016 |
| 4.2 4.5 6.1 7.1 | 1.0 / 25 1.0 / 12 - / 28 1.0 / 26 | Updated RUC/Future Studies & Deleted Note Added Zorillo-Ajo 345 kV Stability note Replaced step 1 with note Updated Liston Stability Step 1 & Step 2 Removed Molina Stability Added Red Tap Stability Updated Real-Time Voltage Issues note Updated ERCOT requesting Resource to operate beyond URL Exceeding URL or Reducing Output Updated Voltage Security Assessment Tool step 1 Updated Specific Scripts for QSE’s T#43 T#44, T#61 & T#62 | September 30, 2016 |
| 4.1 4.5 | 1.0 / 40 1.0 / 13 | Updated Review Planned Outage Notes step Cascading Condition Added Basecase / Post-Contingency Exceedance of Phase Angle Added Panhandle Stability step Weighted Short Circuit Ratio and updated step 1 Added Pomelo Stability | November 2, 2016 |
| 3.3 3.6 4.1 4.5 4.6 6.1 10.1 | 1.0 / 17 1.0 / 0 1.0 / 41 1.0 / 14 1.0 / 24 1.0 / 29 1.0 / 6 | Updated Notes and State Estimator/RTCA section Created a new procedure for resolving Real-time Data Issues per NOGRR162 Updated 2nd Note, step 3 Post-Contingency Overloads Updated Laredo Area Stability step 1 Updated Special Protection Systems (SPS) to Remedial Action Schemes (RAS) Updated per STP agreement Deleted Telemetry Issue that could affect SCED and/or LMPs All procedures in this manual have been reviewed | December 30, 2016 |
| 1.1 1.3 2.1 2.3 2.4 3.1 3.2 3.3 3.5 3.6 4.1 4.2 4.3 4.5 4.6 4.7 5.2 6.1 7.1 7.3 7.5 7.6 8.2 8.3 10.1 | 1.0 / 3 1.0 / 5 1.0 / 17 1.0 / 7 1.0 / 8 1.0 / 4 1.0 / 18 1.0 / 9 1.0 / 1 1.0 / 42 1.0 / 26 1.0 / 14 1.0 / 15 1.0 / 25 1.0 / 15 1.0 / 2 1.0 / 30 1.0 / 27 1.0 / 22 1.0 / 13 1.0 / 10 1.0 / 12 1.0 / 11 1.0 / 7 | Updated Introduction Purpose Deleted section 1.3 Updated for IRO-001-4 Updated procedure purpose Updated procedure purpose Updated GAP Study Updated categories to show RAS Updated Notes Updated Voltage Security Assessment Tool step 2 Updated procedure purpose Changed step Situational Awareness to Mitigating Activities Added step IROL Deleted step Unknown State Updated step ONTEST Updated Reliability Margin Updated CFE to CENACE Updated step Note Updated Zorillo - AJO Stability step 1 Removed Liston Stability Updated Red Tap Stability step 1 Updated Pomelo Stability step 1 Added Bakersfield Stability Updated title with AMP Updated Remedial Action Schemes (RAS) steps Added Automatic Mitigation Plan (AMP) Updated Remedial Action Plan (RAP) step 1 & 5 Updated Pre-Contingency Action Plan (PCAP) step 1 & 2 Updated Mitigation Plan (MP) steps fully resolve constraint, <2% Absolute Shift Factors and Contingency Occurs Updated Note & Manual Dispatch to take a Unit Off-Line Updated Planned Outage Updated title to Voltage Issues at Nuclear Power Plants Added Real-Time Voltage Issues step 3 Updated ERCOT requesting Resource to operate beyond URL steps Updated heading title, OCN step 1, Advisory step 1, Watch step 1, and Emergency Notice step 1 Implement EEA Level 3 Moved step 1 to step 2 & added step 1 Updated CFE to CENACE Updated note Updated Procedure Purpose Updated Procedure Purpose Updated Heading title to QSE Issues | March 31, 2017 |
| 3.3 3.6 4.1 4.2 4.4 | 1.0 / 19 1.0 / 2 1.0 / 43 1.0 / 27 1.0 / 28 | Added Section on ICCP Outages Updated IROL Added Section Post-Contingency Overloads on the South DC Ties Updated Model Inconsistencies/Updates step 2 Updated step Reliability Margin, step 1 and added Cancel Updated step Reliability Margin | April 6, 2017 |
| 3.6 4.1 4.4 4.5 5.2 | 1.0 / 3 1.0 / 44 1.0 / 29 1.0 / 16 1.0 / 3 | Updated step IROL Updated Post-Contingency Overloads on the South DC Ties step 1 Updated step ≤400MW Removed Bakersfield Stability Updated steps | June 1, 2017 |
| 7.1 7.3 | 1.0 / 28 1.0 / 23 | Updated step BAAL Firm Load Shed Updated Implement EEA Level 3 step 2 | June 30, 2017 |
| 3.3 3.7 4.1 7.3 | 1.0 / 20 1.0 / 0 1.0 / 45 1.0 / 24 | Updated Procedure Purpose Deleted notes and updated State Estimator/RTCA step 1 Added new section Real-time Assessment (RTA) Added new procedure Manual Real-time Assessment (RTA) Added new section Monitoring Sub Synchronous Resonance (SSR) Added Note to EEA Level 2 and EEA Level 3 | July 28, 2017 |
| 4.5 5.1 7.3 | 1.0 / 17 1.0 / 13 1.0 / 25 | Deleted Laredo Area Stability Renamed Pomelo to North Edinburg – Lobo & updated Added Rescheduled High Impact Outage (RO) Updated 1st note | August 31, 2017 |
| 6.1 | 1.0 / 31 | Added East HVDC Tie Voltage Limits | September 29, 2017 |
| 4.5 6.1 | 1.0 / 18 1.0 / 32 | Renamed Zorillo - Ajo 345kV Stability to Nelson Sharpe – Rio Hondo 345kV Stability Added new GTC East Texas Stability Updated Power System Stabilizers (PSS) & Automatic Voltage Regulators (AVR) note | October 31, 2017 |
| 4.1 9.2 | 1.0 / 46 1.0 / 5 | All procedures in this manual have been reviewed Added Operating Instruction and EDI scenario Unsolved Contingencies Updated Primary Control Center 4th note | December 28, 2017 |
| 3.3 6.1 | 1.0 / 21 1.0 / 33 | Updated Procedure Purpose, added ICCP Outages to include MIS and outage scheduler Updated Future Voltage Issues and updated Power System Stabilizers (PSS) & Automatic Voltage Regulators (AVR) step 1 | February 28, 2018 |
| 3.6 4.5 | 1.0 / 4 1.0 / 19 | Updated Real-Time Data Issues known by the TO and Real-Time Data Issues that affect Network Security Analysis steps Added new GTC McCamey Stability | March 30, 2018 |
| 2.2 4.2 4.5 7.1 | 1.0 / 5 1.0 / 28 1.0 / 20 1.0 / 29 | Updated procedure purpose Updated Rio Grande Valley step Reliability Margin Added new GTC Treadwell Stability Added Unannounced Constant Frequency Control Test | May 1, 2018 |
| 4.1 4.2 4.4 4.5 6.1 7.5 | 1.0 / 47 1.0 / 29 1.0 / 30 1.0 / 21 1.0 / 34 1.0 / 14 | Added Phase Shifter Updated Rio Grande Valley step 2 Updated North – Houston step ≤400MW Updated Treadwell Stability Added Generator Voltage Set Points Updated steps and added Emergency Dispatch Instruction Confirmation Emergency | May 31, 2018 |
| 3.1 4.1 4.2 4.3 4.4 7.4 | 1.0 / 9 1.0 / 48 1.0 / 30 1.0 / 15 1.0 / 31 1.0 / 19 | Updated step STP Lines Updated note Updates step 1 for Rio Grande Valley Updated 1st note and Studies step Updated step ≤300MW Clarified step in Move from EEA Level 1 to EEA 0 | August 31, 2018 |
| 4.1 4.2 | 1.0 / 49 1.0 / 31 | Updated Post-Contingency Overloads on the South DC Ties step 1 for NPRR 825 Updated Unsolved Contingencies step 1 Updated SSR Alerts to SSR Alarms Updated Rio Grande Valley step 1 for NPRR 825 | October 1, 2018 |
| 7.5 | 1.0 / 15 | BLT RC Notification | November 1, 2018 |
| 4.6 6.1 | 1.0 / 26 1.0 / 35 | ## Added step 6 to Remedial Action Plan (RAP) Added step and renumbered steps to Power System Stabilizers (PSS) & Automatic Voltage Regulators (AVR) All procedures in this manual have been reviewed | December 28, 2018 |
| 4.2 4.9 | 1.0 / 32 1.0 / 6 | ## Updated step 1 ## Updated GTC | January 31, 2019 |
| 3.5 4.1 4.5 4.9 | 1.0 / 10 1.0 / 50 1.0 / 22 1.0 / 7 | ## Updated step Mitigating Activities ## Updated step Qualifying Resources Added Raymondville – Rio Hondo Stability Updated step GTC and added note | March 29, 2019 |
| 4.1 | 1.0 / 51 | ## Added Note | May 01, 2019 |
| 7.3 | 1.0 / 26 | ## Moved Load Management Program from EEA1 to EEA2 | May 31, 2019 |
| 4.3 7.3 | 1.0 / 16 1.0 / 27 | ## Updated step Cascading Condition Updated Implement EEA Level 3 step 2 | August 1, 2019 |
| 3.3 4.1 4.5 4.6 7.1 7.3 9.1 | 1.0 / 22 1.0 / 52 1.0 / 23 1.0 / 27 1.0 / 30 1.0 / 28 1.0 / 10 | ## Updated State Estimator/RTCA step 1 Updated Title to Monitoring Sub Synchronous Resonance (SSR) and process, Added Monitoring Sub Synchronous Resonance (SSR) without Capacitor Switching action and Added Unresolvable Congestion with EMR Generation available ## Updated Panhandle Stability steps and updated Raymondville – Rio Hondo Stability step 1 Updated step RAS Status Change Updated Specific Scripts for QSE’s steps Added Typical Hotline Script for Media Appeal Added step 3 and renumbered steps | November 1, 2019 |
| 3.1 4.1 4.5 7.3 7.4 | 1.0 / 10 1.0 / 53 1.0 / 24 1.0 / 29 1.0 / 20 | Updated STP lines Updated step 3 in Managing Constraints in SCED Deleted GTC Notes and added Bearkat Stability Updated MSSC Updated MSSC All procedures in this manual have been reviewed | January 1, 2020 |