- Power Operations Bulletin # 927

ERCOT has posted/revised the Reliability Unit Commitment manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

- http://www.ercot.com/mktrules/guides/procedures/index.html

## 2.3	Publish A/S Requirements and Review System Conditions

Procedure Purpose:  To publish and verify daily Ancillary Service requirements are posted to the market.

| Protocol Reference | 4.2.1.1(1) | 4.2.1.1(2) | 4.2.1.2(2) | 4.3(2) |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | BAL-002-2 R2 | EOP-011-1 R2, R2.1, R2.2, R2.3, R2.2.3.2, R2.2.3.3 | TOP-002-4 R4, R4.4 |  |

| Version: 1 | Revision: 14 | Effective Date: January 31, 2020 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - Review and update A/S Requirements must be completed prior to 0500. - The Shift Supervisor must verify the posted ancillary service requirements for the 1st day of the month. |
| ### Review Weather Data Information |  |
| 1 | REVIEW the Weather Data for the next operating day in the EMS. |
| 2 | REVIEW REFERENCE DISPLAY: EMS Applications>Weather Details>Real Time Displays>Weather Forecast Directory IF: - The Last Weather Source Update or Last Weather Read is less than one (1) hour old; THEN: - Using the usual sources, review the weather forecast for at least two days out. IF: - The data update or read is more than one (1) hour old; THEN: - Notify the Shift Supervisor and the Help Desk. |
| 3 | Evaluating the weather forecast for several days ahead is needed to help determine if there is a potential for fuel supply problems. The trigger will usually be an extreme weather event which will cause temperatures to be below freezing for an extended period of time, though there could be other reasons. It may be necessary to consider fuel switching and optimize fuel supply if a reliability issue exists. |
| Fuel Switching | IF: - Notified of fuel limitations; THEN: - Consult with Supervisor and determine if reliability concerns exits - Identify potential transmission issues - Identify potential capacity issues IF: - Reliability concerns exists; THEN: - Consider fuel switching options (gas to oil) if capability exists. |
| Optimize Fuel Supply | IF: - A particular fuel supply is at risk; THEN: - Consult with Supervisor and determine if reliability concerns exits - Identify potential transmission issues - Identify potential capacity issues IF: - Reliability concerns exists; THEN: - Consider RUC committing Resources with fuel that is not at risk. |
| ### Review and Select Load Forecast |  |
| 1 | - Review and Select load forecast for next day (Refer to Desktop Guide RUC Section 2.17. |
| 2 | IF: - There is a large difference between the load forecasts, AND - There is uncertainty on which load forecast is correct; THEN: - Call the Load Forecasting group for guidance on updating the weather or load forecast. |
| 3 | Notify by e-mail the following distribution lists of the issue: - Load Forecasting & Analysis - 1 ERCOT Shift Supervisors |
| ### Publish A/S Requirements |  |
| 1 | REFERENCE DISPLAY: Market Participation > Physical Market > AS Market > AS Plan Before 04:00, verify the hourly ERCOT system total A/S requirements for each of the following, for each hour of the operating day: - Reg-Up; - RRS. - Reg-Down; - Non-Spin. |
| 2 | REFERENCE DISPLAY: Market Participation > Monitoring > Event Manager > Events Search / Filter for AS_OBLIGATION_CALC Before 06:00, verify the hourly ERCOT system total A/S requirements have been automatically published at 04:55: IF: - Status indicates complete, no further action is necessary, OR - Status indicates anything else; THEN: - Change status to start now and select submit to database poke point. |
| ### Increasing A/S Requirements before A/S Obligations Publish |  |
| NOTE | This procedure would be performed when it has been determined that additional A/S is needed, such as to support a weather event. |
| NOTE | If an Emergency Condition may exist that would adversely affect system reliability, ERCOT may change the percentage of Load Resources that are allowed to provide RRS from the monthly amounts determined previously. |
| 1 | REFERENCE DISPLAY: Market Participation > Physical Market > AS Market > AS Plan Before 04:00, increase the hourly ERCOT system total A/S requirements for each requirement needed for each hour of the next operating day: - Reg-Up; - RRS. - Reg-Down; - Non-Spin. |
| 2 | REFERENCE DISPLAY: Market Participation > Monitoring > Event Manager > Events Search / Filter for AS_OBLIGATION_CALC Before 06:00, verify the hourly ERCOT system total A/S requirements have been automatically published at 04:55: IF: - Status indicates complete, no further action is necessary, OR - Status indicates anything else; THEN: - Change status to start now and select submit to database poke point. |
| 3 | IF: - The A/S requirements were increased, THEN: - The next day will copy the new A/S requirements unless you return the A/S requirements to the A/S Plan requirements for the month. REFERENCE DISPLAY: - Market Participation > Physical Market > AS Market > AS Plan Before 04:00 update the A/S requirements. |
| NOTE | Refer to the A/S requirements for the current month’s A/S Plan if no changes are required. |
| ### Priority Outages |  |
| 1 | A Priority Outage is one that affects generation. Prior to 1200: - Review the Outage Notes for the next Operating Day, make lists of Priority Outages, sorted by the affected TOs, - The file is located in P:\DAY AHEAD – TDSP PRIORITY OUTAGE NOTIFICATION, - Email the Priority Outages to the appropriate TO using the email addresses provided in the RUC Desktop Guide Section 2.22, - Copy and paste the information into the body of the email, - The Subject line should read “Priority Outages”, “<Company Name>”, “<Date>” - At the bottom of each email, be sure to include a Confidentiality Notice and your signature, - Ensure each document has a Note which states to notify ERCOT within 30 minutes of the Actual Start and Actual End times for the Priority Outages, - If email is unavailable, follow the same guidelines using the Fax Machine, - Place hard copies in Daily Log File. |
| ### Blackstart Availability |  |
| 1 | REFERENCE DISPLAY: Market Participation > Physical Market > Market Participant Submissions > Availability Plan ERCOT SharePoint > System Operations – Control Center > Documents > Blackstart Availability REVIEW: - Blackstart Availability Plan for next operating day (OD+1 tab) IF: - Blackstart Availability Plan for next operating day is missing THEN: - Call the QSE and request them to submit their Blackstart Availability Plan for next operating day - Update the Blackstart Availability spreadsheet located on SharePoint |
| Log | LOG when completed and any additional actions taken. |
| ### Verification of Published A/S Requirements |  |
| NOTE | This step may be completed after 0600. |
| 1 | VERIFY by spot-checking the following information posted to the ERCOT Market Information System (MIS) for the next operating day (or two days if two-day Ahead market is in effect) is posted. - Planned Transmission line and equipment outages for the operating day. - MIS; Grid; Transmission; Transmission Outages; Approved and Accepted Transmission Outages - Weather assumptions used to provide the system conditions forecast. - MIS; Markets; Day-Ahead Market; Day-Ahead Public Information; Weather assumptions - The hourly ERCOT System total Ancillary Service requirements for Regulation Down – REGDN, Regulation Up – REGUP, Responsive Reserve – RRS, and Non-spinning Reserve – NSPIN. - MIS; Markets; Day-Ahead Market; Ancillary Service Plans; DAM Ancillary Service Plan. |
| Log | LOG any significant problems including any action taken. |

## 3.1	Tasks prior to Execution of HRUC

Procedure Purpose:  To make manual corrections for bad/suspect telemetry, load forecast modifications, or to RUC commit/de-commit Resources prior to running the RUC process.

| Protocol Reference | 3.12.1(3) | 5.1 | 5.2.2.2(11) | 5.3(3) |
| --- | --- | --- | --- | --- |
|  | 5.5.1 | 5.5.2(9) |  |  |
| Guide Reference |  |  |  |  |
| NERC Standard | TOP-002-4 R4, R4.2, R4.3 |  |  |  |

| Version: 1 | Revision: 9 | Effective Date: January 31, 2020 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Tasks prior to execution of HRUC |  |
| NOTE | The RUC Study Period for DRUC is the next Operating Day. The RUC Study Period for HRUC is the balance of the current Operating Day plus the next Operating Day if the DRUC for the Operating Day has been solved or after 18:00 if DRUC did not solve. |
| Continuous Monitoring | REVIEW REFERENCE DISPLAY: Market Operation>EMS Interface>EMSI Workflow Parameters Market Operation>EMS Interface>EMSI Workflow IF: - The EMSI Workflow Parameters does not indicate EMSI has run in the last hour and Load Forecast are NOT running (should be continuous); THEN: - Open EMSI Workflow, select “Start up”. When start up is complete, select “Run”. IF: - EMSI Workflow does not complete; THEN: - Notify Helpdesk and Control Room staff. |
| Load Forecast | Periodically monitor the Load Forecast to ensure it is accurate: IF: - Adjustments need to be made, they will be done in the EMS and updated to the MMS; THEN: - Adjust (Refer to Desktop Guide RUC Section 2.17). |
| Wind Forecast Updates | Periodically monitor the Wind Forecast and verify data is updating: IF: - Wind forecast is not updating; THEN: - Notify Supply Integration & Grid Application group, - Be aware that this could skew HRUC results. |
| RMR Consideration | All other generation resources should be considered prior to a RMR commitment for capacity purposes: IF: - An RMR unit needs to be considered in HRUC; THEN: - Ensure COP status is “OFF”. IF: - An RMR unit is needed but is not to be considered in HRUC; THEN: - Commit unit before HRUC is executed, - Follow 3.2 Review, Approve and Post HRUC Results step RMR Commitment. |
| COP Validation | REVIEW REFERENCE DISPLAY: Market Participation>Monitoring>Event Manager>Events>filter Event Name for COP Validation IF: - A Resource Forced Outage has occurred and the QSE has not update their COP, OR - COP Validation ERROR; THEN: - Select “START-NOW" in the Status column, - Be aware that the results may be skewed and determine the need for procuring equivalent MW capacity elsewhere. |
| Review AS Differences | REVIEW REFERENCE DISPLAYS: Market Participation>Physical Market>SASM Market>AS Responsibility – QSE Market Participation>Monitoring>Event Manager>Events IF: - AS Differences exist; THEN: - Notify the Resource Operator. |
| Bad/Suspect Telemetry | Periodically monitor: IF: - Notified of bad/suspect telemetry; THEN: - Determine if issues will be resolved for next HRUC run, - Discuss with Shift Supervisor if the HRUC should be run or delayed until the issues can be resolved, - Consider requesting Operations Support Engineer to manual over-ride SCADA values (be aware that this could skew the results), - If it is determined to delay HRUC, follow the “HRUC Failure/Timeline Deviation” procedure. |
| E-Tags | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment> HRUC Displays> DSI Displays> DSI Data Processes> DSI DC Tie Schedule Market Operation>Reliability Unit Commitment> HRUC Displays> DSI Displays> External Input Data> MI COP Verify that E-tags are being imported into the MMS: IF: - Individual schedules need to be reviewed; THEN: - Go to the MI COP display and filter ‘ERCOT’ as the QSE name. |
| Verify | REVIEW REFERENCE DISPLAYS: Market Operation>EMS Interface>EMSI Workflow Parameters Market Operation>EMS Interface>EMSI Workflow Messages EMSI has completed successfully within the last hour Market Operation>Reliability Unit Commitment>HRUC Displays>UC Displays>HRUC UC Execution Control Parameters Market Operation>Reliability Unit Commitment>HRUC Displays>NSM Displays>NSM Execution Control Parameters Market Operation>Reliability Unit Commitment>HRUC Displays>DSI Displays>DSI Execution Control Parameters - “Retrieve MF Interface Data” flag set to “Yes”. - “Retrieve MI Interface Data” flag set to “Yes”. - “Retrieve EMS Interface Data” flag set to “Yes”. - “Check Market Status set to “Yes”, - “Use Save case set to “No” |
| DSI | EXECUTE: - The DSI sequence; VERIFY: - For error or warning messages and take necessary action if needed to correct the errors, - The input data is properly transferred. If NOT: - Contact Help Desk immediately to determine the cause and expected time of resolution. |
| Manual Commitment | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP RUC Commitment/Decommitment Summary Market Operation>Reliability Unit Commitment>HRUC Displays>DSI Displays> External Input Data>MF Generator Parameters Market Operations>Reliability Unit Commitment>HRUC Displays>DSI Displays>DSI Data Processes> DSI Operator Manual Commitment Market Operations>Reliability Unit Commitment>HRUC Displays>DSI Displays>External Input Data> MF Generator Parameter All other generation resources should be considered prior to a RMR commitment for capacity purposes: IF: - An RMR unit is needed and is not to be considered in HRUC; THEN: - RUC commit unit before HRUC is executed, - Follow 3.2 Review, Approve and Post HRUC Results step RMR Commitment. IF: - Additional resources are needed to solve for transmission congestion; THEN: - Consult with the Operations Support Engineer and/or the Transmission and Security Desk Operator to determine which resources should be RUC committed, AND - Determine the temporal constraints for each of the units. IF: - The resource start-up time doesn’t allow enough time to re-evaluate the need for its commitment in future HRUC Study Periods; THEN: - Change ‘blank’ to ‘Commit’, - List reason. |
| NOTE | If a RMR unit was RUC committed in DSI Operator Manual Commitment and it is the only change since the DSI was last run the next step is not necessary. |
| Verify | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>DSI Displays>DSI Execution Control Parameters IF: - Manual changes have been made to the HRUC input data; CHANGE: - The appropriate flags are set to prevent the data from being over-written. - “Retrieve MF Interface Data set to No”, - “Retrieve MI Interface Data set to No”, - “Retrieve EMS Interface Data set to No”, OR - “Use Save case set to “Yes” |
| ### Verify HRUC executed at XX: 03 |  |
| 1 | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>HRUC Displays>Workflow>HRUC Workflow Market Operation>Reliability Unit Commitment>HRUC Displays>Workflow>HRUC Workflow Messages Verify execution of the HRUC sequence. |

## 3.2	Review, Approve and Post HRUC Results

Procedure Purpose:  Monitor RUC applications to determine if systems are functioning properly.  Verify results and correct for any warning or error messages.  Review and approve final results for market posting.

| Protocol Reference | 4.4.8 | 5.1 | 5.3(3) | 5.5.1 |
| --- | --- | --- | --- | --- |
|  | 5.5.2 | 5.5.3 | 6.1(2) | 6.4.9.1.2 |
| Guide Reference |  |  |  |  |
| NERC Standard | IRO-001-4 R1 | IRO-008-2 R1, R2, R3 | TOP-001-4 R1, R2 | TOP-002-4 R1, R2, R3, R4, R4.1, R4.4, R5 |

| Version: 1 | Revision: 32 | Effective Date: January 31, 2020 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | See Desktop Guide Common to Multiple Desks Section 2.16 if the savecase function fails when running RUC |
| Monitor | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>HRUC Displays>Workflow>HRUC Workflow Market Operation>Reliability Unit Commitment>HRUC Displays>Workflow>HRUC Workflow Messages - Monitor the HRUC Workflow display to determine when it is complete, ENSURE: - The workflow has completed before the study is approved and published. IF: - The study is approved before it completes, - Incorrect RUC deployments are sent to QSE’s THEN: - Make hotline call to notify QSE’s that deployments for HRUC are invalid, - Notify Director Control Room Operations and/or Designee, - ERCOT may use information from the DAM processes as decision support during the HRUC processes. |
| System Summary | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>UC Displays>Output Display Menu>System Outputs>Summary IF: - All load forecasts seem unreasonable; THEN: - Select the most reasonable forecast, AND - Call the Load Forecasting group for guidance on updating the weather or load forecast - Notify by e-mail the following distribution lists of the issue: - Load Forecasting & Analysis - 1 ERCOT Shift Supervisors |
| Excess Generation | During periods of low load and excess generation: PERIODICALLY REVIEW: - Splunk Dashboard Viewer under the MOS_DEV folder: - “Last Approved HRUC Capacity” which is based on the last ran HRUC solution VERIFY: - TOTAL_LOAD is less than SS_LASL, IF: - Load forecast is reasonable AND the decision needs to be made in the near future, THEN: - Decommit generation from the HRUC next study, - Priority should be on WGR’s or Resources that resolve congestion; IF: - The decision needs to be made immediately, THEN: - Issue an electronic Dispatch Instruction confirmation - (priority should be given to WGRs and Resources that resolve congestion - Choose “DECOMMIT” as the Instruction Type from Resource tab - Enter “ERCOT requested RUC decommit/capacity surplus” in Other Information. When issuing a VDI or confirmation, ensure the use of three-part communication: - Issue the Operating Instruction - Receive a correct repeat back - Give an acknowledgement |
| A/S Infeasibility | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP Undeliverable Ancillary Service Capacity Summary Market Participation>Physical Market>SASM Market>AS Infeasibility Market Participation>Physical Market>SASM Market>AS Replacement IF: - Undeliverable Ancillary Service are indicated; THEN: - Determine if the infeasibility is valid IF: - Valid; THEN: - Notify the affected QSE for the following information - the amount of A/S that must be reduced, and - the start and stop times of the reduction. - The QSE can substitute or ERCOT can open a SASM IF: - The QSE elects to substitute; THEN: - Determine the feasibility of the substitution. - If deemed infeasible, a SASM can be opened - Notify the Resource Operator of possible infeasibility issue. |
| A/S Insufficiency from SASM | If a SASM market has been previously run, the following display will indicate if additional A/S Insufficiencies exist: REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP Decision Support for Ancillary Service Deployment IF: - A/S Insufficiency; THEN - If deemed necessary, RUC commit the necessary Resources that are qualified to provide the service that is deficient while honoring temporal constraints, - Refer to Desktop Guide RUC Section 2.18. |
| Undeliverable A/S Capacity | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP Undeliverable Ancillary Service Capacity Summary IF: - Undeliverable A/S due to transmission constraints; THEN: - Notify the Resource Operator. |
| STNET Study | Each hour run a STNET study for four hours out (example it is 0100, run study for 0500) to review voltage violations. IF: - Voltage contingencies or unsolved contingencies exist; THEN: - Check “Voltage Tracking Issues spreadsheet” on SharePoint to ensure the contingency is not listed. - If not listed, convey the voltage violations to the Transmission and Security Operator - Create a savecase, use naming convention “SC_RUC(HE)_(DATE) - Make at least one detailed log entry per shift that the studies are being executed. If any new voltage violations are identified that do not have a solution, log the information and notify the Transmission and Security Operator of the new violation(s). |
| Violated Constraints | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP Binding Constraint Summary Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP Constraint Summary REVIEW: - Violated constraints. If needed, notify Operations Support Engineer to determine the validity; IF: - Invalid, no further action is required; IF: - Valid; AND - Related to a phase shifter tap settings, THEN: - Notify Operations Support Engineer to determine and determine if adjusting a Phase Shifter would reduce the flow, - Create Suggestion Plan for Constraint, - Manually RUC commit resources as needed Refer to Desktop Guide RUC Section 2.14. |
| HRUC Committed Units | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>DSI Displays>External Input Data>MF Generator Parameter IF: - HRUC recommends the commitment of any unit; THEN: - Determine the validity, - Determine the temporal constraints for each of the units recommendation. - Refer to Desktop Guide RUC Section 2.23. IF: - Temporal constraint exceedances at the same facility do not conflict, - The resource start-up time allows enough time to re-evaluate the need for its commitment in future HRUC Study Periods, and - There is no reliability reason requiring the resource commitment decision to be made immediately; THEN: - De-select the resource prior to approving the HRUC study by changing ‘Commit’ to ‘blank’ and list reason, IF: - Temporal constraint exceedances at the same facility, - There is a reliability reason requiring the resource commitment decision to be made immediately; - Resources returning from outages - Congestion or Capacity deficiencies that are creating HRUC performance issues THEN: - Log the reason for not de-selecting the resource. NOTE: A reason must be entered for commit, decommit, and uncommitting, otherwise a message window will pop up in DSP approval process. Examples below: - Evaluate later (should be used when waiting until the last possible hour to commit) - Short start (should be used for units that can start within 1 hour) - Voltage support - Valley import - Capacity - Constraint name (SLWSCRL5) * Do not use special characters When issuing a confirmation, ensure the use of three-part communication: - Issue the Operating Instruction - Receive a correct repeat back - Give an acknowledgement |
| EMR Resources | Resources with “EMR” Resource status can only be RUC committed during Emergency conditions. |
| RMR Resources | QSEs will show a COP status of OFF when Resources are available. RMR Resources will only be dispatched from the Hourly Reliability Unit Commitment (HRUC). |
| RMR Commitment | WHEN: - HRUC recommends a RMR unit, AND - A capacity reserve shortage is projected and no market Resources are available to meet the projected system demand, and there is a risk of an EEA event; THEN: - Determine if an RMR Resource will need to be considered in HRUC Study Period; ISSUE: - Watch for projected reserve capacity shortage with no market solution; THEN: - Ensure COP status is “OFF” and the resource start-up time allows enough time to procure the RMR for the hours showing to be deficient with risk of an EEA event; SELECT: - Commit Resource before HRUC is approved - Commit Resource, - List reason (RMR for Capacity). Call QSE with any modification to the Delivery Plan as a result of a commitment. |
| Hotline | Q#77 - Typical Hotline Script for Watch for projected reserve capacity shortage Notify Transmission Operator to make Hotline call to TOs. |
| Post | Typical MIS posting: ERCOT issued a Watch for a projected reserve capacity shortage with no market solution available. HRUC recommended RMR Resources have been committed. |
| Cancel | WHEN: - Committed RMR Resources are off-line THEN: - Making hotline call to QSEs - Cancelling MIS posting - Notify Transmission Operator to make hotline call to TOs. Q#78 - Typical Hotline Script for canceling Watch for projected reserve capacity shortage |
| Manual Commitment | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP RUC Commitment/Decommitment Summary Market Operation>Reliability Unit Commitment>HRUC Displays>DSI Displays> External Input Data>MF Generator Parameters IF: - Additional resources are needed to solve for transmission issues (such as for voltage support) and were not picked up in the HRUC run; THEN: - RUC commit unit before HRUC is approved - Change ‘blank’ to ‘Commit’, - List reason RUC commit for (constraint name, valley import or voltage support), a message window will pop up in DSP approval process if no reason is provided. - Give courtesy call to QSE when commitments are made |
| Manual Commitment to bring a Unit of a Combined Cycle On-line | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays>DSP Combined Cycle Plant Suggestion Plan IF: - Additional resources are needed to solve for transmission issues and were not picked up in the HRUC run; THEN: - RUC commit higher configuration of a Combined Cycle before HRUC is approved - Determine the temporal constraints for the higher configuration. - Change ‘blank’ to ‘Commit’, - List reason RUC commit for (constraint name, valley import or voltage support), a message window will pop up in DSP approval process if no reason is provided. - Give courtesy call to QSE when commitments are made Refer to Desktop Guide Reliability Unit Commitment Desk 2.20 |
| NOTE | - Resources cannot be decommitted for just a portion of a DAM-Committed Interval, which is a one-hour interval. - ERCOT may only decommit a Resource to resolve transmission constraints that are otherwise unsolvable or to maintain the reliability of the ERCOT System. Qualifying Facilities (QFs) may be decommitted only after all other types of Resources have been assessed for decommitment. - If ERCOT communicates HRUC commitments and decommitments verbally to a QSE, then the same Resource attributes communicated programmatically must be communicated when ERCOT gives a verbal Resource commitment or decommitment. - QSE’s shall acknowledge the notice of commit or decommit by updating their COP. |
| HRUC Decommitted Resources | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP RUC Commitment/Decommitment Summary IF: - If HRUC recommends decommitments; Determine if: - Outage related, - Possible Network Model error/ Normal Breaker status variances, - COP error for Combine Cycle configurations / JOU, - Qualifying Facilities should be de-committed ONLY as a last resort, THEN: - If this is a true decommitment: - Confirm Decommitment - List reason (most likely reason is ‘transmission outage’), a message window will pop up in DSP approval process if no reason is provided - If Decommitment is error related: - No action is required |
| Canceling RUC Commitments | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>DSI Displays>DSI Data Processes>DSI Operator Manual Commitment IF: - A Resource is RUC committed that needs to be canceled; - Only cancel RUC commits if the ERCOT Operator Resource commitment was unintended. THEN: - Issue electronic Dispatch Instruction to cancel the RUC instruction - Choose “CANCEL RUC COMMIT” as the Instruction Type - Enter “unintended commitment” in other information When issuing a VDI or confirmation, ensure the use of three-part communication: - Issue the Operating Instruction - Receive a correct repeat back - Give an acknowledgement - Remove unintended RUC commit from DSI Operator Commitment by changing (AUTO) to (OFF) for the hours in question. |
| Post | Notice Type: Operational Information Notice Priority: Low Audience: Public Typical MIS posting: Cancelled RUC commitment at timestamp [Date & Time] for [resource] for [Date & Time] due to unintended commitment. |
| ### VSAT and RUC perform AC Analysis |  |
| NOTE | IF: - RUC cannot complete the process; THEN: - Notify the Transmission & Security Operator and additional personnel as required. |
| Validate | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>UC Displays>Output Display Menu>System Outputs>Summary VERIFY: - Input data - Updated Time - Results are reasonable |
| Approval | HRUC must be approved by XX:50 REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP Execution Control Parameters IF: - The HRUC results are reasonable and after all necessary modifications have been made; THEN: - Sort the RUC Commitment column before approving so it shows commitments at the top of the screen that currently may be lower in the table but not shown in the window; - Approve the results (all RUC commitment, operator manual commitment/decommit/blank out must have a reason, otherwise a message window will pop up), OR IF: - The results are unacceptable; THEN: - Click on Disapprove button, AND - Follow the Manage HRUC Timeline Failure in the next section. IF: - Disapprove button was selected in error; THEN: - Contact Helpdesk to open ticket for EMMS Production Support to correct it. |
| After Approval | AFTER: - Approval button is pushed; THEN: - Double check display Market Participation>Physical Market>Market Results>HRUC> HRUC Results, - Make sure the records in this display matches data in display Market Operation>Reliability Unit Commitment>HRUC Displays >DSP Displays>DSP RUC Commitment/Decommitment Summary. IF: - Displays are different, the RUC commitments thought to be blanked out were sent out; THEN: - Notify the Helpdesk to call the On-Call EMMS Production support, and - Issue electronic Dispatch Instructions to cancel RUC instructions When issuing a VDI or confirmation, ensure the use of three-part communication: - Issue the Operating Instruction - Receive a correct repeat back - Give an acknowledgement |
| Log | Log actions taken. |

## 3.3	HRUC Failure/Timeline Deviation

Procedure Purpose:  To address situations in which the HRUC process has failed.  Failures can be identified by software failure, results not approved in a timely manner or certain conditions.

| Protocol Reference | 6.5.9.1(2) | 6.5.9.3.3(2)(e) |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 16 | Effective Date: January 31, 2020 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Logs | Document decisions made and actions taken within this procedure in the Operator Logs. |
| ### HRUC Failure/Timeline Deviation |  |
| Failure | IF: - HRUC solved with invalid solution, - Time does not allow for full review of results, OR - HRUC software fails without expectation of timely repair; THEN: - Notify Help Desk and Control Room Staff, - Issue a Watch by making a Hotline call to QSEs - Make posting on MIS Public. - Notify Transmission Operator to make Hotline call to TOs Q#79 - Typical Hotline Script for Watch for HRUC failure/timeline deviation WHEN: - HRUC is operating properly; THEN: - Making hotline call to QSEs - Cancelling MIS posting - Notify Transmission Operator to make hotline call to TOs. Q#80 - Typical Hotline Script to Cancel Watch for HRUC failure/timeline deviation |
| Create Save Case | IF: - HRUC is aborted or shut down; THEN: - Go to display System Administration > Savecase Management. - Choose File Type as HRUC. - Fill in File Name (no spaces allowed) - Fill in Description. - Push Create Button. - The message will show up in the Text field. - Refresh the display (F5), make sure the savecase name will show up in the File Name Field. Also refer to Desktop Guide Common to Multiple Desks Section 2.16, if needed. - Contact Helpdesk to notify EMMS Production Support that HRUC was aborted or shut down and a Savecase was created. |
| NOTE | IF: - HRUC is having trouble solving in the required timeline due to transmission/capacity violations in the study; THEN: - Have Operations Support Engineer check validity of violation AND if correct, - Consider committing Resource(s) sooner instead of waiting to evaluate later. |
| Commit/ De-Commit Resources By VDI | IF Needed: - RUC Commit/De-Commit Resources by issuing electronic Dispatch Instructions for the following: - Choose COMMIT or DECOMMIT as the Instruction Type from the RES Level, - Enter reason RUC commit for (capacity, capacity surplus or contingency name) in “other information” When issuing a VDI or confirmation, ensure the use of three-part communication: - Issue the Operating Instruction - Receive a correct repeat back - Give an acknowledgement |

## 3.7	Manual Dispatch of Resources

Procedure Purpose:  Manually Dispatch Resources as necessary to ensure system security when HRUC cannot be used.

| Protocol Reference | 5.1(12) | 5.5.2 | 5.5.3(3) | 6.5.9 (3) |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | EOP-011-1 R1, R1.1, R1.2, R1.2.4 |  |  |  |

| Version: 1 | Revision: 16 | Effective Date: January 31, 2020 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - ERCOT shall honor all Resource operating parameters in Dispatch Instruction / Operating Instructions under normal conditions and Emergency Condition. During Emergency Conditions, ERCOT may verbally request QSE’s to operate its Resources outside normal operating parameters. If such request is received by a QSE, the QSE shall discuss the request with ERCOT in good faith and may choose to comply with the request - A QSE can self-commit by setting the telemetered Resource Status to ONOPTOUT for the first SCED run that the Resource is On-Line and available for SCED dispatch during the first hour of a contiguous block of RUC-Committed Hours - If a QSE-committed Resource experiences a Forced Outage or Startup Loading Failure in an hour for which another Resource under the control of the same QSE is committed by a RUC instruction, the QSE may opt out of the RUC instruction by self-committing the Resource as described above - If a Resource is RUC committed from one operating day to the next operating day, new RUC commits will need to be sent for the new day. |
| ### Manual RUC Commit of a Resource |  |
| 1 | IF: - It has been determined that a Resource is needed in real-time for a transmission condition or critical inertia level after the close of the Adjustment Period (Typically will be short start, Quick Start resources available or resources scheduled to come off within the operating hour); THEN: - Notify QSE an electronic Dispatch Instruction will be issued - Verify lead time with QSE - Issue an electronic Dispatch Instruction to RUC commit the Resource, - Choose “COMMIT” as the Instruction Type from Resource level - Enter reason, such as RUC commit for contingency name, capacity or critical inertia level in “other information” - Confirm with QSE that the electronic Dispatch Instruction was received - The same Resource attributes communicated programmatically must be communicated when giving a VDI. When issuing a VDI or confirmation, ensure the use of three-part communication: - Issue the Operating Instruction - Receive a correct repeat back - Give an acknowledgement See Desktop Guide Common to Multiple Desks Section 2.3 for additional information to submit a correct electronic Dispatch Instruction. |
| LOG | Log all actions. |
| ### Manual Dispatch of an OFFQS Resource |  |
| 1 | IF: - It has been determined that a OFFQS Resource is needed in real-time for a transmission condition; THEN: - Notify QSE an electronic Dispatch Instruction will be issued - Verify LSL when resource is generating to the grid - Issue an electronic Dispatch Instruction to RUC commit the Resource, - Verbal Dispatch Instructions [RUC Desk] - Notification Date/Time: This is the time the QSE was first notified. - Start Date/Interval(IE): This is the hour ending start time of the VDI - End Date/Interval(IE): This is the hour ending end time of the VDI (if known) - Resource Name: Name of OFFQS Resource being committed - Instruction Type: Choose “COMMIT” - Reason: Voltage Stability or critical inertia level - Enter reason, such as RUC commit for contingency name in “other information” - Confirm with QSE that the electronic Dispatch Instruction was received - The same Resource attributes communicated programmatically must be communicated when giving a VDI. When issuing a VDI or confirmation, ensure the use of three-part communication: - Issue the Operating Instruction - Receive a correct repeat back - Give an acknowledgement See Desktop Guide Common to Multiple Desks Section 2.3 for additional information to submit a correct electronic Dispatch Instruction. |
| LOG | Log all actions. |
| ### Manual Dispatch to take a Unit Off-Line |  |
| 1 | IF: - A manual dispatch instruction / Operating Instruction will result in the unit being dispatched off-line (i.e., less than the minimum operating limit for that Resource); THEN: - Issue an electronic Dispatch Instruction taking the Resource to zero until it can be released, - Choose “DECOMMIT” as the Instruction Type from Resource level - Enter RUC Decommit for contingency name in “other information” When issuing a VDI or confirmation, ensure the use of three-part communication: - Issue the Operating Instruction - Receive a correct repeat back - Give an acknowledgement - Ensure QSE updates telemetry. |
| ### Manual Dispatch to take a Unit of a Combined Cycle Off-line |  |
| 1 | IF: - System conditions require one unit of a Combined Cycle Plant to be manually dispatched off-line; THEN: - Contact the QSE and request which unit the QSE would like to shutdown, - Request the planned/current CC configuration and then the CC configuration that the Resource will need to be operating, - Issue an electronic Dispatch Instruction confirmation to “COMMIT” the QSE to their CC configuration. All data must be entered but pay attention to the following details. - Choose the proper QSE from the Participant name - Select the CC configuration that you are instructing the Resource to operate in from the Resource name - Choose “COMMIT” as the Instruction Type from Resource level - Enter RUC decommit for contingency name in “other information” When issuing a VDI or confirmation, ensure the use of three-part communication: - Issue the Operating Instruction - Receive a correct repeat back - Give an acknowledgement - Log the above information. |
| ### Manual Dispatch to bring a Unit of a Combined Cycle On-line |  |
| 1 | IF: - System conditions require a unit of a Combined Cycle Plant to be manually dispatched on-line; THEN: - Contact the QSE and notify which unit will be committed, - Request the planned/current CC configuration and then the CC configuration that the Resource will need to be operating, - Determine the temporal constraints for the CC configuration. - Issue an electronic Dispatch Instruction to “COMMIT” the QSE to their CC configuration. All data must be entered but pay attention to the following details. - Choose the proper QSE from the Participant name - Select the CC configuration that you are instructing the Resource to operate in from the Resource name - Choose “COMMIT” as the Instruction Type from Resource level - Enter RUC commit for contingency name or critical inertia level in “other information” When issuing a VDI or confirmation, ensure the use of three-part communication: - Issue the Operating Instruction - Receive a correct repeat back - Give an acknowledgement - Log the above information. |
| ### Canceling RUC Commitments |  |
| 1 | IF: - A Resource is RUC committed that needs to be canceled; - Only cancel RUC commits if the ERCOT Operator Resource commitment was unintended. THEN: - Issue an electronic Dispatch Instruction to cancel the RUC instruction - Choose “CANCEL RUC COMMIT” as the Instruction Type - Enter “unintended RUC commitment” in other information |
| Post | Notice Type: Operational Information Notice Priority: Low Audience: Public Typical MIS posting: Cancelled RUC commitment at timestamp [Date & Time] for [resource] for [Date & Time] due to unintended commitment. |
| LOG | Log all actions. |

## 4.2	Tasks prior to Execution of DRUC

Procedure Purpose:  To make manual corrections for bad/suspect telemetry, load forecast modifications, or to commit Resources prior to running the RUC process.

| Protocol Reference | 5.1 | 5.3(1) | 5.5.1 |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | TOP-002-4 R4, R4.2, R4.3 |  |  |  |

| Version: 1 | Revision: 8 | Effective Date: January 31, 2020 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### By 13:00 each day, perform the following |  |
| COP | REVIEW REFERENCE DISPLAYS: Market Participation>Physical Market>Market Operator Data> Missing COP Check>Market Participation>Monitoring>Event Manager>Events VERIFY: - “Missing COP Check” has automatically notified the QSEs of missing COPs; SELECT: - “START-NOW" in the Status column if not already completed by Market Operations. |
| Load Forecast | Review the Day Ahead Load Forecast in the EMS: IF: - Adjustments need to be made in the EMS; THEN: - Adjust using the following: (Refer to Desktop Guide RUC Section 2.17) Reference Displays: - Load Forecast - Similar Day Function - Load Forecast Scaling functions - Perform load scaling or - Perform peak scaling or - Perform factor scaling - Manually override forecast value(s) - Notify the Shift Supervisor if an invalid Load Forecast exists for the study period of DRUC. |
| Outage Notes/Off-Line Studies | IF: - Resources are needed for identified Voltage issues; THEN: - Once COPs have been updated, identify the appropriate resources that can be utilized if needed. |
| Review | REVIEW REFERENCE DISPLAY: Market Operation>EMS Interface>EMSI Workflow Parameters IF: - The EMSI Workflow Controller (Time Stamped – runs XX:50 every hour) function (data transfer between EMS and MMS) and Load Forecast are NOT running (should be continuous); THEN: - Notify Help Desk and Control Room Staff. |
| ### By 13:30 each day, perform the following |  |
| NOTE | - The DRUC process may not be used to buy Ancillary Service unless the Ancillary Service Offers submitted in the DAM are insufficient to meet the requirements of the Ancillary Service Plan. - By default, Resources without an entry in COP are considered to have a Resource Status of OUT and are unavailable in RUC Procedure. |
| WRUC | IF: - Prior to 1330, ERCOT may issue a WRUC instruction to a QSE that a Resource is required to be On-Line for all or part of a future Operating Day; THEN: - The QSE may self-commit the Resource for the WRUC instructed hours by updating the Resource’s COP to reflect the appropriate On-Line Status for the WRUC hours prior to the DRUC process execution, OR - The Resource will be committed as part of the DRUC process for all WRUC-instructed hours not DAM-committed or QSE self- committed. |
| ### By 14:00 each day, perform the following |  |
| NOTE | As time permits, contact QSEs that have NOT submitted a COP for the DRUC study period. |
| Long Lead Times | Identify resources that have a lead-time greater than the DRUC timeline, WRUC results should be utilized for identifying resources with long lead-times. IF: - Resources are identified; THEN: - RUC Commit the necessary resources as needed. |
| ### By 14:25 each day, perform the following |  |
| NOTE | If the DAM did not complete by 1330, then DRUC will be delayed. MPs need an hour between the completion of DAM and the opening of DRUC to update COPs. |
| Verify | Verify that the DAM has completed. IF: - DAM will not complete until after 1430; THEN: - Follow the “Manage DAM/DRUC Timeline Deviation/Failure” procedure. |
| Setting parameters for ONLINE | REVIEW REFERENCE DISPLAY: System Administration>Data Management Verify that “Connect to Schema” is set to “ONLINE”. |
| Verify | REVIEW REFERENCE DISPLAYS: Market Operation>EMS Interface>EMSI Workflow Parameters Market Operation>EMS Interface>EMSI Workflow Messages EMSI has completed successfully within the last hour Market Operation>Reliability Unit Commitment>DRUC Displays>UC Displays>DRUC UC Execution Control Parameters Market Operation>Reliability Unit Commitment>DRUC Displays>NSM Displays>NSM Execution Control Parameters Market Operation>Reliability Unit Commitment>DRUC Displays>DSI Displays>DSI Execution Control Parameters - “Retrieve MF Interface Data” flag set to “Yes”. - “Retrieve MI Interface Data” flag set to “Yes”. - “Retrieve EMS Interface Data” flag set to “Yes”. - “Check Market Status set to “Yes”, - “Use Save case set to “No” |
| ### At 14:30 each day, perform the following |  |
| DSI | EXECUTE: - The DSI sequence VERIFY: - For error or warning messages and take necessary action if needed to correct the errors, - The input data is properly transferred. If NOT: - Contact EMMS production support personnel immediately to determine the cause and expected time of resolution. |
| Verify | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>DRUC Displays>DSI Displays>External Input Data>MI DAM AS Insufficiency This display will give the Operator an indication if any A/S insufficiencies have occurred in DAM. If insufficiencies exist, the Operator can start looking at resources that can be committed to resolve the insufficiency in DSP. |
| E-Tags | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment> DRUC Displays> DSI Displays> DSI Data Processes> DSI DC Tie Schedule Market Operation>Reliability Unit Commitment> DRUC Displays> DSI Displays> External Input Data> MI COP Verify that E-tags are being imported into the MMS. IF: - Individual schedules need to be reviewed; THEN: - Go to the MI COP display and filter ‘ERCOT’ as the QSE name |
| Verify | - Identify and correct Bad/Suspect Telemetry - Modify Input for Block Load Transfer (BLT) movement - Modify Input for Verbal Dispatch Instructions Refer to Desktop Guide RUC Section 2.3 |
| Manual Commitment | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment> DRUC Displays> DSI Displays>DSI Data Processes>DSI Operator Manual Commitment IF: - Additional resources are needed to solve for voltage issues; THEN: - Consult with the Operations Support Engineer and/or the Transmission and Security Desk Operator to determine which resources should be RUC committed, AND - Determine the temporal constraints for each of the units. IF: - The resource start-up time doesn’t allow enough time to re-evaluate the need for its commitment in future HRUC Study Periods; THEN: - Filter for the unit - Change ‘Auto’ to ‘On’, - List reason. |
| Set Flags | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>DRUC Displays>DSI Displays>DSI Execution Control Parameters IF: - Manual changes have been made to the DRUC input data; CHANGE: - The appropriate flags are set to prevent the data from being over-written. - “Retrieve MF Interface Data set to No”, - “Retrieve MI Interface Data set to No”, - “Retrieve EMS Interface Data set to No”, OR - “Use Save case set to “Yes” |
| Execute | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>DRUC Displays>Workflow>DRUC Workflow Market Operation>Reliability Unit Commitment>DRUC Displays>Workflow>DRUC Workflow Messages Execute the entire DRUC sequence (Run All). |
| STNET Studies | Notify: - Operations Support Engineer to run NSA for each hour of the next operating Day. |

## 4.3	Review, Approve and Post DRUC Results

Procedure Purpose:  To work collaboratively with Market Operations Support Personnel in reviewing, and if necessary, modifying DRUC data, to approve and post the final DRUC results.

| Protocol Reference | 4.4.8 | 5.1 (9) | 5.3(3) | 5.5.1(9) |
| --- | --- | --- | --- | --- |
|  | 5.5.2 | 5.5.3(2) | 6.4.9.1(3) |  |
| Guide Reference |  |  |  |  |
| NERC Standard | IRO-008-2 R1, R2, R3 | TOP-002-4 R1, R2, R3, R4, R4.1, , R4.4, R5 |  |  |

| Version: 1 | Revision: 31 | Effective Date: January 31, 2020 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | See Desktop Guide Common to Multiple Desks Section 2.16 if the savecase function fails when running RUC |
| Monitor | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>DRUC Displays>Workflow>DRUC Workflow Market Operation>Reliability Unit Commitment>DRUC Displays>Workflow>DRUC Workflow Messages |
| Review | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>DRUC Displays>UC Displays>Output Display Menu>System Outputs>Summary When DRUC has completed. If necessary, work with Market Operations and Operations Support Engineer to review the results. - Monitor the DRUC Workflow display to determine when it is complete, ENSURE: - The workflow has completed before the study is approved and published, IF: - The study is approved before it completes, - Incorrect RUC deployments are sent to QSE’s THEN: - Make hotline call to notify QSE’s that deployments for DRUC are invalid, - Notify the Director Control Room Operations and/or Designee immediately, - Abnormal system condition in the summary display after IUC (Initial Unit Commitment component of MMS) and NCUC (Network Constrained Unit Commitment component of MMS). - For Under Generation, prepare for following “DRUC Committed Units” section of this procedure - For Over generation, check for COP or Load Forecast errors - For System Lambda greater than $10, check intermediate NSM (Network Security Manager Component of MMS) results for constraint violation. For abnormal constraints in the NSM outputs and abnormal commitments in IUC and NCUC outputs, refer to Desktop Guide RUC Section 2.6, step 5. |
| NOTE | - Resources with NO Current Operating Plan (COP) entry are considered as “Unavailable” in RUC. - Resources with “EMR” Resource status can only be RUC committed during Emergency conditions. |
| System Summary | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>DRUC Displays>UC Displays>Output Display Menu>System Outputs>Summary Market Operation>Reliability Unit Commitment>DRUC Displays>UC Displays>Output Display Menu>System Outputs>Summary Line Flow DETERMINE IF: - The load forecast is reasonable for each hour, - Any under/over generation; THEN: - Be aware of these when running HRUC. |
| A/S Insufficiency from DAM | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP Decision Support for Ancillary Service Deployment Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP RUC Commitment/Decommitment Summary IF: - Notified from Market Operations of A/S Insufficiency from DAM; THEN - Issue a Watch to QSEs - Notify Transmission Operator to make Hotline call to TOs - Verify Market Operations has posted message on MIS Public - Refer to Desktop Guide RUC Section 2.1. Q#85 - Typical Hotline Script for Watch for A/S insufficiency in DAM, procuring in DRUC WHEN: - A/S offers are committed in DRUC; THEN: - Making hotline call to QSEs - Cancelling MIS posting - Notify Transmission Operator to make hotline call to TOs. Q#86 - Typical Hotline Script Cancel Watch for A/S insufficiency in DAM |
| Undeliverable A/S Capacity | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP Undeliverable Ancillary Service Capacity Summary IF: - Undeliverable A/S due to Transmission Constraints and Reliability issues exist; THEN: - Notify the QSEs and provide the following information: - The amount of its Resource capacity that does not qualify to provide A/S - The projected hours - Notify the Resource Desk Operator. |
| Violated Constraints | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP Binding Constraint Summary Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP Constraint Summary REVIEW: - Violated constraints. If needed, notify Operations Support Engineer to determine the validity; IF: - Invalid, no further action is required, - Valid; THEN - Locate the constraint on the DSP Constraint Summary display, - Create a Suggestion Plan for the identified violated constraint - Review the temporal constraints of the suggested resources - If resource start-up time allows enough time to re-evaluate the need for its commitment, be aware of these conditions when running HRUC, - RUC commit resources as needed prior to DRUC approval if needed due to temporal constraints. |
| NOTE | RUC Operators can decide to postpone a commitment if the startup time is well into the future. It will be left up to future HRUC solutions to actually commit the unit. |
| DRUC Committed Units | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>DRUC Displays>DSI Displays>External Input Data>MF Generator Parameter Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays>DSP RUC Commitment/Decommitment Summary IF: - DRUC recommends the commitment of any unit; THEN - Determine the validity, - Determine the temporal constraints for each of the units, IF: - The resource start-up time allows enough time to re-evaluate the need for its commitment in future HRUC Study Period, AND - There is no reliability reason requiring the resource commitment decision to be made immediately; THEN: - De-select the resource prior to approving the DRUC study by changing ‘Commit’ to ‘blank’ and list reason. IF: - There is reliability reason requiring the resource commitment decision to be made immediately; - Resources with long start-up times - Resources returning from outages - Congestion or Capacity deficiencies that may create HRUC performance issues THEN: - Log the reason for not de-selecting the resource. NOTE: A reason must be entered for commit, decommit, uncommitting, examples below: - Evaluate later (should be used when waiting until the last possible hour to commit) - Short start (should be used for units that can start within 1 hour) - Voltage support - Valley import - Constraint name (SLWSCRL5) * Do not use special characters When issuing a confirmation, ensure the use of three-part communication: - Issue the Operating Instruction - Receive a correct repeat back - Give an acknowledgement |
| Excess Generation | During periods of low load and excess generation: PERIODICALLY REVIEW: - Splunk Dashboard Viewer under the MOS_DEV folder: - “6 DRUC Capacity” which is based on the last ran DRUC VERIFY: - TOTAL_LOAD is less than SS_LASL, IF: - Load forecast is reasonable AND the decision can be made in the future, THEN: - Issue OCN for Excess Reserve Capacity - Notify Transmission Operator to make Hotline call to TOs - Post message on MIS Public Q#87 - Typical Hotline Script for OCN for Excess Capacity Typical MIS Posting: ERCOT issued an OCN due to a projected excess reserve capacity for [HE XX – HE XX]. WHEN: - Projected excess reserve capacity; THEN: - Making hotline call to QSEs - Cancelling MIS posting - Notify Transmission Operator to make hotline call to TOs. Q#88 - Typical Hotline Script to Cancel OCN for Excess Capacity |
| DRUC Committed For Capacity Shortage | IF: - DRUC recommends Resource(s) for capacity; THEN - Determine if start-up time allows enough time to re-evaluate, and - De-select the Resource(s) prior to approving the DRUC, After DRUC is approved: - Issue an OCN for projected reserve capacity shortage - Notify Transmission Operator to make Hotline call to TOs - Post message on MIS Public Q#89 - Typical Hotline Script for OCN for commiting capacity in DRUC Typical MIS Posting: ERCOT issued an OCN due to a projected capacity shortage for [HE XX – HE XX]. WHEN: - Projected reserve capacity shortage no longer exist; THEN: - Making hotline call to QSEs - Cancel MIS posting - Notify Transmission Operator to make hotline call to TOs. Q#90 - Typical Hotline Script cancellation for OCN for commiting capacity in DRUC |
| Manual Commitment | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP RUC Commitment/Decommitment Summary IF: - Additional resources are needed to solve for transmission issues (such as voltage support) and were not picked up in the DRUC run, - The resource start-up time doesn’t allow enough time to re-evaluate the need for its commitment in the HRUC Study Period, OR - A Resource was given a WRUC instruction and chose not to self-commit for all hours needed; THEN: - Change ‘blank’ to ‘Commit’ - List reason (capacity, constraint name or voltage issue). - Give courtesy call to QSE when commitments are made |
| NOTE | Resources cannot be decommitted for just a portion of a DAM-Committed Interval, which is a one-hour interval. ERCOT may only decommit a Resource to resolve transmission constraints that otherwise cannot be resolved. Qualifying Facilities (QFs) may be decommitted only after all other types of Resources have been assessed for decommitment. |
| DRUC Decommitted Resources | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP RUC Commitment/Decommitment Summary IF: - If RUC recommends commitments/decommitments; DETERMINE IF: - Outage related’ - Possible Network Model error’ - COP error for Combine Cycle configurations / JOU, - Qualifying Facilities should be de-committed ONLY as a last resort; THEN: - If this is a true decommitment: - Confirm Decommitment - List reason (most likely reason is ‘transmission outage’) - If Decommitment is error related: - No action is required |
| NOTE | Once you have completed your review of DRUC, consult with Market Operations to ensure they see no issues before approving. |
| Validate | REVIEW REFERENCE DISPLAY: Market Participation>Physical Market>SASM Market>AS Responsibility - QSE Market Operation>Reliability Unit Commitment>DRUC Displays>UC Displays>Output Display Menu>System Outputs>Summary VERIFY: - Input data - Updated Time - Results are reasonable |
| Approval | DRUC must be approved by 1600 REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP Execution Control Parameters IF: - The DRUC results are reasonable after all necessary modifications have been made; THEN: - Sort the RUC Commitment column before approving so it shows commitments at the top of the screen that currently may be lower in the table but not shown in the window; - Approve the results, OR IF: - The results are unacceptable; THEN: - Click on Disapprove button - Follow the Manage DRUC Failure/Timeline Deviation procedure. IF: - Disapprove button was selected in error; THEN: - Contact Helpdesk to open ticket for EMMS Production Support to correct it. |
| NOTE | If the Operator disapproves the results, the results will be saved in the database for future analysis and will not be published to the MPs. |
| After Approval | AFTER: - Approval button is pushed; THEN: - Double check display Market Participation>Physical Market>Market Results>DRUC> DRUC Results, - Make sure the records in this display matches data in display Market Operation>Reliability Unit Commitment>DRUC Displays >DSP Displays>DSP RUC Commitment/Decommitment Summary. IF: - Displays are different, the RUC commitments thought to be blanked out were sent out; THEN: - Notify the Helpdesk to call the On-Call EMMS Production support, and - Issue VDIs to cancel RUC instructions When issuing a VDI or confirmation, ensure the use of three-part communication: - Issue the Operating Instruction - Receive a correct repeat back - Give an acknowledgement |
| Canceling RUC Commitments | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>DSI Displays>DSI Data Processes>DSI Operator Manual Commitment IF: - A Resource is RUC committed and needs to be canceled; - Only cancel RUC commits if the ERCOT Operator Resource commitment was unintended. THEN: - Issue an electronic Dispatch Instruction confirmation to cancel the RUC instruction - Choose “CANCEL RUC COMMIT” as the Instruction Type - Enter “unintended commitment” in other information When issuing a VDI or confirmation, ensure the use of three-part communication: - Issue the Operating Instruction - Receive a correct repeat back - Give an acknowledgement - Remove unintended RUC commit from DSI Operator Commitment by changing (AUTO) to (OFF) for the hours in question. |

## 5.2	Review WRUC Results

Procedure Purpose:  To identify commitments with a long lead time and develop a list of violated/binding constraints that have a high-probability of being binding in SCED or DAM.

| Protocol Reference | 5.1 |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 12 | Effective Date: January 31, 2020 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - WRUC does not send commitments or electronic Dispatch Instructions to QSEs. - WRUC does not retrieve any QSE-submitted Three-Part Supply Offers. - WRUC relies exclusively on the QSE-submitted COPs. |
| Monitor | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>WRUC Displays>Workflow>WRUC Workflow Market Operation>Reliability Unit Commitment>WRUC Displays>Workflow>WRUC Workflow Messages |
| Violated Constraints | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>WRUC Displays>DSP Displays> DSP Binding Constraint Summary Market Operation>Reliability Unit Commitment>WRUC Displays>DSP Displays> DSP Constraint Summary REVIEW: - Violated constraints; IF: - WRUC identifies a Resource with a lead-time greater than the DRUC time-line and it is confirmed in the Outage Notes or a gap study; THEN: - Instruct the QSE that their Resource needs to be On-line by [date] at [time] and they have the option of: - Self-committing the Resource by updating the COP before the DRUC process execution, or - ERCOT will commit the Resource in the DRUC process. |
| Electronic Dispatch Instruction | When instructing a QSE their resource needs to be On-line by [date] at [time]: - Commit Resources by issuing electronic Dispatch Instructions for the following: - Choose the proper QSE from the Participant name - Choose COMMIT as the Instruction Type from the RES Level, - Enter reason RUC commit for (capacity, or contingency name) in “other information” When issuing a VDI or confirmation, ensure the use of three-part communication: - Issue the Operating Instruction - Receive a correct repeat back - Give an acknowledgement |
| Disapprove | IF: - WRUC completes the 7 days successfully, disapprove the study IF: - WRUC fails to complete the 7 days, rerun with 5 days. When it completes successfully, disapprove the study. - If fails to complete the 7 days, send e-mail to “Shiftsupv” to make notification that WRUC was unable to complete the 7 days. Provide error message in e-mail. - If fails to complete the 5 days, send e-mail to “Shiftsupv” to make notification that WRUC was unable to complete the 5 days. Provide error message in e-mail. |
| Create Save Case | IF: - WRUC is aborted or shut down; THEN: - Go to display System Administration > Savecase Management. - Choose File Type as WRUC. - Fill in File Name (no spaces allowed) - Fill in Description. - Push Create Button. - The message will show up in the Text field. - Refresh the display (F5), make sure the savecase name will show up in the File Name Field. - Notify Helpdesk and send e-mail to “shiftsupv” for back office to follow up. Also refer to Desktop Guide Common to Multiple Desks Section 2.16, if needed. |
| Log | - Log actions taken. |

## 6.2	EEA

Procedure Purpose: To RUC commit Resource that can be brought On-Line within the timeframe of the emergency.

| Protocol Reference | 3.9.1 | 6.5.9.4 | 6.5.9.4.1 | 6.5.9.4.2 |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.5.3.1 |  |  |  |
| NERC Standard | EOP-011-1 R2, R2.1, R2.2, R2.2.2, R2.2.3, R2.2.3.1 |  |  |  |

| Version: 1 |  | Revision: 9 | Effective Date: January 31, 2020 |  |
| --- | --- | --- | --- | --- |
| Step | Action |  |  |  |
| SWGRs using EMRSWGR Status | REFERENCE DISPLAY: Market Participation > Physical Market > Market Operator Data > SWGR Capacity Status Summary Switchable Generation Resource (SWGRs) is a Generation Resource that can be connected to either the ERCOT Transmission Grid or a non-ERCOT Control Area. Use the Switchable Generation Resources (SWGRs) User Guide (See Desktop Guide Reliability Unit Commitment Desk Section 2.21) for a list of resources. EMRSWGR: Available for RUC commitment only for ERCOT-declared Emergency Condition or ERCOT foresees entering into an emergency event. IF: - A SWGR is in EMRSWGR status; VERIFY: - QSE appropriately set temporal limits, - QSE appropriately set LSL and HSL to reflect operating limits, - The SWGR can be brought On-Line within the timeframe of the emergency; THEN: - Notify Shift Supervisor for coordination and possible transfer of non-ERCOT Control Area generation. |  |  |  |

| ERCOT Request Switch of SWGR | IF: - The non-ERCOT Control Area RC releases the SWGR; THEN: - Follow the VDI EMR process below. NOTIFY: - The QSE of ERCOT committing the resource into ERCOT, - To avoid direct connection between the ERCOT interconnection and Eastern interconnection instruct a “break before make” with all switching. Q#122 Typical Script ERCOT requests SWGR: |
| --- | --- |
| ERCOT is the Controlling Party | IF: - MISO or SPP call to request one or more SWGR be switched into them; THEN: - As soon as practicable, determine that releasing the SWGRs does not cause an Adverse Reliability Impact for ERCOT. NOTIFY: - The QSE of ERCOT releasing the resource into MISO or SPP, - To avoid direct connection between the ERCOT interconnection and Eastern interconnection instruct a “break before make” with all switching. Q#123 Typical Script SPP or MISO requests SWGR: |
| Primary Party Switch request / Recall | IF: - MISO or SPP calls to request the Switch of one or more SWGR’s in which they are identified as the Primary Party. - Or when the Primary Party makes notification of an existing or anticipated Emergency Condition and Recalls the SWGR’s: THEN: - The Secondary System Operator will release the SWGR as soon as possible, even if doing so would require controlled load shed. - See list of Primary Party and Secondary Parties in Exhibit B of the Coordination_Plans NOTIFY: - The QSE of ERCOT releasing the resource into MISO or SPP, - To avoid direct connection between the ERCOT interconnection and Eastern interconnection instruct a “break before make” with all switching. Q#124 Typical Script Notification to QSE of Release: |
| SWGR Requested by ERCOT released back to SPP or MISO | WHEN: - ERCOT is no longer in an existing or anticipated Emergency Condition. - As soon as practicable, determine that releasing the SWGRs does not cause an Adverse Reliability Impact for ERCOT. NOTIFY: - The QSE of ERCOT releasing the resource into MISO or SPP, - To avoid direct connection between the ERCOT interconnection and Eastern interconnection instruct a “break before make” with all switching. Q#125 Typical Script SWGR Requested by ERCOT released back to SPP or MISO: |
| VDI | IF: - A Generation Resource (without Non-Spin obligation) which has a unit status of OFF, EMR or EMRSWGR and can be brought On-line within the timeframe of the emergency; THEN: - Issue an electronic Dispatch Instruction to commit the Resource - Choose “Commit” as the Instruction Type from Resource level - Choose “System Capacity” as the Reason - VDIs need a start/stop time (issue one hour at a time) - Enter “RUC commit for capacity” in “other information” When issuing a VDI or confirmation, ensure the use of three-part communication: - Issue the Operating Instruction - Receive a correct repeat back - Give an acknowledgement |
| 1 | IF: - A Generation Resource was scheduled to come Off-line before the start of the emergency and requests to come Off-line; THEN: - Issue an electronic Dispatch Instruction to commit the Resource - Choose “Commit” as the Instruction Type from Resource level - VDIs need a start/stop time (issue one hour at a time) - Enter “RUC commit for capacity” in “other information” When issuing a VDI or confirmation, ensure the use of three-part communication: - Issue the Operating Instruction - Receive a correct repeat back - Give an acknowledgement |
| Log | Log all actions. |

## 7.1	Monthly Testing of Satellite Phones

Procedure Purpose:  To ensure ERCOT maintains communication capability via the Satellite Phone System.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | COM-001-3 R9 |  |  |  |

| Version: 1 | Revision: 6 | Effective Date: January 31, 2020 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Primary Control Center |  |
| NOTE | When a participant dials into the conference bridge before the moderator dials in, they will hear music and be placed on hold. |
| NOTE | On the first weekend of each month, between the hours of 0000 Saturday and 0500 Monday, the Satellite Phone System Conference Bridge will be tested with the TOs. As the Shift Supervisor makes the call to the individual TO, they will set a time that the ERCOT Operator will call the Satellite Phone System Conference Bridge and establish communication with the appropriate TO. |
| NOTE | Use the ERCOT Satellite Phone User Guide (See Desktop Guide Common to Multiple Desks Section 2.7) for a list of the TOs that will be contacted by the ERCOT Operator and instructions on how to place a Satellite Phone System Conference Bridge call. |
| NOTE | The numbers for the ERCOT Operator to call into the Conference Bridge are Desk specific. Select: SATELLITE directory or go to page 41 to view the programmed numbers on the Turret phone for each Bridge: - BLACKSTRT RUC – RUC Desk - BLACKSTRT RRD - Reliability Risk Desk - BLACKSTRT RES – Resource Desk - BLACKSTRT REAL – Real-Time Desk - BLACKSTRT TS#1 – Transmission Desk (Island Coordination) - BLACKSTRT TS#2 – Transmission Desk |
| 1 | IF: - Open a helpdesk ticket and cc “shiftsupv” - The preprogrammed number does not function correctly, THEN: - Refer to the ERCOT Satellite Phone User Guide (See Desktop Guide Common to Multiple Desks Section 2.7.2) for the appropriate conference number and continue with this procedure. |
| 2 | When prompted: - Enter the Moderator Pass Code - If necessary, allow five minutes for Participants to dial in - As each Participant connects, record the following: - Name of Participant - Company Name - Any problems identified with the connection process |
| 3 | IF: - One or more of the TOs fails to connect to the Bridge call; THEN: - Follow up with the TO to determine the cause: - Reason for inability to connect - Establish a time for a retest of the TOs not able to connect in the initial test. |
| 4 | Inform the Shift Supervisor when test is complete indicating any issues identified. |
| LOG | Log the test date and results in the Operations Log. |
| ### Alternate Control Center |  |
| 1 | When working out of the alternate during the monthly scheduled dates: - Test the turret Satellite phone on each desk. |
| 2 | Inform the Shift Supervisor when test is complete indicating any issues identified. |
| Log | Log the test date and results in the Operations Log. |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Frosch, Hartmann, Barcalow, Lowrie, and Stone | Preparers | November 10, 2010 |
| Frosch and Hartmann | Procedure writers and editors | November 29, 2010 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2010 |
| Frosch and Hartmann | Procedure writers and editors | January 26, 2011 |
| Frosch and Hartmann | Procedure writers and editors | March 23, 2011 |
| Frosch and Hartmann | Procedure writers and editors | April 20, 2011 |
| Frosch and Hartmann | Procedure writers and editors | June 6, 2011 |
| Frosch and Hartmann | Procedure writers and editors | July 18, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 22, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 30, 2011 |
| Frosch and Hartmann | Procedure writers and editors | October 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 16, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | April 25, 2012 |
| Frosch and Hartmann | Procedure writers and editors | July 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | October 26, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 26, 2013 |
| Frosch and Hartmann | Procedure writers and editors | May 28, 2013 |
| Frosch and Hartmann | Procedure writers and editors | July 8, 2013 |
| Cheng, Frosch and Hartmann | Procedure writers and editors | August 7, 2013 |
| Frosch and Hartmann | Procedure writers and editors | December 11, 2013 |
| Frosch and Hartmann | Procedure writers and editors | December 20, 2013 |
| Frosch, Gaddy and Hartmann | Procedure writers and editors | April 1, 2014 |
| Frosch, Gaddy and Hartmann | Procedure writers and editors | May 27, 2014 |
| Frosch and Hartmann | Procedure writers and editors | September 29, 2014 |
| Frosch and Hartmann | Procedure writers and editors | December 10, 2014 |
| Frosch and Hartmann | Procedure writers and editors | February 25, 2015 |
| Frosch and Hartmann | Procedure writers and editors | April 29, 2015 |
| Hartmann and Gaddy | Procedure writers and editors | July 13, 2015 |
| Hartmann and Gaddy | Procedure writers and editors | September 25, 2015 |
| Hartmann and Gaddy | Procedure writers and editors | December 22, 2015 |
| Frosch, Hartmann and Gaddy | Procedure writers and editors | January 22, 2016 |
| Hartmann and Gaddy | Procedure writers and editors | February 23, 2016 |
| Frosch, Hartmann and Gaddy | Procedure writers and editors | June 24, 2016 |
| Hartmann and Gaddy | Procedure writers and editors | September 26, 2016 |
| Hartmann and Gaddy | Procedure writers and editors | October 31, 2016 |
| Hartmann and Gaddy | Procedure writers and editors | December 23, 2016 |
| Hartmann, Gaddy and Frosch | Procedure writers and editors | March 27, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | May 26, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | June 23, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | September 27, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | December 22, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | February 22, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | March 26, 2018 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | April 27, 2018 |
| Hartmann, Gaddy, Ballew | Procedure writers and editors | May 25, 2018 |
| Hartmann, Gaddy, Ballew | Procedure writers and editors | August 24, 2018 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | December 21, 2018 |
| Hartmann, Gaddy, Luker and Frosch | Procedure writers and editors | March 26, 2019 |
| Hartmann, Gaddy and Pence | Procedure writers and editors | May 13, 2019 |
| Hartmann, Gaddy and Pence | Procedure writers and editors | May 28, 2019 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | October 29, 2019 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | December 20, 2019 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | January 27, 2020 |

Manual Change History

| Procedure | Ver/Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All Sections | 1.0 / 0 | New procedures for all sections for Nodal implementation | November 28, 2010 |
| 2.3 2.4 3.2 3.3 4.3 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Added new procedure “Phase Shifter Tap Settings” Updated Note Updated step “Monitor” Updated steps “Commit/De-Commit”, “Violated Constraints” and “HRUC Committed” Updated step “Review”, “A/S Insufficiency from DAM” and “DRUC Committed” | December 1, 2010 |
| 2.3 4.2 4.3 4.4 | 1.0 / 2 1.0 / 1 1.0 / 2 1.0 / 1 | Updated “Review Weather Data Information” step 2 Added steps “DRUC Committed for Capacity Shortage” and “Projected Reserve Capacity Shortage” Updated steps “DAM Timeline Deviation, DAM Failure, DRUC Delay & Software Failure” change to step 1 | December 15, 2010 |
| 3.2 4.3 4.1 4.4 6.1 | 1.0 / 2 1.0 / 3 1.0 / 2 - / 2 1.0 / 1 | Updated step “HRUC Committed Units”, “Manual Commitment”, added steps “Excess Generation” and “Canceling RUC commitments” Updated step DRUC Committed Units”, “Manual Commitment, added steps “Excess Generation” and “Canceling RUC commitments” Updated step “DAM Timeline Deviation”, DAM Failure”, DRUC Delay” Updated scripts Updated script | January 31, 2011 |
| 3.2 3.3 3.5 4.3 4.4 6.1 | 1.0 / 3 1.0 / 2 - / 0 - /4 - / 3 1.0 / 2 | Updated step Canceling RUC Commitments Deleted HRUC Timeline Deviation and updated HRUC Failure/Timeline Deviation Added new section Updated step Canceling RUC Commitments Updated step DAM Timeline Deviation in DAM Timeline Deviation/Failure Timeline not Met in section DRUC Timeline Deviation/Failure Updated Watch and Emergency Notice | March 25, 2011 |
| 2.5 3.2 3.3 4.3 6.1 6.2 | 1.0 / 1 1.0 / 4 1.0 / 3 1.0 / 5 1.0 / 3 1.0 / 1 | Updated Monthly MIS Posting Updated step Canceling RUC Commitments Updated step Failure Updated step Canceling RUC Commitments Updated step 1 in Watch and Emergency Notice Updated step & removed step Market Notification | April 22, 2011 |
| 3.2 3.5 4.3 4.4 5.2 6.1 | 1.0 / 5 1.0 / 1 1.0 / 6 1.0 / 4 1.0 / 1 1.0 / 4 | Updated steps HRUC Committed Units and Approval Updated all steps Updated step Approval Updated step DAM Timeline Deviation Updated step Long Lead Times Updated all steps | June 8, 2011 |
| 2.3 3.1 3.2 3.5 4.2 4.3 4.4 4.5 | 1.0 / 3 1.0 / 1 1.0 / 6 1.0 / 2 1.0 / 2 1.0 / 7 1.0 / 5 1.0 / 1 | Added steps for Publish A/S Requirements Updated Load Forecast step Updated steps Excess Generation, A/S Insufficiency from SASM, Violated Constraints and Approval Corrected title to match TOC and updated 1st note Updated Load Forecast step Updated Approval step Added subtitles, step DRUC Delay & step 1 Moved section 2.6 to 4.5 | July 20, 2011 |
| 2.3 2.4 3.2 3.3 4.3 6.1 7.1 | 1.0 / 4 - / 1 1.0 / 7 1.0 / 4 1.0 / 8 1.0 / 5 1.0 / 1 | Added Note to Increasing A/S Requirements before A/S Obligations Publish Added information on RMR Resource Commitment Updated step Excess Generation, added RMR Resources, RMR Commitment and Canceling RUC Commitments Updated step Commit/Decommit Resources by VDI Updated step Canceling RUC Commitments Added Projected Reserve Capacity Shortage to Watch Updated 4th note | August 24, 2011 |
| 3.2 4.2 4.3 6.1 7.1 | 1.0 / 8 1.0 / 3 1.0 / 9 1.0 / 6 1.0 / 2 | Added Note, updated step Hotline, Post and added step Cancel Deleted step RMR, updated Manual Commitment, deleted Note Updated Note Added Extreme Hot Weather in Watch Updated 3rd note and step 1 | September 1, 2011 |
| 2.3 2.4 3.1 3.2 4.3 4.4 4.5 4.6 4.5 Original | 1.0 / 5 1.0 / 2 1.0 / 2 1.0 / 9 1.0 / 10 1.0 / 6 1.0/ 0 1.0 / 0 1.0 / 2 | Deleted Phase Shifter Tap Settings Deleted step Resources Updated step Manual Commitment in Tasks prior to execution of HRUC Updated step RMR Resources and Canceling RUC Commitments Updated step for Canceling RUC Commitments Moved A/S Insufficiency in DAM to section 4.5 & DAM Failure to section 4.6 Moved A/S Insufficiency in DAM to section 4.5 & deleted Increase A/S Capacity needs about Day-Ahead Requirements Moved from section 4.5 Deleted procedure (was section 4.5), duplicate | November 1, 2011 |
| 2.3 6.1 | - / 6 1.0 / 7 | Removed Invalid SPS/RAP due to Outage Updated Post in “Notifications” All procedures in this manual have been reviewed. | December 15, 2011 |
| 1.2 3.5 4.3 4.6 | 1.0 / 1 1.0 / 3 1.0 / 11 1.0 / 3 | Updated Scope Updated all steps Updated A/S Insufficiency from DAM Updated desktop guide section | January 19, 2012 |
| 2.1 2.3 2.5 3.1 3.2 3.3 3.7 4.2 4.3 4.4 4.5 4.6 5.2 6.1 7.1 | 1.0 / 1 1.0 / 7 1.0 / 2 1.0 / 3 1.0 / 10 1.0 / 5 1.0 / 0 1.0 / 4 1.0 / 12 - / 7 1.0 / 3 1.0 / 4 1.0 / 2 1.0 / 8 1.0 / 3 | Updated 4th Paragraph Updated Desktop Guide reference Updated Monthly MIS Posting Updated Desktop Guide reference Updated Desktop Guide references and step After Approval Added step Create Save Case Added new procedure Projected Capacity Reserve Shortage with no Market Solution Updated Desktop Guide references Updated Desktop Guide references and added step After Approval Added step 2 Updated Desktop Guide reference Updated Desktop Guide reference Added step Create Save Case Updated step 1 of Watch Updated Desktop Guide references | March 1, 2012 |
| 1.1 2.1 3.1 3.2 3.3 4.2 4.3 5.1 5.2 6.1 8.1 | 1.0 / 1 1.0 / 2 1.0 / 4 1.0 / 11 1.0 / 6 1.0 / 5 1.0 / 13 1.0 / 1 1.0 / 3 1.0 / 9 1.0 / 1 | Changed Shift Engineer to Operations Support Engineer Changed TSP,DSP to TO Changed Shift Engineer to Operations Support Engineer Changed Shift Engineer to Operations Support Engineer Changed Shift Engineer to Operations Support Engineer Changed Shift Engineer to Operations Support Engineer and added WRUC Changed Shift Engineer to Operations Support Engineer and Manual Commitment Changed Shift Engineer to Operations Support Engineer Changed Shift Engineer to Operations Support Engineer and updated step Long Lead Times for NPRR402 Updated OCN, Advisory, Watch, Emergency Notice sections Changed Shift Engineer to Operations Support Engineer | May 1, 2012 |
| 1.1 1.3 2.3 3.1 3.2 3.3 4.2 4.3 4.4 5.2 6.1 7.1 | 1.0 / 2 1.0 / 1 1.0 / 8 1.0 / 5 - / 12 - / 7 - / 6 - / 14 - / 8 1.0 / 4 1.0 / 10 1.0 / 4 | Updated last paragraph, HRUC Removed ERCOT Shift Supervisor paragraph Updated step 3, added Fuel Switching and Optimize Fuel Supply & 2nd note Changed Shift Engineer to Operations Support Engineer Updated HRUC Committed Units Updated Create Save Case Updated Manual Commitment on 14:30 each day Updated DRUC Committed Units Updated step 2 in Delay of DRUC Updated Create Save Case Updated all step 1’s Updated 4th note | July 16, 2012 |
| 2.2 3.2 4.3 | 1.0 / 1 1.0 / 13 1.0 / 15 | Added Hotline Call Communication Updated Manual Commitment and Validate Updated Manual Commitment and Validate All procedures in this manual have been reviewed. | November 1, 2012 |
| 2.3 4.3 4.6 | 1.0 / 9 1.0 / 16 1.0 / 5 | Added Blackstart Availability Updated Review Updated steps SASM not able to Procure all A/S Requested & Cancel Emergency Notice | March 1, 2013 |
| 3.1 3.2 3.3 3.5 3.7 4.3 4.4 4.5 4.6 5.2 6.1 | 1.0 / 6 1.0 / 14 1.0 / 8 1.0 / 4 1.0 / 1 1.0 / 17 1.0 / 9 1.0 / 4 1.0 / 6 1.0 / 5 1.0 / 11 | Updated step Deselect Contingencies Updated step Monitor, Excess Generation, Hotline, & Cancel Updated step Failure & Create Save Case Updated step REG/RRS Updated all steps Updated 1st Note, A/S Insufficiency from DAM, Excess Generation &DRUC Committed from Capacity Shortage Updated all steps Updated all steps Updated all steps Updated step Create Save Case Updated Notifications | June 1, 2013 |
| 3.5 4.3 4.4 4.6 6.1 | 1.0 / 5 1.0 / 18 1.0 / 10 1.0 / 7 1.0 / 12 | Correct typo in script Correct typo’s in scripts Updated Delay of DRUC steps Corrected reference in desktop guide Updated step 1 in Watch & Emergency Notice | July 15, 2013 |
| 3.2 3.3 | 1.0 / 15 1.0 / 9 | Updated step HRUC Committed Units, Manual Commitment, HRUC Decommitted Resources & Approval Updated step Create Save Case | August 9, 2013 |
| 3.2 4.3 5.1 5.2 | 1.0 / 16 1.0 / 19 1.0 / 2 1.0 / 6 | Updated steps Violated Constraints, HRUC Committed Units, RMR Commitment & Manual Commitment Updated steps Violated Constraints, DRUC Committed Units & Manual Commitment Updated titles Updated Violated Constraints, Disapprove & Log. Deleted Long Lead Times, All procedures in this manual have been reviewed. | December 13, 2013 |
| 3.3 4.4 4.6 6.1 | 1.0 / 10 1.0 / 11 1.0 / 8 1.0 / 13 | Updated for NPRR542 Updated for NPRR542 Updated for NPRR542 Updated for NPRR542 and 529 | January 1, 2014 |
| 2.3 3.2 3.3 3.6 4.3 6.2 6.3 | 1.0 / 10 1.0 / 17 - / 11 1.0 / 1 1.0 / 20 1.0 / 0 1.0 / 2 | Updated Review and Select Load Forecast Updated step System Summary, HRUC Committed Units & VDI information Updated VDI information Added Manual Commit of a Resource & Canceling RUC Commitments Updated VDI information Updated DRUC Committed Units & VDI information Added new EEA procedure Change section number from 6.2 to 6.3 | April 4, 2014 |
| 2.2 2.3 2.4 2.5 3.2 3.6 4.5 4.6 5.2 6.1 | 1.0 / 2 1.0 / 11 1.0 / 3 1.0 / 3 1.0 / 18 1.0 / 2 1.0 / 5 1.0 / 9 1.0 / 7 1.0 / 14 | Added VDIs to Master QSEs Added Note to Increasing A/S before Publishing Added Note Updated Monthly MIS Posting step Updated step A/S Infeasibility Updated step 1 Updated step A/S Insufficiency Offers Updated DAM Failure Updated step Disapprove Added Note, updated Advisory & Watch | June 1, 2014 |
| 3.2 6.1 | 1.0 / 19 1.0 / 15 | Updated Undeliverable A/S Capacity, added STNET Study and title change on VSAT and RUC perform AC Analysis Updated Generic Script | October 1, 2014 |
| 3.2 3.2 4.3 6.2 | 1.0 / 20 1.0 / 20 1.0 / 21 1.0 / 1 | Updated step STNET Study, HRUC Committed Units & Manual Commitment Updated STNET Study, HRUC Committed Units & Manual Commitment Updated step DRUC Committed Units & Manual Commitment Added step All procedures in this manual have been reviewed | December 15, 2014 |
| 2.2 2.3 3.2 3.3 3.6 4.3 4.4 6.2 | 1.0 / 3 1.0 / 12 1.0 / 21 1.0 / 12 1.0 / 3 1.0 / 22 1.0 / 12 1.0 / 2 | Added Dispatch & Verbal Dispatch Instruction Deleted Meterlogix number. Updated Priority Outages Corrected VDI vs. Dispatch Instruction and Manual Commitment Corrected VDI vs. Dispatch Instruction Corrected VDI vs. Dispatch Instruction Updated step Manual Commitment & corrected VDI vs. Dispatch Instruction Updated DAM Timeline Deviation Corrected VDI vs. Dispatch Instruction | March 1, 2015 |
| 3.2 3.3 3.5 3.6 3.7 4.3 4.4 4.5 4.6 6.1 | 1.0 / 22 1.0 / 13 1.0 / 6 1.0 / 4 1.0 / 2 1.0 / 23 1.0 / 13 1.0 / 6 1.0 / 10 1.0 / 16 | Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Updated to implement NPRR679 Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure | May 1, 2015 |
| All Sections 5.2 | 1.0 / 1 1.0 / 8 | Added a “Q” for QSE scripts Updated Disapprove with email notification | July 15, 2015 |
| 3.6 | 1.0 / 5 | Updated 1st note | October 1, 2015 |
| 2.5 3.3 3.5 3.7 4.3 4.4 4.5 4.6 6.1 | 1.0 / 4 1.0 / 14 1.0 / 7 1.0 / 3 1.0 / 24 1.0 / 14 1.0 / 7 1.0 / 11 1.0 / 17 | Updated Monthly MIS Posting Added step After 20th of the month Updated step Last Day of the Month Updated HRUC Failure/Timeline Deviation step Failure Q#79 & Q#80 Updated step REG/RRS – RUC Committed Shortages Q#81& Q#82 Updated step Hotline Q#83 Updated step Cancel Q#84 Updated step A/S Insufficiency from DAM Q#86 Updated step Excess Generation Typical Script Q#87 & Q#88 Updated DAM Timeline Deviation step DAM Timeline Deviation Q#92 Updated Title DRUC Delay Updated DRUC Delay step DRUC Completes By 18:00 Q#94 Updated DRUC Delay step 2 Typical Script Q#96 Updated step A/S Insufficiency Offers Q#97 Updated step DAM Complete with A/S Q#98 Updated step Cancel Watch Q#99 Updated step DAM Failure Q#100 Updated step Cancel Watch Q#101 Updated Title Operating Condition Script Updated Operating Condition Script step Hotline Q#46 Updated Operating Condition Script step Hotline Cancellation Q#47 All procedures in this manual have been reviewed | December 31, 2015 |
| 2.1 3.6 3.6 3.7 | 1.0 / 3 1.0 / 0 1.0 / 6 1.0 / 4 | Updated System Operator Responsibility and Authority Added new Assigning Ancillary Services procedure Change section number from 3.6 to 3.7 Change section number from 3.7 to 3.8 Updated Hotline Q#83 Updated Cancel Q#84 | February 10, 2016 |
| 1.3 5.2 | 1.0 / 2 1.0 / 9 | Removed Interchange Coordinator Added step EDI step | March 1, 2016 |
| 2.1 2.2 2.4 3.1 3.2 3.3 3.6 3.7 4.3 5.2 6.1 6.2 | 1.0 / 4 1.0 / 4 1.0 / 4 1.0 / 7 1.0 / 23 1.0 / 15 1.0 / 1 1.0 / 7 1.0 / 25 1.0 / 10 1.0 / 18 1.0 / 3 | Updated for COM-002-4 Updated for COM-002-4 Added steps Note, Resources, 1, 2, & 3 Updated RMR Consideration &Manual Commitment steps Updated for COM-002-4 Updated for COM-002-4 Updated for COM-002-4 Updated for COM-002-4 & noteUpdated for COM-002-4 Updated for COM-002-4 Updated for COM-002-4 Updated for COM-002-4 | June 30, 2016 |
| 3.4 | 1.0 / 1 | Added Resources Startup Time Less Than One Hour | September 30, 2016 |
| 6.2 | 1.0 / 5 | Deleted step 2 | November 2, 2016 |
|  |  | All procedures in this manual have been reviewed | December 30, 2016 |
| 1.3 2.1 2.5 3.7 5.2 6.1 6.3 8.1 | 1.0 / 3 1.0 / 5 1.0 / 5 1.0 / 8 1.0 / 11 1.0 / 19 1.0 / 3 1.0 / 2 | Deleted section 1.3 Updated for IRO-001-4 Updated procedure purpose Updated Monthly MIS Posting Updated note Updated Manual Dispatch to take a Unit Off-Line step 1 Updated note Updated Title and all 1st steps Updated Market Notifications steps Updated Note Updated Title and QSE Issues step 1 and step 3 | March 31, 2017 |
| 3.2 3.6 3.7 3.8 4.3 | 1.0 / 24 1.0 / 2 1.0 / 9 1.0 / 5 1.0 / 26 | Updated step Excess Generation Updated step OpsMon Display to Splunk Display Updated Manual Commit of a Resource step 1 Updated step Monitor Updated step Excess Generation | June 1, 2017 |
| 3.2 3.7 | 1.0 / 25 1.0 / 10 | Added Manual Commitment to bring a Combined Cycle On Line Updated 1st Note and Manual Dispatch to bring a Unit of a Combined Cycle On-line | June 30, 2017 |
| 3.7 | 1.0 / 11 | Added Manual Dispatch of an OFFQS Resource | September 29, 2017 |
| 2.4 7.1 | 1.0 / 5 1.0 / 5 | All procedures in this manual have been reviewed Removed Greens Bayou Unit 5 Updated Primary Control Center 4th note | December 28, 2017 |
| 3.7 | 1.0 / 12 | Updated Manual Commit of a Resource, Manual Dispatch of an OFFQS Resource and Manual Dispatch to bring a Unit of a Combined Cycle On-line | February 28, 2018 |
| 3.2 | 1.0 / 26 | Added EMR Resources step | March 28, 2018 |
| 2.2 3.5 | 1.0 / 5 1.0 / 8 | Updated procedure purpose Updated REG/RRS - RUC Committed Shortages | May 1, 2018 |
| 2.3 4.4 6.2 | 1.0 / 13 1.0 / 15 1.0 / 5 | Added Email to Priority Outages Subsection Updated step DRUC Delay Added SWGR language in procedure | May 31, 2018 |
| 3.7 | 1.0 / 13 | Updated Manual Dispatch of an OFFQS Resource | August 31, 2018 |
| 3.1 3.2 4.1 4.2 4.3 | 1.0 / 8 1.0 / 27 1.0 / 1 1.0 / 7 1.0 / 27 | Moved Deselect Contingencies to Desktop Guide Reliability Unit Commitment Desk Clarfication for step HRUC Committed Units Added note to clarify when an an OFF-LINE study is required Moved Deselect Contingencies to Desktop Guide Reliability Unit Commitment Desk Deleted Bad/Suspect Telemetry Clarfication for step DRUC Committed Units All procedures in this manual have been reviewed | December 28, 2018 |
| 3.2 4.3 | 1.0 / 28 1.0 / 28 | Updated step HRUC Committed Units Updated step Review | March 29, 2019 |
| 3.2 3.7 | 1.0 / 29 1.0 / 14 | Added step Post to Canceling RUC Commitments Added step Post to Canceling RUC Commitments | May 16, 2019 |
| 6.2 | 1.0 / 6 | Updated for NPRR901 | May 31, 2019 |
| 3.2 3.7 4.3 6.2 | 1.0 / 30 1.0 / 15 1.0 / 29 1.0 / 7 | Updated step Approval Updated NOTE Updated step Approval Updated steps and added SWGR Requested by ERCOT released back to SPP or MISO | November 1, 2019 |
| 3.2 4.3 6.2 | 1.0 / 31 1.0 / 30 1.0 / 8 | Updated step Monitor Updated step Review Updated step VDI All procedures in this manual have been reviewed | January 1, 2020 |
| 2.3 3.1 3.2 3.3 3.7 4.2 4.3 5.2 6.2 7.1 | 1.0 / 14 1.0 / 9 1.0 / 32 1.0 / 16 1.0 / 16 1.0 / 8 1.0 / 31 1.0 / 12 1.0 / 9 1.0 / 6 | Clarified RUC-commits/decommits Clarified RUC-commits/decommits Clarified RUC-commits/decommits Clarified RUC-commits/decommits Clarified RUC-commits/decommits Clarified RUC-commits/decommits Clarified RUC-commits/decommits Clarified RUC-commits/decommits Clarified RUC-commits/decommits Updated Primary Control Center steps 1 & 3 | January 31, 2020 |