- Power Operations Bulletin # 933

ERCOT has posted/revised the Reliability Risk Desk manual.

A copy of the procedure can be found at:

- http://www.ercot.com/mktrules/guides/procedures/index.html

## 3.4	Monitor Curtailed Intermittent Renewable Resource Performance

Procedure Purpose:  To monitor intermittent resources to confirm units are responding and following curtailments properly.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | TOP-001-4 R2 |  |  |  |

| Version: 1 | Revision: 1 | Effective Date: February 28, 2020 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Wind or Solar Unit Curtailments |  |
| NOTE | An Intermittent Renewable Resource (IRR) must comply with Dispatch Instructions when receiving a flag signifying that the IRR has received a Base Point below the HDL used by SCED. When the SBBH (SCED Basepoint Below HDL) flag is set this will assist the intermittent resources in recognizing the need to reduce generation output due to transmission network constraint violations. |
| NOTE | IRRs with a telemetered resource status equal to OFF, OUT or ONTEST should ignore the SBBH flag. If a curtailment is necessary for an IRR that is telemetering a Unit status of ONTEST ERCOT Operations will verbally communicate the necessary Dispatch instructions to the resource’s QSE. |
| ONTEST | Resources with a Resource Status of ONTEST, may not be issued dispatch instructions except: - For Dispatch Instructions that are a part of the testing; or - During conditions when the Resource is the only alternative for solving a transmission constraint (would need QSE to change Resource Status); or - During Force Majeure Events that threaten the reliability of the ERCOT System. THEN: - Discuss with Shift Supervisor and Coordinate with the Transmission & Security Operator |
| NOTE | HSL should remain at the forecasted output capability for the IRR. If HSL is observed decreasing with the curtailed SCED dispatch instructions then notify the resource’s QSE to investigate. |
| Base Point Deviation | IF: - A QSE has an Intermittent Renewable Resource (IRR) with a large Base Point deviation AND the resource is not curtailed - Their generation is not moving in the proper direction to correct their Base Point Deviation; THEN: - Possible reasons, if known (Base Point deviation, large forecast errors, failed telemetry, icing conditions, down or up ramp event, unit trip, etc.) - Notify the QSE of the issue. |
| LOG | Log all actions. |

## 4.1	Responding to Wind Forecast Errors

Procedure Purpose:  Make corrections to errors in the weather forecast data (in EMS) and/or  switch between two wind forecasts needed to contribute to reliable system performance.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 4 | Effective Date: February 28, 2020 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | The wind forecasts produced by both UL (Underwriters Laboratories) and Energy & Meteo (E&M) provide enhanced situational awareness by additional means of validating the expected wind conditions. The selected wind forecast between two is sent to Wind QSEs to update their COP and used by the downstream EMS applications. |
| NOTE | Do not continuously switch between two wind forecasting services for a small gain in accuracy (i.e. “chasing the forecast”) |
| STWPF Selection Change due to forecast vs. output deviation | IF: - The end of adjustment period selected wind forecast which is currently in use has been greater than the actual wind HSL for more than 2000 MW for at least three hours or 3000 MW for at least one hour or reliability concern and the other vendor forecast has been more accurate; THEN: - Log the period of time for which the forecast has been underperforming and the accuracy of both forecasts. Inform the Shift Supervisor and potentially switch forecast selection to alternative wind forecast which has been more accurate, - E-mail the information to: - Operations Analysis - 1 ERCOT Shift Supervisors Reference Display: ERCOT EMP Applications>Wind Forecasting Service>Hourly EMS wind forecast and other necessary displays. |
| NOTE | The projected wind ramp rate (PWRR) calculation is such that it will revert to using persistence (PWRR=0) if the actual wind HSL has been ramping in the opposite direction of the PWRR value for more than 25 minutes (5 intervals). RLC will set the PWRR to 0 to minimize the impact and then cancel the flag after the PWRR is forecasting the ramp to be the same as the actual ramp again. |
| Intra-Hour wind Forecast | IF: - Alarmed, make sure frequency isn’t rapidly declining and wind hasn’t turned direction and is ramping very fast (really only need to be concerned when getting above 300-400 MW per 5 minutes and causing frequency to decline below 59.95 Hz). If frequency does drag and regulation is exhausted, the Real-Time Desk should follow their procedure for manually running SCED. Watch the PWRR and wind ramp to help inform the Real-Time Desk; THEN: - Notify an Operations Analysis Engineer to do further analysis, - E-mail the information to: - Operations Analysis - 1 ERCOT Shift Supervisors |
| LOG | Log all actions. |

## 4.3	Operations in the Rio Grande Valley Region

Procedure Purpose:  To monitor the wind forecast in the instance of a capacity shortage potential in the Lower Rio Grande Valley (RGV).

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 1 | Effective Date: February 28, 2020 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Load in capacity short area is high and wind is also forecasted to be above 75% of regional capacity. |  |
| REVIEW | IF: - The RGV wind forecast seems invalid, OR - IRR generation is not meeting the RGV wind forecast that could cause a reliability concern, THEN: - Notify an Operations Analysis Engineer for adjustments, - E-mail the information to: - Operations Analysis - 1 ERCOT Shift Supervisors |
| Manually Override Short Term Wind Power Forecast | Contact the Operations Analysis Engineer to do further analysis and to possible override the Forecast. |
| ACTION | Further analysis could potentially reduce the forecasted value of the region in question to the WGRPP value or another lower output that should allow the system to have adequate reserves given an under forecast. |
| LOG | Log all actions. |

## 4.4  Operations in the Panhandle region

Procedure Purpose:  To monitor the wind forecast in the instance of a capacity shortage in the Panhandle region.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 2 | Effective Date: February 28, 2020 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Panhandle region is high export and wind is also forecasted to be above 75% of regional capacity. |  |
| REVIEW | IF: - The Panhandle wind forecast seems invalid, OR - IRR generation is not meeting the Panhandle wind forecast that could cause a reliability concern, THEN: - Notify an Operations Analysis Engineer for adjustments, - E-mail the information to: - Operations Analysis - 1 ERCOT Shift Supervisors |
| Manually Override Short Term Wind Power Forecast | Contact the Operations Analysis Engineer to do further analysis and to possible override the Forecast. |
| ACTION | Further analysis could potentially reduce the forecasted value of the region in question to the WGRPP value or another lower output that should allow the system to have adequate reserves given an under forecast. |
| LOG | Log all actions. |

## 4.5  Severe Weather Operations

Procedure Purpose:  To monitor the wind forecast during operations with severe weather conditions.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 1 | Effective Date: February 28, 2020 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Loss of Wind Farm Turbines due to Severe Weather |  |
| NOTE | Significant weather events can consist of, but are not limited to the following: - Tornados - Strong straight line winds - Hail - Severe lightning - Flooding - Freezing precipitation - Hard freeze |
| Manually Override Short Term Wind Power Forecast | The ERCOT Operator will contact the Operations Analysis Engineer to conduct further analysis and to override system: IF: - A severe weather related de-rate has occurred at a given wind farm, and - The telemetry, Outage Scheduler and COP have not been correctly updated by the QSE. Contact Operations Analysis Engineer to do further analysis and potentially override the forecast given the description above after checking the following: - Number of turbines online - Number of turbines offline - Outage scheduler - Telemetered wind speed (MPH) |
| NOTE | The QSE should: - Update wind generating unit’s telemetry to reflect the number of turbines lost. - NTON – number of turbines online - NTOF – number of turbines offline - NTUN – number of turbines unknown - Update ERCOT Outage Scheduler for updated HSL information that correctly reflects the number of turbines lost. This follows procedure for forced outages and should be done immediately. - Update unit’s COP in relation to the most recent forecast for the next hour(s) that pertains to the duration the turbines will be lost and accurately reflects the number of turbines lost. Notification to the QSE may be necessary if the above are not complete within the designated time frame. |
| Post | Coordinate with the Real-Time Operator for making hotline calls and the posting of the notices on MIS Public. |
| Cancel Posting | Coordinate with the Real-Time Operator for the cancelation of the postings on MIS Public and making hotline calls. |
| LOG | Log all actions. |
| ### High Wind Output Forecast with Forecasted Severe Weather in a Region |  |
| Manually Override Short Term Wind Power Forecast | The ERCOT Operator will contact the Operations Analysis Engineer to conduct further analysis and to override the system if all of the following conditions are met: - The wind forecast is persistently higher than the actual output (the over-forecast error will exceed 20% of installed capacity of wind farms affected or 1000 MW in a region) for a future period of time. - Weather forecasts from multiple sources indicate a winter/tropical storm will occur in the same time-line as the high forecasted output. |
| ACTION | Further analysis could potentially reduce the forecasted value of the region in question to a lower output. |
| EXAMPLE | Below is an example of the STWPF being much higher due to turbines freezing. You will see the light blue line much lower than the multiple colored lines that are forecasts. When the actual output begins to dip away from the forecast and icing conditions exist, it is likely an override is needed. |
| LOG | Log all actions. |

## 4.6  Solar Forecast

Procedure Purpose:  To monitor Maxar Solar forecast during normal and abnormal operations. It is presumed that under normal operating conditions that the solar forecast override will very rarely be used. However, there are certain scenarios that might dictate an override.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 1 | Effective Date: February 28, 2020 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Maxar Solar Forecast |  |
| NOTE | If solar forecast is invalid or appears to have other discrepancies; - Contact Operations Analysis Engineer to do further analysis and determine if it is necessary to override Solar forecast; - Solar Forecast can only be overwritten by Maxar |
| Maxar Solar Forecast | IF: - The Maxar Solar Forecast seems invalid; THEN: - Notify an Operations Analysis Engineer for adjustments, - E-mail the information to: - 1 ERCOT Shift Supervisors - Operations Analysis Reference Display: Curtailment Tool Forecast section and other necessary displays. |
| LOG | Log all actions. |

## 8.1	Monthly Testing of Satellite Phone Conference Bridge

Procedure Purpose:  To ensure ERCOT maintains communication capability via the Satellite Phone System.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 3 | Effective Date: February 28, 2020 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Primary Control Center |  |
| NOTE | When a participant dials into the conference bridge before the moderator dials in, they will hear music and be placed on hold. |
| NOTE | On the first weekend of each month, between the hours of 0000 Saturday and 0500 Monday, the Satellite Phone System Conference Bridge will be tested with the TOs. As the Shift Supervisor makes the call to the individual TO, they will set a time that the ERCOT Operator will call the Satellite Phone System Conference Bridge and establish communication with the appropriate TO. |
| NOTE | Use the ERCOT Satellite Phone User Guide (See Desktop Guide Common to Multiple Desks Section 2.7) for a list of the TOs that will be contacted by the ERCOT Operator and instructions on how to place a Satellite Phone System Conference Bridge call. |
| NOTE | The numbers for the ERCOT Operator to call into the Conference Bridge are Desk specific. Select: SATELLITE directory or go to page 41 to view the programmed numbers on the Turret phone for each Bridge: - BLACKSTRT RUC – RUC Desk - BLACKSTRT RRD – Reliability Risk Desk - BLACKSTRT RES – Resource Desk - BLACKSTRT REAL – Real-Time Desk - BLACKSTRT TS#1 – Transmission Desk (Island Coordination) - BLACKSTRT TS#2 – Transmission Desk |
| 1 | IF: - Open a helpdesk ticket and cc “shiftsupv” - The preprogrammed number does not function correctly, THEN: - Refer to the ERCOT Satellite Phone User Guide (See Desktop Guide Common to Multiple Desks Section 2.7.2) for the appropriate conference number and continue with this procedure. |
| 2 | When prompted: - Enter the Moderator Pass Code - If necessary, allow five minutes for Participants to dial in - As each Participant connects, record the following: - Name of Participant - Company Name - Any problems identified with the connection process |
| 3 | IF: - One or more of the TOs fails to connect to the Bridge call; THEN: - Follow up with the TO to determine the cause: - Reason for inability to connect - Establish a time for a retest of the TOs not able to connect in the initial test. |
| 4 | Inform the Shift Supervisor when test is complete indicating any issues identified. |
| LOG | Log the test date and results in the Operations Log. |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Hartmann, Gaddy, Self, and Frosch | Preparers | January 24, 2017 |
| Hartmann, Gaddy and Frosch | Procedure writers and editors | March 27, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | May 26, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | June 23, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | July 24, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | September 27, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | December 22, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | February 22, 2018 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | March 26, 2018 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | April 27, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | May 25, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | August 24, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | December 21, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | January 25, 2019 |
| Hartmann, Gaddy and Pence | Procedure writers and editors | July 29, 2019 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | October 29, 2019 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | December 20, 2019 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | January 27, 2020 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | February 24, 2020 |

Manual Change History

| Procedure | Ver/Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All | 1.0 / 0 | New procedures | January 30, 2017 |
| 2.1 3.1 4.4 5.1 7.1 7.2 9.1 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Updated System Operator Responsibility and Authority Updated Up Ramp Event step 2 Updated Panhandle Region Updated Reliability Risk Desk performs STNET Study Updated title and all 1st steps Updated Implement EEA Level 3 steps Updated Title | March 31, 2017 |
| 3.1 | 1.0 / 2 | Updated Down Ramp Event step 1, 2 & 3 Updated Up Ramp Event step 1 & 2 | June 1, 2017 |
| 3.1 7.2 | 1.0 / 3 1.0 / 2 | Updated Down Ramp Event step 2 Updated 1st note, step 1 changed to EEA Level 3 | June 30, 2017 |
| 7.2 | 1.0 / 3 | Added note Implement EEA Level 2 and Level 3 | July 28, 2017 |
| 7.2 | 1.0 / 4 | Updated Implement EEA Level 3 | September 29, 2017 |
| 8.1 | 1.0 / 1 | All procedures in this manual have been reviewed Updated Primary Control Center 4th note | December 28, 2017 |
| 3.3 | 1.0 / 1 | Updated Day Ahead RRS Sufficiency Monitoring, moved Real-time RRS Sufficiency Monitoring down, added Look Ahead Critical Inertia Level Sufficiency Monitoring and Real-time Critical Inertia Level Sufficiency Monitoring | February 28, 2018 |
| 9.1 | 1.0 / 2 | Updated Note | March 30, 2018 |
| 2.2 | 1.0 / 1 | Updated procedure purpose | May 1, 2018 |
| 5.1 | 1.0 / 2 | Added Phase Angles steps | May 31, 2018 |
| 5.1 | 1.0 / 3 | Updated and named step to Voltage contingencies | August 31, 2018 |
| 4.1 4.2 | 1.0 / 1 1.0 / 1 | Updated procedure purpose, added note and updated step Updated procedure purpose, added note and updated step All procedures in this manual have been reviewed | December 28, 2018 |
| 4.2 | 1.0 / 2 | Updated steps | January 31, 2019 |
| 3.1 4.1 | 1.0 / 3 1.0 / 2 | Deleted all steps Monitor Large Ramp Events Added Intra-Hour Wind Forecast and added Note Updated STWPF Selection Change due to forecast vs. output deviation and added Note | August 1, 2019 |
| 4.1 4.7 5.1 | 1.0 / 3 1.0 / 0 1.0 / 4 | Removed Weather Forecast Created section Weather Forecast Errors Updated Voltage Contingencies | November 1, 2019 |
| 7.2 7.3 | 1.0 / 5 1.0 / 1 | Updated MSSC Updated MSSC All procedures in this manual have been reviewed | January 1, 2020 |
| 3.3 5.1 7.3 8.1 | 1.0 / 2 1.0 / 5 1.0 / 2 1.0 / 2 | Clarified RUC-commits/decommits Clarified RUC-commits/decommits Clarified RUC-commits/decommits Updated Primary Control Center steps 1 & 3 | January 31, 2020 |
| 3.4 4.1 4.3 4.4 4.5 4.6 8.1 | 1.0 / 1 1.0 / 4 1.0 / 1 1.0 / 2 1.0 / 1 1.0 / 1 1.0 / 3 | Updated 3rd Note Updated 1st Note Updated Procedure Purpose & steps Updated Procedure Purpose & steps Updated Procedure Purpose Updated Procedure Purpose, Title & steps Updated Title and removed Alternate Control Center | February 28, 2020 |