- Power Operations Bulletin # 965

ERCOT has posted/revised the Resource Desk manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

- http://www.ercot.com/mktrules/guides/procedures/index.html

## 1.1	Purpose

This procedure provides the System Operator assigned to the Resource Desk with detailed Procedures required for performing duties assigned to that position.

The Resource Desk shall monitor Ancillary Service levels to ensure QSEs are meeting their A/S obligations, execute a Supplemental Ancillary Service Market to procure additional/insufficient A/S as needed, deploy/recall A/S (Non-Spin, Load Resources providing RRS, etc.) as system conditions require or as instructed by the Shift Supervisor.  The Resource Desk Operator will also be responsible for various communication testing (Hotline, Satellite Phone, etc.), issuing market notifications and ERCOT Website postings using Notice Builder, compliance monitoring, Forced Outage Detection (Resources), monitoring and responding to telemetry issues, resolving Market Participant issues and questions, and assisting other desk Operators in the Control Room as needed.

## 3.3	Notifications for Diminishing Reserves and Deploying Non-Spin

Procedure Purpose:  Monitor the Physical Responsive Capability (PRC) for issuing advance notice of diminishing Responsive Reserve.  This also includes the deployment of Non-Spin when PRC drops below 2500 MW.

| Protocol Reference | 3.17.3(2) | 6.5.7.6.2.2(13) | 6.5.7.6.2.3 | 6.5.9.4.1 |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.5.3.1(1)(d) | 4.5.3.1(1)(e) |  |  |
| NERC Standard | EOP-011-1 R2, R2.1, R2.2, R2.2.3, R2.2.3.1 | IRO-001-4 R1 | TOP-001-4 R2 |  |

| Version: 1 | Revision: 17 | Effective Date: December 31, 2020 |
| --- | --- | --- |

| Step | Action |  |
| --- | --- | --- |
| ### Advisory |  |  |
| Issue Advisory | WHEN: - PRC falls < 3000 MW; THEN: - Coordinate with the Real-Time Operator and Shift Supervisor, - Post message on the ERCOT Website Typical ERCOT Website Posting an Advisory for PRC: “ERCOT is issuing an Advisory for Physical Responsive Capability less than 3000 MW.” |  |
| Cancel Advisory | WHEN: - PRC > 3000 MW; THEN: - Coordinate with Real-Time Operator and Shift Supervisor, AND - Cancel message on ERCOT Website. |  |
| Log | Log all actions. |  |
| ### Watch |  |  |
| Issue Watch & Deploy Off-Line Non-Spin | WHEN: - PRC falls < 2500 MW; THEN: - Coordinate with Real-Time Operator and Shift Supervisor, - Coordinate with the Transmission Operator to verify the Non-Spin does not create congestion, - Deploy Non-Spin, (Refer to Desktop Guide Resource Desk Section 2.1.1) - Post message on the ERCOT Website for Non-Spin deployment, and - Post message for Watch on the ERCOT Website Typical ERCOT Website Posting for Non-Spin deployment: “At [x:xx] approximately [xx] MW of Non-Spin has been deployed, anticipated duration is [xx].” Typical ERCOT Website Posting a Watch for PRC: “ERCOT is issuing a Watch for Physical Responsive Capability less than 2500 MW”. |  |
| Additional Deployment | IF: - Additional Non-Spin becomes available going into next hour; THEN: - Determine if the additional Non-Spin is needed, - Deploy if needed (Refer to Desktop Guide Resource Desk Section 2.1.1) |  |
| Request Resource Stay Online | IF: - Notified by a QSE that their Off-line Non-Spin obligation has ended, AND - PRC < 2500 MW; THEN: - Request that the Resource stay On-line, - Request RUC operator to issue an electronic Dispatch Instruction to RUC commit |  |
| NOTE | If Non-Spin is deployed from one operating day to the next operating day, new deployments will need to be sent for the new day. |  |
| Recall Non-Spin | WHEN: - PRC > 2800 MW; THEN: - Coordinate with the Real-Time Operator and Shift Supervisor - Recall the Non-Spin (Refer to Desktop Guide Resource Desk Section 2.1.4) - Post message on the ERCOT Website to recall the Non-Spin, and - Cancel message for Watch on the ERCOT Website Typical ERCOT Website Posting for Non-Spin Recall: - “At [x:xx], All Non-Spin has been recalled.” |  |
| Log | Log all actions. |  |

## 3.4	System Failures

Procedure Purpose: To ensure Market Participants are notified via ERCOT Website using Notice Builder of any SCED/RLC/LFC (AGC) failures on the ERCOT systems.

| Protocol Reference | 6.5.9.2(2) | 6.5.9.3.3 |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | TOP-001-4 R9 |  |  |  |

| Version: 1 | Revision: 11 | Effective Date: December 31, 2020 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### SCED/RLC/LFC (AGC) Failures |  |
| 1 | WHEN: - Notified by the Real-Time Operator of a SCED/RLC/LFC(AGC) failure; THEN: - Post the appropriate message on the ERCOT Website - WATCH for SCED failure - Emergency Notice if both MMS and EMS have failed Typical ERCOT Website posting a Watch / Emergency Notice for SCED/RLC/LFC (AGC) Failure: “ERCOT has issued an [Watch or Emergency Notice] due to the failure of [SCED/RLC Failure], and/or [LFC].” |
| 2 | WHEN: - Notified by the Real-Time Operator that SCED/RLC/LFC(AGC) has been restored; THEN: - Cancel message on the ERCOT Website |
| Log | Log all actions. |
| ### ICCP, ERCOT Website, and Outage Scheduler Outages |  |
| 1 | WHEN: - Notified by the Real-Time Operator of a ICCP, ERCOT Website or Outage Scheduler failure; THEN: - Post an OCN on ERCOT Website Typical OCN ERCOT Website posting ICCP, ERCOT Website and Outage Scheduler Outage: “ERCOT has issued an OCN for the [planned / unplanned outage] of ERCOT’s [ICCP, ERCOT Website, and/or Outage Scheduler] outage.” |
| 2 | WHEN: - Notified by the Real-Time Operator that the ICCP, ERCOT Website and/or Outage Scheduler has been restored; THEN: - Cancel message on ERCOT Website |
| Log | Log all actions. |

## 3.7	Deploying Non-Spin for Critical Inertia Level

Procedure Purpose:  Monitor and detect possible time periods when Critical Inertia Level may be inadequate based on expected online inertia with recommended actions.

| Protocol Reference | 6.5.7.6.2.3(14) |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 2 | Effective Date: December 31, 2020 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Deploy Off-Line Non-Spin | IF: - Notified by the ERCOT Reliability Risk operator of the need to deploy Non-Spin due to Critical Inertia Level. THEN: - Coordinate with Reliability Risk operator and Shift Supervisor, - Coordinate with the Transmission Operator to verify the Non-Spin does not create congestion, - Deploy Non-Spin, (Refer to Desktop Guide Resource Desk Section 2.1.1) - Post message on the ERCOT Website for Non-Spin deployment. Typical ERCOT Website Posting for Non-Spin deployment: “At [x:xx] approximately [xx] MW of Non-Spin has been deployed, anticipated duration is [xx].” |
| NOTE | If Non-Spin is deployed from one operating day to the next operating day, new deployments will need to be sent for the new day. |
| Request Resource Stay Online | IF: - Notified by a QSE that their Off-line Non-Spin obligation has ended, AND - The Resources is still needed; THEN: - Request the RUC operator to issue an electronic Dispatch Instruction to RUC commit. |
| Additional Deployment | IF: - Additional Non-Spin becomes available going into next hour; THEN: - Determine if the additional Non-Spin is needed, - Deploy if needed (Refer to Desktop Guide Resource Desk Section 2.1.1) |
| Termination | IF: - Notified by the ERCOT Reliability Risk Operator that Non-Spin is no longer needed; THEN: - Recall the Non-Spin, by sending a Zero MW XML (Refer to Desktop Guide Resource Desk Section 2.1.4). - Post message on the ERCOT Website to recall the Non-Spin Typical ERCOT Website Posting for Non-Spin Recall: “At [x:xx], All Non-Spin has been recalled.” |
| LOG | Log all actions. |

## 3.8	Unannounced Resource Testing

Procedure Purpose: This procedure provides direction and guidelines for conducting unannounced testing of resources.

| Protocol Reference | 8.1.1.2 |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 3.3.1 |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 5 | Effective Date: December 31, 2020 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Unannounced Resource Testing |  |
| NOTE | - Operations Analysis will provide the list of resources to be tested. - The list of units are located at ERCOT SharePoint > System Operations – Control Center > Documents > Unannounced Unit Testing List. Use the current document. - In addition, the Shift Supervisor may request at his discretion an unannounced test of any resource, other than Hydro, Wind, PhotoVoltaic (PV) and Nuclear-fueled Resources. - Tests may be conducted as they best fit within the activities of the ERCOT Control Room, a minimum of 4 resources per week. - The Resource to be tested must be On-line before beginning the test. - No more than two Generation Resources within one QSE simultaneously, Combine Cycle Resources associated to the same train will be counted as one Generation Resource. - To identify potential congestion it may be necessary to conduct a Security Analysis Study using a Powerflow Base Case or Real-time Snap shot of the System. - NDCRC – Net Dependable Capability / Reactive Capability is located on the ERCOT Website in the Applications folder - Operations Analysis will complete the following items in the NDCRC: - Telemetry at Start of Test ERCOT reported value (MW) - Telemetry when HSL is reached ERCOT reported value (MW) - HSL is reached checkbox - Current Seasonal HSL(Net MW) - 30 Min Avg Real Time Telemetry (MW) - Additional Comments - Overall Test Results |
| Reference | Please refer to Desktop Guide Common to Multiple Desks for Unannounced Resource Testing process. |
| Caution | - Do not perform an unannounced test during a Watch for PRC or EEA event. - Do not perform an unannounced test on a unit with an approved unit test. - If an unannounced test is underway when a Watch or EEA event commences, the test may be cancelled. |
| Testing Rules and Scripts | ISSUE an instruction to the QSE for the Resource being tested. The QSE has the following time to reach its HSL, depending on its output when the test begins: - At LSL – 60 minutes to reach 90% of HSL, and an additional 20 minutes to reach HSL - Between LSL and 50 % of HSL – 60 minutes to reach HSL - Above 50 % of HSL – 30 minutes to reach HSL Q#120 - Typical script to Perform Unannounced Unit Test: Combine Cycle Resources should include all units of the train. All QSEs associated with a jointly owned unit will be tested simultaneously. When the Resource reaches the time requirement or it’s HSL, SUSTAIN it at or above the Resources HSL for at least 30 minutes. NOTIFY the QSE that the test is complete, and RELEASE the resource from its VDI. If the Resource fails to reach its HSL within the time frame, CONTINUE TO HOLD the resource for at least 30 minutes, and LOG this in the ERCOT logs. NOTIFY the QSE that the test is complete, and RELEASE the Resource from its VDI. Q#121 - Typical script to End Unannounced Unit Test: COMPLETE the ERCOT values on the Unannounced Seasonal Generation Verification Test via the NDCRC application on the ERCOT Website in a reasonable timeframe. ERCOT Website>Applications>NDCRC |
| Electronic Dispatch Instruction Confirmation | Issue electronic Dispatch Instruction when test is complete so that the initiation and completion times are correct: ISSUE: - Electronic Dispatch Instruction confirmation to QSE (see Desktop Guide Common to Multiple Desks Section 2.3) - Choose “UNANNOUNCED CAPACITY TEST” as the Instruction Type from Resource level - Initiation Time and Completion Time should be correct times - In text, state “RETEST” if applicable - Confirm with Market Participant electronic Dispatch Instruction received. When issuing a VDI or confirmation, ensure the use of three-part communication: - Issue the Operating Instruction - Receive a correct repeat back - Give an acknowledgement |
| Notify | When test is complete, include the following information: - Resource(s) - Date - Notification Time - Start time of 30 Minute Hold - Completion Time Send an e-mail to: - Operations Analysis - Shift Supervisors |
| Log | Log all actions. |

| Retest | - The QSE can have the opportunity to request another test as quickly as possible (at a time determined by ERCOT) and may request a retest up to two times per month - QSEs should submit retest requests to shiftsupv@ercot.com. - Any requested retest must take place within three Business Days after the request for retest - Any VDI issued as a result of a QSE-requested retest will be considered as an instructed deviation only for compliance purposes ISSUE: - Electronic Dispatch Instruction confirmation to QSE (see Desktop Guide Common to Multiple Desks Section 2.3) - Choose “UNANNOUNCED CAPACITY TEST” as the Instruction Type from Resource level - Initiation Time and Completion Time should be correct times - In text, state “RETEST” When issuing a VDI or confirmation, ensure the use of three-part communication: - Issue the Operating Instruction - Receive a correct repeat back - Give an acknowledgement |
| --- | --- |
| Demonstration Test | The QSE may demonstrate an increased value of HSL by operating the Generation Resource at an Output Schedule for at least 30 minutes. In order to raise an output schedule above the Seasonal HSL, the QSE may set the Resource telemetered HSL equal to its output temporarily for the purposed of the demonstration tests. The test must take place within three Business Days after the request. - Send an e-mail to: - Operations Analysis - Shift Supervisors |
| Notify | When test is complete, include the following information: - Resource(s) - Date - Notification Time - Start time of 30 Minute Hold - Completion Time Send an e-mail to: - Operations Analysis - Shift Supervisors |
| Log | Log all actions. |

## 5.1	Supplemental Ancillary Service Market

Procedure Purpose:  To open and execute a Supplemental Ancillary Service Market (SASM) for A/S when the DAM process is insufficient, when increasing A/S above DAM requirement, when there is infeasibility (stranded) caused by congestion, or failure to provide by the QSE.

| Protocol Reference | 3.16 | 4.5.2 | 5.2.2.2 | 6.4.9.1.1(3) |
| --- | --- | --- | --- | --- |
|  | 6.4.9.1.2(3) | 6.4.9.1.3(2) | 6.4.9.2 |  |
| Guide Reference |  |  |  |  |
| NERC Standard | TOP-002-4 R4, R4.4 |  |  |  |

| Version: 1 | Revision: 30 | Effective Date: December 31, 2020 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - There is no definitive time by which a SASM needs to start, however the SASM process must be completed at least one hour before the start of the Operating Hour (Example: for A/S needed in HE 14, SASM must be completed by HE 12). The SASM timeline depends on the triggering of the event. - ERCOT may not buy more of one A/S in place of the quantity of a different service. - A QSE may not self-arrange for A/S procured in response to Emergency Conditions. |
| SASM Failure | IF: - The SASM workflow controller fails during any stage of the run; THEN: - Manually create a savecase before workflow is shutdown (see Desktop Guide Common to Multiple Desks Section 2.16) - Press the Abort button to cancel the current run, - Press the Shut Down button, - Press the Start-up button, - Press the Run All button to restart the sequence IF: - The SASM workflow controller continues to fail; THEN: - Notify Market Operations |
| ### Procurement of Ancillary Services when DAM process is insufficient |  |
| Procurement Timeline | If the Day-Ahead Market is aborted the ancillary services have to be procured through SASM. The SASM must be executed in the Adjustment Period for the next day (which starts at 1800). ERCOT shall allow at least 1 hour between the issuance of the Watch and the beginning of this SASM. The SASM timeline is as follows Time X = Notify QSEs of time the SASM will begin Time X + 30min = Determine amount of A/S to be procured Time X + 35min = Execute SASM Time X + 45min = Notify QSEs with awards Time X + 60min = Validate COPs for A/S Resource Responsibility |
| 1 | IF: - The Day-Ahead Market is aborted; THEN: - Verify that the RUC Operator has issued a Watch, - Procure adequate Ancillary Services for the next operating day through a SASM, (Refer to Desktop Guide Resource Desk Section 2.4.4) |
| 2 | IF: - SASM did not procure the amount of A/S requested; THEN: - Notify the Shift Supervisor of the remaining A/S insufficiencies to be procured through RUC if necessary. |
| 3 | PREPARE: - Email with the following information: - SASM ID (use YYYYMMDDHHMMSS format) - Delivery Date - Delivery Hour - QSE and Resource name (if known) you are replacing the AS for - AS type(s) - MW amounts you are replacing - Total MW amount SASM has awarded - Verify PVT transferred SEND: - E-mail to the following distribution list - SASM |
| ### Increasing Ancillary Services for Extreme Cold Weather |  |
| NOTE | When temperatures or wind chill is expected to be below freezing for sustained periods and may impact load levels or generation availability, it may be necessary to procure additional Non-Spin and/or RRS. After DRUC has completed, determine if sufficient reserves are available to meet peak demand. |
| A/S Plan Increase Timeline | Time X is greater than two hours from the start of the Operating Hour for which the additional A/S capacity is required. The timeline is as follows: Time X = Notify QSEs, post on ERCOT Website Time X + 30 min = QSEs to update Offers Time X + 35 min= Execute the SASM Time X + 45 min = Publish results Time X + 60 min = Validate COPs and A/S schedules |
| 1 NOTE: SASM time XX:XX should be 30 minutes later than time hotline call issued | IF: - Temperature or wind chill is forecasted to be below 32°F, AND - Splunk: 11 COP vs MTLF ‘SS_HASL_MARGIN’ < 600 MW, OR - Temperature or wind chill is forecasted to be below 20°F, AND - Splunk: 11 COP vs MTLF ‘SS_HASL_MARGIN’ < 1300 MW; THEN: - Issue a Watch by making a Hotline call to QSEs - Post message on ERCOT Website - Notify Transmission Operator to make Hotline call to TOs - Procure additional Non-Spin and/or RRS through a SASM (Refer to Desktop Guide Resource Desk Section 2.4.3). Q#73 - Typical Hotline Script for Watch to Increase A/S and open SASM Typical ERCOT Website Posting for Watch to Increase A/S and open SASM: ERCOT is issuing a Watch due to the need to increase the system wide Ancillary Services requirement above what was procured in the Day-Ahead Market due to [state the reliability reason]. |
| 2 | WHEN: - SASM is complete; THEN: - Notify the Shift Supervisor if any insufficiencies exists to determine if procurement through RUC is needed (RUC as capacity, do not assign A/S to the Resource). THEN: - Cancel the Watch by making Hotline call to QSEs - Cancel posting on the ERCOT Website - Notify Transmission Operator to make Hotline call to TOs Q#74 - Typical Hotline Script to Cancel Watch to Increase A/S and SASM complete |
| 3 | PREPARE - Email with the following information: - SASM ID (use YYYYMMDDHHMMSS format) - Delivery Date - Delivery Hour - QSE and Resource name (if known) you are replacing the AS for - AS type(s) - MW amounts you are replacing - Total MW amount SASM has awarded - Verify PVT transferred SEND: - E-mail to the following distribution list: - SASM |
| LOG | Log all actions. |
| ### Increasing Ancillary Services for other reasons |  |
| A/S Plan Increase Timeline | Time X is greater than two hours from the start of the Operating Hour for which the additional A/S capacity is required. The timeline is as follows: Time X = Notify QSEs and post on the ERCOT Website Time X + 30 min = QSEs to update Offers Time X + 35min= Execute the SASM Time X + 45min = Publish results Time X + 60min = Validate COPs and A/S schedules |
| 1 NOTE: SASM time xx:xx should be 30 minutes later than time hotline call issued | IF: - More Ancillary Services are needed for one or more Operating Hours than were provided in the Day-Ahead; THEN: - Issue a Watch by making a Hotline call to QSEs - Post message on the ERCOT Website - Notify Transmission Operator to make Hotline call to TOs - Procure more Ancillary Services through a SASM (Refer to Desktop Guide Resource Desk Section 2.4.3). Q#73 - Typical Hotline Script for Watch to Increase A/S and open SASM Typical ERCOT Website Posting for Watch to Increase A/S and open SASM: ERCOT is issuing a Watch due to the need to increase the system wide Ancillary Services requirement above what was procured in the Day-Ahead Market due to [state the reliability reason]. |
| 2 | IF: - SASM did not procure the amount of A/S requested; THEN: - Notify the Shift Supervisor of the remaining A/S insufficiencies to be procured through RUC if necessary. IF: - SASM procured the additional A/S; THEN: - Cancel the Watch by making Hotline call to QSEs - Cancel posting on the ERCOT Website - Notify Transmission Operator to make Hotline call to TOs Q#74 - Typical Hotline Script to Cancel Watch to Increase A/S SASM complete |
| 3 | PREPARE: - Email with the following information: - SASM ID (use YYYYMMDDHHMMSS format) - Delivery Date - Delivery Hour - QSE and Resource name (if known) you are replacing the AS for - AS type(s) - MW amounts you are replacing - Total MW amount SASM has awarded - Verify PVT transferred SEND: - E-mail to the following distribution list: - SASM |
| ### Replacement of Ancillary Service Due to Infeasibility or Failure to Provide |  |
| NOTE | - Undeliverable/Infeasibility is when a QSE can not provide their A/S because ERCOT has asked them to move it due to congestion - Failure to provide is all other reasons |
| Infeasability Not Replaced Through a SASM | IF: - It is determined the infeasible amount is not significant enough to replace through a SASM; THEN: - Send to settlements by clicking “Settlement Snapshot”. Reference Desktop Guide Resource Desk section 2.4.1 |
| Undeliverable /Insufficient A/S Timeline | If the SASM is being executed to replace A/S capacity, either due to transmission constraints or QSE failure to provide, the timeline is as follows: Time X = Determine type and amount of A/S to procure. Notify QSEs and post on the ERCOT Website Time X + 30min = QSEs to update Offers Time X + 35min = Execute the SASM Time X + 45min = Publish Awards Time X + 60min = Validate COPs and A/S schedules |
| Infeasibility | IF: - A/S capacity allocated to a Resource is undeliverable based on system conditions; THEN: - Provide QSE the following information: - The amount by which the QSE must reduce the A/S currently allocated to each affected Resource, and - The start and stop times of the reduction Within the two-hour advance notice, the QSE may do one of the following: - Substitute capacity from other Resources, - Substitute capacity from other QSE using A/S trades, or - Replace all or part of the A/S through a SASM |
| Failure to Provide | IF: - Some or all of a QSE’s Resource-specific A/S capacity will not be available in Real-Time; THEN: - Substitute capacity to meet its responsibility, or - Request it be replaced through a SASM |
| 1 | IF: - A QSE is unable to provide the A/S capacity allocated to a specific Resource; THEN: - Determine if the infeasible/insufficient amount is significant enough to replace through SASM IF: - It is determined the infeasible/insufficient amount is not significant enough to replace through SASM; THEN: - Send to settlements by clicking “Settlement Snapshot”. Reference Desktop Guide Resource Desk section 2.4.2 IF: - It is determined that a SASM should be run; THEN: - Post on the ERCOT Website - Make a Hotline call to QSE’s - Notify Transmission Operator to make Hotline call to TO’s Q#72 - Typical Hotline Script to Execute a SASM for Failure to Provide/Infeasibility: Typical Posting: “ERCOT will execute a SASM at [xx:xx] for operating day [xx/xx/xx] for HE [xx-xx] for [type of A/S] MW [X], [X], [X]”. THEN: - Execute SASM (Refer to Desktop Guide Resource Desk Section 2.4.1 or 2.4.2). |
| 2 | IF: - SASM did not procure the amount of A/S requested; THEN: - Notify the Shift Supervisor of the remaining A/S insufficiencies to be procured through RUC if necessary. |
| 3 | IF: - A QSE is unable to provide their SASM awards; THEN: - Determine if there is time to open an additional SASM, AND - Send failure to provide notification. |
| 4 | Cancel posting on the ERCOT Website |
| 5 | PREPARE: - Email with the following information: - SASM ID (use YYYYMMDDHHMMSS format) - Delivery Date - Delivery Hour - QSE and Resource name (if known) you are replacing the AS for - AS type(s) - MW amounts you are replacing - Total MW amount SASM has awarded - Verify PVT transferred SEND: - E-mail to the following distribution list; - SASM |
| ### Daily Reconfiguration Supplemental Ancillary Services Market (RSASM) |  |
| Daily RSASM Timeline | (Refer to Desktop Guide Resource Desk Section 2.4.7) Reconfiguration Supplemental Ancillary Service Market (RSASM) allows QSEs to modify their Ancillary Services (AS) during the Operating Day. RSASMs are expected to be run daily for Operating Hours HE 13 thru 24.) The timeline is as follows: Time 08:45 = Events-AS_Resp_Check for 0900 (Start Now) commit to Database Time 09:00 = Execute SASM Time 09:15 = Notify QSEs with awards Time 09:30 = Validate COPs and A/S schedules |
| 1 | QSEs must have valid AS Offers of an amount equal to or greater than the requested reconfiguration amount; IF: - There are not sufficient AS Offers to cover the total requested amount; THEN: - Do not publish the RSASM, - Post an Operational Information message, low priority, on the ERCOT Website - Send email to SASM distribution list - QSEs will retain their original AS Supply Responsibility and should update their COPs accordingly Typical ERCOT Website Posting for Daily RSASM: The Daily RSASM will not be occurring due to insufficient AS Offers. |
| 2 | IF: - There are NO participating QSEs in the RSASM process; THEN: - Do not proceed with RSASM process - Post an Operational Information, low priority, message on the ERCOT Website - Send email to SASM distribution list Typical ERCOT Website Posting for Daily RSASM: The Daily RSASM will not be occurring due to zero participating QSEs. |
| 3 | IF: - There ARE participating QSEs in the RSASM THEN: - Proceed with the RSASM PREPARE: - Email with the following information: - SASM ID (use YYYYMMDDHHMMSS format) - Delivery Date - Delivery Hour - QSE - AS type(s) - MW amounts you are replacing - Total MW amount RSASM has awarded - Verify PVT transferred SEND: - E-mail to the following distribution list: - SASM |
| LOG | Log all actions. |

## 6.1	Manage Resource Forced & Maintenance Outages

Procedure Purpose:  Monitor and respond to Resource Forced and Maintenance outages.

| Protocol Reference | 3.1.4.2 | 3.1.4.4 | 3.1.4.5 | 3.1.4.6 |
| --- | --- | --- | --- | --- |
|  | 3.1.4.7 | 3.1.6.4 | 3.1.6.9 | 3.1.6.10 |
|  | 3.1.6.11 | 6.5.7.1.6 |  |  |
| Guide Reference | 2.4 |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 10 | Effective Date: December 31, 2020 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Forced Outages |  |
| NOTE | The QSE should: - Immediately notify ERCOT of a forced outage, - Enter the forced outage in the Outage Scheduler within two hours, - Update their COP within 1 hour - Update their telemetry. A call to the QSE may be necessary if the above are not complete within the designated time frame. |
| NOTE | ERCOT Operators can only make the following changes in the Outage Scheduler: - Remove actual start/end time if it is within 2 hours of the time the MP entered the outage, - Change status, - Add notes If a MP needs assistance or is unable to enter their outages, instruct them to Outage Coordination. Outage Coordination has an “Impersonation” certification that will allow them to make the needed changes. |
| ### Maintenance Outages |  |
| Definition | - Level 1- Equipment that must be removed from service within 24 hours to prevent a potential Forced Outage; - Level 2 - Equipment that must be removed from service within 7 days to prevent a potential Forced Outage; and - Level 3 - Equipment that must be removed from service within 30 days to prevent a potential Forced Outage. |
| Maintenance Outage with start time ≤ 24 Hours | IF: - A Maintenance Outage is received, review the outage if the scheduled start time is within the next 24 hours; THEN: - Discuss with the Transmission and Security Operator to determine if the outage will cause any reliability issues. |
| Accept Maintenance Outage with start time ≤ 24 Hours | IF: - No reliability issues identified; THEN: - Accept the Maintenance Outage. |
| Coordinate Maintenance Outage with start time ≤ 24 Hours | IF: - Reliability issues exist; THEN: - Coordinate the start of the outage with the QSE to ensure system reliability as long as the outage is allowed to start within 24 hours, AND - Accept the Maintenance Outage. |
| Coordinate Maintenance Level 2 and 3 Outage ≤ 24 Hours | REQUEST: - Support from the Transmission Desk or Shift Supervisor, IF: - Maintenance Level 2 and 3 outages are received with a start time of less than the next 24 hours, AND - Reliability issues exist; THEN: - Coordinate the start of the outage with the QSE to ensure system reliability as long as the outage is within the allowed Maintenance Level 2 (7 Days) and 3 (30 Days) outage criteria, - ERCOT Outage Coordination group may help coordinate a new start time. IF: - Reliability issues continue; THEN: - REQUEST the Operations Support Engineer investigate the development of a MP or TOAP (see section 4.6 Mitigation Plan) located in the Transmission Desk Procedure, - Accept the Maintenance Outage after coordination. |
| Maintenance Level 2 and 3 Outages | IF: - Maintenance Level 2 and 3 outages are received with a start time of greater than the next 24 hours; THEN: - The ERCOT Outage Coordination group has a process to review all Maintenance Level 2 and 3 outages without further action. |
| Log | Log all actions. |
| ### Forced Derate |  |
|  | IF: - A Resource’s capability is reduced by 10 MW or 5% of its Seasonal net max sustainable rating and is expected to last more than 48 hours; THEN: - The QSE must do the following: - Enter the derating into the Outage Scheduler as a Forced Outage, - Replace AS responsibility if applicable - Update their COP to reflect the changes, - Update the necessary telemetered parameters for the Resource. |
| ### Short-Notice Resource Outages |  |
|  | IF: - A newly proposed Resource Outage or proposed changes to a Planned Outage is submitted three days or less from the outage start date; THEN: - Notify Outage Coordination Group. |
| ### Opportunity Outages |  |
| NOTE | Opportunity Outages for Resources are a special category of Planned Outages that may be approved by ERCOT when a specific Resource has been forced Off-Line due to a Forced Outage and the Resource has been previously accepted for a Planned Outage during the next eight days. The QSE must give as much notice as practicable to ERCOT. |
| 1 | WHEN: - A Forced Outage occurs on a Resource that has an accepted or approved Outage scheduled within the following eight days, AND IF: - Approved by ERCOT; THEN: - The Resource may remain Off-Line and start the accepted or approved Outage earlier than scheduled. IF: - Reliability issues exist; THEN: - Reject the outage to ensure system reliability, IF: - No issues identified; THEN: - Approve the Outage as received, - Notify the QSE and Outage Coordination Group. |
| ### Returning from Planned Outage Early |  |
| Verify | IF: - A Resource returns from a Planned Outage early; THEN: - Coordinate with the Transmission and RUC Operators to determine if there is an associated transmission outage or any reliability issues exist. |
| Approve | IF: - No issues identified; THEN: - Notify the QSE of approval and to update their COP and Telemetry, - Notify the Outage Coordination Group. |
| Deny | IF: - Reliability issues, OR - Transmission is not available; THEN: - Coordinate between the TO and QSE to schedule a time agreeable to both parties for all facilities to be restored to service, - Notify the QSE within two hours, - Issue a VDI to stay Off-Line (see Desktop Guide Common to Multiple Desks Section 2.3) - Choose “Can Not Return Early From Outage” as the Instruction Type from Resource level. When issuing a VDI or confirmation, ensure the use of three-part communication: - Issue the Operating Instruction - Receive a correct repeat back - Give an acknowledgement |
| Log | Log all actions. |

| ### Advance Action Notice (AAN) |  |
| --- | --- |
| Definition | A type of Operating Condition Notice (OCN) that identifies a possible future Emergency Condition and describes future action ERCOT expects to take to address that condition unless the need for ERCOT action is alleviated by Qualified Scheduling Entity (QSE) and/or Transmission Service Provider (TSP) actions or by other system developments. |
| NOTE | ERCOT may issue an Advance Action Notice (AAN) in anticipation of a possible Emergency Condition. Any AAN will identify actions ERCOT expects to take to address the possible Emergency Condition unless the need for ERCOT action is alleviated by QSE and/or TSP actions taken, or by other system developments that occur, before a time stated in the AAN. |
| Time Periods | ERCOT shall issue the AAN a minimum of 24 hours prior to performing an OAE. Additionally, unless impracticable, the OAE should not be performed until eight Business Hours have elapsed following issuance of the AAN. ERCOT shall not issue an OSA under this Section unless it has first completed an OAE. |
| 1 | IF: - ERCOT forecasts an inability to meet applicable transmission reliability standards and has exercised all other reasonable options - There are Resources with approved or accepted Resource Outages, whose approval or acceptance could be withdrawn to meet the applicable transmission reliability standards THEN: - As instructed by the Shift Supervisor and in coordination with System Operations Management, Outage Coordination Management and Operations Support Management, issue an AAN. |
| Hotline Issue AAN | Hotline call will usually be made by the RUC Operator, the script below is for reference if needed: Q#126 - Typical Hotline Script for an AAN |
| Post | Coordinate with the Transmission Operator for the posting of the notice on the ERCOT Website Typical Posting Script: ERCOT issued an AAN due to a possible future Emergency Condition of [reserve capacity deficiency or reliability problem] beginning [date HE XX] until [date HE XX]. [Summary of actions ERCOT may take]. ERCOT may seek [amount of capacity] from an OAE and then make the OSA. On [date] at [xx:xx] ERCOT will execute an OAE if deemed necessary. |
| 2 | IF: - Conditions change THEN: - Update the AAN |
| Hotline Update AAN | Hotline call will usually be made by the RUC Operator, the script below is for reference if needed: Q#127 –Typical Hotline Script for an Update of an AAN |
| Updated Post | Coordinate with the Transmission Operator for the posting of the updated notice on the ERCOT Website Typical Posting Script: ERCOT has updated an AAN due to conditions changing and a possible future Emergency Condition of [reserve capacity deficiency or reliability problem] beginning [date HE XX] until [date HE XX]. [Summary of actions ERCOT may take]. ERCOT may seek [amount of capacity] from an OAE and then make the OSA. On [date] at [xx:xx] ERCOT will execute an OAE if deemed necessary. |
| Hotline Cancel AAN | WHEN: - ERCOT determines that the possible Emergency Condition has been alleviated by QSE or TSP action, by ERCOT action, or by other system developments; THEN: - Using the Hotline, cancel the AAN. Hotline call will usually be made by the RUC Operator, the script below is for reference if needed: Q#128 - Typical Hotline Script to cancel an AAN |
| Cancel Posting | WHEN: - ERCOT determines that the possible Emergency Condition has been alleviated by QSE or TSP action, by ERCOT action, or by other system developments. THEN: - Coordinate with the Transmission Operator to cancel the ERCOT Website message(s). |
| Log | Log all actions. |

## 7.1	Market Notifications

Procedure Purpose:  Guidelines for issuing Emergency Conditions and the four possible levels: Operating Condition Notices (OCN), Advisories, Watches, and Emergency Notices.

| Protocol Reference | 6.3.3 | 6.5.9.3 | 6.5.9.3.1 | 6.5.9.3.2 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.3.3 | 6.5.9.3.4 |  |  |
| Guide Reference | 4.2.1 | 4.2.2 | 4.2.3 | 4.2.4 |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 22 | Effective Date: December 31, 2020 |
| --- | --- | --- |

| Step | Action |  |
| --- | --- | --- |
| ### OCN |  |  |
| NOTE | Consider the severity of the potential Emergency Condition. The severity of the Emergency Condition could be limited to an isolated local area, or the condition might cover large areas affecting several entities, or the condition might be an ERCOT-wide condition potentially affecting the entire ERCOT System. |  |
| 1 | As instructed by the Shift Supervisor or when appropriate, issue an Operating Condition Notice (OCN). The OCN can be issued for any of the following reasons or to obtain additional information from TOs or QSEs. - There is a projected reserve capacity shortage that could affect reliability and may require more Resources - When extreme cold weather is forecasted approximately 5 days away - When extreme hot weather is forecasted approximately 5 days away - When an approaching Hurricane / Tropical Storm is approximately 5 days away - Unplanned transmission Outages that may impact reliability - When adverse weather conditions are expected, ERCOT may confer with TOs and QSEs regarding the potential for adverse reliability impacts and contingency preparedness |  |
| ### AAN |  |  |
| Definition | A type of Operating Condition Notice (OCN) that identifies a possible future Emergency Condition and describes future action ERCOT expects to take to address that condition unless the need for ERCOT action is alleviated by Qualified Scheduling Entity (QSE) and/or Transmission Service Provider (TSP) actions or by other system developments. |  |
| 1 | As instructed by the Shift Supervisor and in coordination with Outage Coordination and Operations Support, issue an Advance Action Notice (AAN). The AAN can be issued for any of the following reasons or to obtain additional information from TOs or QSEs. - There is a projected reserve capacity shortage that could affect reliability and may require more Resources - When extreme cold weather is forecasted approximately 5 days away - When extreme hot weather is forecasted approximately 5 days away - When an approaching Hurricane / Tropical Storm is approximately 5 days away - Unplanned transmission Outages that may impact reliability When adverse weather conditions are expected, ERCOT may confer with TOs and QSEs regarding the potential for adverse reliability impacts and contingency preparedness |  |
| ### Advisory |  |  |
| 1 | As instructed by the Shift Supervisor or when appropriate, issue an Advisory. The Advisory can be issued for any of the following reasons or to obtain additional information from TOs or QSEs. - When an approaching Hurricane / Tropical Storm is approximately 3 days away - When extreme cold weather is forecasted approximately 3 days away - When extreme hot weather is forecasted approximately 1 to 3 days away - When conditions are developing or have changed and more Ancillary Services will be needed to maintain current or near-term reliability - ERCOT may exercise its authority to increase Ancillary Service requirements above the quantities originally specified in the Day-Ahead Market in accordance with ERCOT procedures - When extreme weather or conditions require more lead-time than the normal Day-Ahead Market allows - Transmission system conditions are such that operations within security criteria are not likely or possible because of Forced Outages or other conditions unless a CMP exists - Loss of communications or control condition is anticipated or significantly limited - ERCOT may require information from QSEs representing Resources regarding the Resources’ fuel capabilities. Requests for this type of information shall be for a time period of no more than seven days from the date of the request |  |
| ### Watch |  |  |
| 1 | As instructed by the Shift Supervisor or when appropriate, issue a Watch. The Watch can be issued for any of the following reasons or to obtain additional information from TOs or QSEs. - A projected reserve capacity shortage is projected with no market solution available that could affect reliability - When an approaching Hurricane / Tropical Storm is approximately 1 day away - When extreme cold weather is projected for next day or current day - When extreme hot weather is projected for next day or current day - Conditions have developed such that additional Ancillary Services are needed in the Operating Period - Insufficient Ancillary Services or Energy Offers in the DAM - Market-based congestion management techniques embedded in SCED will not be adequate to resolve transmission security violations - Forced Outages or other abnormal operating conditions have occurred, or may occur that require operations with active violations of security criteria as defined in the Operating Guides unless a CMP exists - The SCED process fails to reach a solution, whether or not ERCOT is using one of the measures in Failure of the SCED Process. - The need to immediately procure Ancillary Services from existing offers - ERCOT may instruct TOs to reconfigure transmission elements as necessary to improve the reliability of the system |  |
| ### Emergency Notice |  |  |
| 1 | As instructed by the Shift Supervisor or when appropriate, issue an Emergency Notice. The Emergency Notice can be issued for any of the following reasons or to obtain additional information from TOs or QSEs. - Loss of Primary Control Center functionality - Load Resource deployment for North-Houston voltage stability - ERCOT cannot maintain minimum reliability standards (for reasons including fuel shortages) during the Operating Period using every Resource practically obtainable from the market - Immediate action cannot be taken to avoid or relive a Transmission Element operating above its Emergency Rating - ERCOT forecasts an inability to meet applicable reliability standards and it has exercised all other reasonable options - A transmission condition has been identified that requires emergency energy from any of the DC-Ties or curtailment of schedules - The Transmission Grid is such that a violation of security criteria as defined in the Operating Guides presents the threat of uncontrolled separation or cascading outages, large-scale service disruption to Load (other than Load being served from a radial transmission line) and/or overload of Transmission Elements, and no timely solution is obtainable through SCED or CMPs - When extreme cold weather is beginning to have an adverse impact on the System - When extreme hot weather is beginning to have an adverse impact on the System - When Hurricane / Tropical Storm is in the ERCOT Region and is beginning to have an adverse impact on the System |  |
| ### Operating Condition Script |  |  |
| Hotline | Hotline calls are usually made by Real-Time Operator, the scripts below are for reference if needed: Notify QSEs of Notice: Q#46 - Typical Hotline Script for Operating Condition [OCN/Advisory/Watch/Emergency] Notify Transmission Operator to make Hotline call to TOs |  |
| Post | - All notices must be posted on the ERCOT Website - For “free form” messages, the “Notice priority” will be specified as follows: - Operational Information/OCN type messages – low priority - Advisory/Watch type messages – medium priority - Emergency type messages – high priority |  |
| Hotline Cancellation | Q#47 - Typical Hotline Script to Cancel Operating Condition [OCN/Advisory/Watch/Emergency] |  |
| Log | Log all actions. |  |

## 7.2	Implement EEA Levels

Procedure Purpose:  To provide for maximum possible continuity of service while maintaining the integrity of the ERCOT system to reduce the chance of cascading outages.

| Protocol Reference | 6.5.7.6.2.2(1)(b) & (13) | 6.5.7.6.2.3(1) | 6.5.9.4 | 6.5.9.4.2 |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.5.3 | 4.5.3.1 | 4.5.3.2 | 4.5.3.3 |
|  | 4.5.3.4 |  |  |  |
| NERC Standard | EOP-011-1 R2, R2.1, R2.2, R2.2.2, R2.2.3, R2.2.3.1, R2.2.7 | IRO-001-4 R1 | TOP-001-4 R2 |  |

| Version: 1 | Revision: 22 | Effective Date: December 31, 2020 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - IF steady state system frequency falls below 59.91 Hz, ERCOT CAN immediately implement EEA 3. - IF steady state system frequency falls below 59.5 Hz, ERCOT SHALL immediately implement EEA 3. |
| ERS-30 | ERS with a thirty-minute ramp period. |
| ERS-10 | ERS with a ten-minute ramp period. |
| WS-ERS | Each Standard Contract Term(SCT) Request for Proposal (RFP) will state what time periods in that SCT weather sensitive can provide offers for. |
| TCEQ | When increased generation is requested during EEA events, Texas Commission on Environmental Quality (TCEQ) will exercise enforcement discretion for exceedances of emission limits as well as operational limits for power generating plants for Generators who exceed air permit limits in order to maximize generation for the duration of the EEA event. ERCOT General Council will send out a Market Notice each time ERCOT enters into an EEA with this reminder. |
| ### Implement EEA Level 1 |  |
| 1 | IF: - PRC < 2300 MW; THEN: - Deploy all available Non-Spin (if not previously deployed) (see Desktop Guide Resource Desk Section 2.1.1). - Determine whether system conditions require the deployment of ERS-30 (see Desktop Guide Resource Desk Section 2.3.2). - Make EEA 1 posting to the ERCOT Website - Use preformatted notice “EEA Level 1” |
| 2 | IF: - ERS-30 is deployed; THEN: - Also deploy WS ERS if available - Notify the Real-Time Operator when XML message has been completed. ERS must be deployed before hotline call is made. |
| 3 | Verify all measures have been implemented. |
| Log | Log all actions. |
| ### Implement EEA Level 2 |  |
| Note | ERCOT may declare an EEA Level 2 when the clock-minute average system frequency falls below 59.91 Hz for 15 consecutive minutes. |
| 1 | IF: - PRC < 1750 MW or unable to maintain system frequency at 59.91 Hz and is not projected to be recovered above 1750 MW within 30 minutes without the use of EEA Level 2; THEN: - Determine when system conditions require the deployment of ERS-30 / ERS-10 / Load Resources - (Do Not forget the WS ERS if available): - Deploy ERS-30 if not already done in EEA1 - Deploy ERS-10 - Deploy Load Resources Group 1 and/or 2 - Notify the Real-Time Operator when XML message has been completed. ERS / Load Resources/ must be deployed first before hotline call is made, - Desktop Guide Resource Desk (Section 2.2.1 for Load Resources; Section 2.3.2 for ERS). - Make EEA 2 posting to the ERCOT Website - Use preformatted notice “EEA Level 2” |
| ERS Time Period Changes | IF: - ERS Resources are deployed, and the Time Period is changing and if ERS is still needed; THEN: - Deploy next Time Period - Take into consideration the time requirement for the ERS-10 and ERS-30 - Notify the Real-Time Operator when XML message has been completed. ERS must be deployed before hotline call is made. |
| 2 | IF: Went straight to EEA Level 2; THEN: - Ensure tasks in EEA Level 1 are complete. |
| 3 | Verify all measures have been implemented. |
| Log | Log all actions. |
| ### Implement EEA Level 3 |  |
| Note | ERCOT may declare an EEA Level 3 when the clock-minute average system frequency falls below 59.91 Hz for 20 consecutive minutes. |
| PRC <1430 MW | ERCOT will declare an EEA Level 3 when PRC cannot be maintained above 1,430 MW. IF: - PRC <1430; THEN: - Make EEA3 posting to the ERCOT Website. ## Typical ERCOT Website Posting: At [time] ERCOT has entered EEA 3 for PRC less than 1430 MW. Firm Load Shed has not been instructed by ERCOT. |
| EEA3 Unable to Maintain 59.91 Hz or PRC <1000 MW | IF: - PRC <1000 MW and is not projected to be recovered above 1,000 MW within 30 minutes or unable to maintain system frequency at 59.91 Hz for 25 consecutive minutes; THEN: - Make EEA 3 posting to the ERCOT Website - Use preformatted notice “EEA Level 3” |
| 1 | Verify all measures have been implemented. |
| Log | Log all actions. |

## 7.3	Restore EEA Levels

Procedure Purpose:  To restore the ERCOT grid to normal state as system conditions warrant while recovering from an EEA event.

| Protocol Reference | 6.5.9.4.3 |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.5.3.5 |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 18 | Effective Date: December 31, 2020 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| RESERVES | 1430 MW of PRC must be restored within 90 minutes. |
| ### Restore Firm Load |  |
| 1 | IF: - Sufficient Regulation Service exist to control to 60 Hz, AND - PRC – Regulation Up Responsibility ≥ 1430 MW for the last 15 minutes; THEN: - Transmission Operator will restore firm load. |
| ### Move from EEA Level 3 to EEA Level 2 |  |
| 1 | IF: - Sufficient Regulation Service exist to control to 60 Hz, AND - PRC is ≥ 1750 MW, AND - All firm load have been instructed to be restored; THEN: - When instructed by the Real-Time Operator to recall Load Resources - Send XML message to recall Load Resources, (see Desktop Guide Resource Desk Section 2.2.4) - Make EEA 3 to EEA 2 posting to the ERCOT Website - Use preformatted notice |
| ### Move from EEA Level 2 to EEA Level 1 |  |
| 1 | IF: - The system can maintain PRC ≥ 2300 MW, AND - All Load Resources have been instructed to be restored; THEN: - Send XML message to recall 30 MIN then 10 MIN ERS (see Desktop Guide Resource Desk Section 2.3.3) - Make EEA 2 to EEA 1 posting to the ERCOT Website - Use preformatted notice |
| ### Move from EEA Level 1 to EEA 0 |  |
| 1 | IF: - The system can maintain PRC ≥ 2300 MW, AND - All RUC committed units secured in EEA 1 can be released, AND - Emergency energy from the DC Ties is no longer needed; THEN: - Terminate EEA 1 by posting to the ERCOT Website - Use preformatted notice “Return to Normal” |
| ### Recall Non-Spin and Cancel Watch |  |
| 1 | WHEN: - Avail_CAP_30Min ≥ 1000, AND - PRC is ≥ 2800 MW; THEN: - Coordinate with the Real Time Operator and recall half of the Non-Spin by sending a Zero MW XML message (Refer to Desktop Guide Resource Desk Section 2.1.3). WHEN: - Avail_CAP_30Min ≥ 1000, AND - PRC is ≥ 3000 MW; THEN: - Coordinate with the Real Time Operator and recall all of the Non-Spin by sending a Zero MW XML message (Refer to Desktop Guide Resource Desk Section 2.1.1). |
| Log | Log all actions. |

## 9.1	Respond to Miscellaneous Issues

Procedure Purpose: To provide a mutually agreed process for resolving Real-Time data issues between ERCOT and the Entities that provide data to ERCOT .  Also to record when a QSE is operating from their backup Control Conters and to notify the ERCOT Transmission Operator when a QSE notifies ERCOT of a change in status with any PSS or AVR.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 7.3.3 |  |  |  |
| NERC Standard | IRO-018-1(i) R1.3 | TOP-003-3 R5.2 | TOP-010-1(i) R1.3 |  |

| Version: 1 | Revision: 9 | Effective Date: December 31, 2020 |
| --- | --- | --- |

| Step |  |  | Action |  |
| --- | --- | --- | --- | --- |
| ### Real-Time Data Issues known by the QSE |  |  |  |  |
| NOTE |  |  | Manually replaced telemetry data is data entered by a QSE on their systems that is transmitted to ERCOT via ICCP in place of the normal points experiencing an issue. If Reliability issues can’t be resolved in a timely manner, ERCOT reserves the right to order the Resource off-line until the problem is resolved. |  |
| Notification of Telemetry Data Issue |  |  | IF: - Notified of a telemetry data issue (telemetry data will not be available or is unreliable for operational purposes; THEN: - The QSE should correct the telemetry data as soon as practicable, or, - Manually replace the data, if available. |  |
| Cannot Resolve |  |  | IF: - The QSE cannot resolve the telemetry data issue within two Business Day, fix the issue in a timely manner; THEN: - The QSE shall provide an estimated time of resolution. |  |
| ### Backup/Alternate Control Center Transfer |  |  |  |  |
| 1 |  |  | When notified by a QSE that they will be transferring to or from their backup/alternate control center, - Identify the [QSE] in the email notification - Send e-mail to “1 ERCOT System Operators” |  |
| Log |  |  | Log all actions. |  |
| ### QSE Issues |  |  |  |  |
| 1 |  | If a QSE is not satisfied with ERCOT Operations responses to their issues, refer them to their Wholesale Client Representative for clarification/resolution. |  |  |
| 2 |  | If the System Operator believes the issue is with ERCOT systems applications (ICCP down, etc.), notify the ERCOT Help Desk. |  |  |
| 3 |  | If a QSE is having an issue with ERCOT system applications (unable to access the portal, outage scheduler, etc.), instruct them to call the ERCOT Help Desk. |  |  |
| 4 |  | As time permits, notify the Shift Supervisor of any actions taken and unresolved issues. |  |  |
| Log |  | Log all actions. |  |  |
| ### Missing Data from ERCOT Website Postings |  |  |  |  |
| 1 |  | IF: - A call is received about data missing or data being incorrect, THEN: - Transfer call to the Help Desk, and - Notify the Shift Supervisor and Operations Support Engineer. |  |  |
| Log |  | Log all actions. |  |  |
| ### Courtesy Hotline calls for ERCOT Application Issues |  |  |  |  |
| 1 |  | WHEN: - Notified from IT support of application(s) issues that are causing Market Participants an inability to submit data to ERCOT; THEN: - Make a courtesy hotline to inform them. Q#76 - Typical Hotline script for Application Issues |  |  |
| ### Power System Stabilizers (PSS) & Automatic Voltage Regulators (AVR) |  |  |  |  |
| 1 | WHEN: - Notified by a QSE of a change in status with any PSS or AVR; THEN: - Transfer call to the ERCOT Transmission Operator. |  |  |  |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Frosch, Hartmann, Stone, and Barcalow | Preparers | November 10, 2010 |
| Frosch and Hartmann | Procedure writers and editors | November 29, 2010 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2010 |
| Frosch and Hartmann | Procedure writers and editors | January 26, 2011 |
| Frosch and Hartmann | Procedure writers and editors | March 23, 2011 |
| Frosch and Hartmann | Procedure writers and editors | April 20, 2011 |
| Frosch and Hartmann | Procedure writers and editors | May 10, 2011 |
| Frosch and Hartmann | Procedure writers and editors | June 6, 2011 |
| Frosch and Hartmann | Procedure writers and editors | July 18, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 30, 2011 |
| Frosch and Hartmann | Procedure writers and editors | September 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | October 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 16, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | April 25, 2012 |
| Frosch and Hartmann | Procedure writers and editors | May 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | May 30, 2012 |
| Barcalow, Frosch and Hartmann | Procedure writers and editors | July 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | August 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | October 26, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 26, 2013 |
| Frosch and Hartmann | Procedure writers and editors | May 28, 2013 |
| Frosch and Hartmann | Procedure writers and editors | July 8, 2013 |
| Cheng, Frosch and Hartmann | Procedure writers and editors | August 7, 2013 |
| Frosch and Hartmann | Procedure writers and editors | September 25, 2013 |
| Frosch and Hartmann | Procedure writers and editors | December 11, 2013 |
| Frosch, Gaddy and Hartmann | Procedure writers and editors | April 1, 2014 |
| Frosch, Gaddy and Hartmann | Procedure writers and editors | May 27, 2014 |
| Frosch and Hartmann | Procedure writers and editors | July 29, 2014 |
| Frosch and Hartmann | Procedure writers and editors | September 29, 2014 |
| Frosch and Hartmann | Procedure writers and editors | December 10, 2014 |
| Frosch and Thompson | Procedure writers and editors | December 19, 2014 |
| Frosch and Hartmann | Procedure writers and editors | February 25, 2015 |
| Frosch and Hartmann | Procedure writers and editors | April 29, 2015 |
| Frosch and Hartmann | Procedure writers and editors | July 13, 2015 |
| Hartmann and Gaddy | Procedure writers and editors | September 4, 2015 |
| Hartmann and Gaddy | Procedure writers and editors | September 25, 2015 |
| Frosch, Gaddy and Hartmann | Procedure writers and editors | October 27, 2015 |
| Hartmann and Gaddy | Procedure writers and editors | December 22, 2015 |
| Hartmann, Gaddy and Frosch | Procedure writers and editors | January 22, 2016 |
| Hartmann and Gaddy | Procedure writers and editors | February 23, 2016 |
| Hartmann and Gaddy | Procedure writers and editors | April 22, 2016 |
| Hartmann, Gaddy and Frosch | Procedure writers and editors | June 24, 2016 |
| Hartmann and Gaddy | Procedure writers and editors | December 23, 2016 |
| Hartmann, Gaddy and Frosch | Procedure writers and editors | March 27, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | May 26, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | June 23, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | July 24, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | October 27, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | December 22, 2017 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | February 22, 2018 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | April 27, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | August 24, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | December 21, 2018 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | October 29, 2019 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | December 20, 2019 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | January 27, 2020 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | February 24, 2020 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | June 25, 2020 |
| Hartmann, Gaddy, Cyphers, and Sheets | Procedure writers and editors | December 23, 2020 |

Manual Change History

| Procedure | Ver/Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All Sections | 1.0 / 0 | New procedures for all sections for Nodal implementation | November 28, 2010 |
| 3.1 3.4 3.5 3.7 4.1 5.1 5.1 5.2 6.1 7.2 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Deleted WGR section, in section “Monitor QSE Ancillary Services Obligation”, updated step Infeasible A/S Capacity from RUC & A/S Difference in COP Updated Note Updated step 3 Updated whole procedure Updated step 2 In section “Procurement of Ancillary Services due to DAM Failure”, “ERCOT Increases the Amount of Ancillary Services”, “Replacement of Ancillary Service Due to Infeasibility/Failure to Provide”, “Replacement of Ancillary Services in Real Time”, Updated step 1 Updated whole procedure In section “Timeline Deviations”, Updated 2nd Note In section “Returning from Planned Outage Early”, Updated Deny In section “Implement EEA Level 1”, Updated step 1 | December 1, 2010 |
| 3.1 3.7 3.8 5.1 | 1.0 / 2 1.0 / 2 1.0 / 0 1.0 / 2 | Deleted “Monitor Base Point Deviations” and updated “A/S Difference in COP” Deleted step Note, Deployment, & Termination New Procedure Updated “Procurement of Ancillary Services due to DAM Failure”, “ERCOT Increases the Amount of Ancillary Services” and “Replacement of Ancillary Service Due to Infeasibility/Failure to Provide“ step 3 and 4 | December 15, 2010 |
| 3.1 3.2 3.4 3.3 3.5 3.7 4.1 5.1 5.2 7.1 7.2 7.3 8.2 | 1.0 / 3 1.0 / 1 1.0 / 2 1.0 / 1 1.0/ 2 1.0 / 3 1.0 / 2 1.0 / 3 1.0 / 2 - / 1 - / 2 1.0 / 1 1.0 / 1 | Updated step Telemetered Status, step 1 in Manual Override Checks and removed workaround step “Real Time A/S shortage” in Monitor QSE Ancillary Services Obligation Updated all steps Updated steps “Deployment” and “Termination” Updated step 1 on “Cancelation” Updated all steps and added note Updated all steps Updated and deleted Notes and step 1 Updated “Procurement of Ancillary Services due to DAM Failure”, “ERCOT Increases the Amount of Ancillary Services”, “Replacement of Ancillary Service Due to Infeasibility/Failure to Provide“ step 3 and added note on Replacement of Ancillary Services in Real Time Updated Second Note on “Timeline Deviations” Updated Hotline on “Scripts” Updated Step 1 on ” Implement EEA Level 1” and “Implement EEA Level 2A” Updated Steps 1 on “Move from EEA Level 3 to EEA Level 2B” and “Cancel Watch” Deleted Site Failover Notification procedure & changed 8.3 to 8.2 | January 31, 2011 |
| 3.3 3.4 3.7 5.1 7.1 | 1.0 / 2 1.0 / 3 1.0 / 4 1.0 / 4 1.0 / 2 | Updated step 1 in “Watch” & step 1 in “Cancelation” Updated “Deployment” and “Termination” Updated “Issue Watch & Deploy Non-Spin” and “Recall Non-Spin” Updated step 2 in “Replacement of Ancillary Service Due to Infeasibility/Failure to Provide” Updated “Watch” and “Emergency Notice” | March 25, 2011 |
| 3.5 7.1 7.3 | 1.0 / 3 1.0 / 3 1.0 / 2 | Updated NERC Recovery Criteria Updated step 1 in Watch and Emergency Notice and step Post Updated 1st and 2nd script in Restore Firm Load, Updated 1st in Move From EEA Level 3 to EEA Level 2B | April 22, 2011 |
| 3.8 3.9 5.1 8.1 | 1.0 / 0 1.0 / 1 1.0 / 5 1.0 / 1 | Added new procedure Changed section number from 3.8 to 3.9 Updated steps 3-5 in Replacement of A/S due to Infeasibility/Failure to Provide, deleted Replacement of A/S in Real-Time Change section name, updated step 2 & 3 | May 11, 2011 |
| 3.3 3.4 3.6 3.7 3.8 7.1 | 1.0 / 3 1.0 / 4 1.0 / 1 1.0 / 5 1.0 / 1 1.0 / 4 | Updated step 1 in Advisory and Watch Updated step Deployment Updated step 1 Updated step Deploy Non-Spin & Post & Deploy Load Resources & Post Updated step Post Updated all steps | June 8, 2011 |
| 3.3 3.4 3.5 3.8 4.1 5.2 7.1 7.2 7.3 9.1 | 1.0 / 4 1.0 / 5 1.0 / 4 1.0 / 2 1.0 / 3 1.0 / 3 1.0 / 5 1.0 / 3 1.0 / 3 1.0 / 1 | Updated step 1 in Advisory and Watch Updated step on Deployment Updated step on PRC Below 2300 Added step Termination, updated steps on Post and Cancel Posting Updated step 2 in Approve/Reject Decommitment QSE Requests in Operating Period Updated step 1 and deleted 2nd note in Timeline Deviations Updated step Watch Updated all steps Updated all steps Added Market Participant Backup Control Center Transfer procedure | July 20, 2011 |
| 3.3 3.4 5.1 7.1 7.2 7.3 8.2 | 1.0 / 5 1.0 / 6 1.0 / 6 1.0 / 6 1.0 / 4 1.0 / 4 1.0 / 2 | Updated step 1 in Cancelation Updated Note, added steps Additional Deployment & Commit, updated steps Note & Deployment Updated 1st Note Added projected reserve capacity shortage and Extreme Hot Weather in Watch Updated 2nd Note, step 1 & 2 in EEA Level 1, step 1 in EEA Level 2A, added note in EEA Level 2B Updated step 1 in Cancel Watch Updated 4th Note and step 1 | September 1, 2011 |
| 7.2 7.3 8.1 | 1.0 / 5 1.0 / 5 1.0 / 2 | Combined EEA 2A & B per NPRR 379 Combined EEA 2A & B per NPRR 379 Updated step 2 | October 1, 2011 |
| 3.1 3.4 3.6 3.8 3.9 4.1 5.1 8.1 | 1.0 / 4 1.0 / 7 1.0 / 2 1.0 / 3 1.0 / 2 1.0 / 4 1.0 / 7 1.0 / 3 | Changed desktop guide reference in Monitor QSE Ancillary Services Obligation Updated step Commit Updated procedure title and all steps Updated steps 1 & Termination, added step 2 Deleted procedure due to protocol change Added 2nd Note Updated steps 1 – 3 in Procurement of A/S due to DAM Failure, steps 1 -2 in ERCOT Increased the Amount of A/S, steps 1 & 4 in Replacement of A/S Due to Infeasibility/Failure to Provide Added Note 2 & 3 | November 1, 2011 |
| 3.3 3.4 3.7 3.8 7.1 | 1.0 / 6 1.0 / 8 1.0 / 6 1.0 / 4 1.0 / 7 | Add Note in Watch Added second Note Added second Note Added Note Updated Post in “Scripts” All procedures in this manual have been reviewed. | December 15, 2011 |
| 1.2 3.1 3.4 4.1 5.1 | 1.0 / 1 1.0 / 5 1.0 / 9 1.0 / 5 1.0 / 8 | Updated Scope Updated Monitor QSE A/S Obligation procedure Updated 1st Note Updated steps 1 & 2 Updated step 2, 3 & 4 | January 19, 2012 |
| 2.1 3.1 3.3 3.4 3.5 3.7 3.8 4.1 5.1 7.1 7.2 7.3 8.2 9.1 | 1.0 / 1 1.0 / 6 1.0 / 7 1.0 / 10 1.0 / 5 1.0 / 7 1.0 / 5 1.0 / 6 1.0 / 9 1.0 / 8 1.0 / 6 1.0 / 6 1.0 / 3 1.0 / 2 | Updated paragraph 4 Updated Desktop Guide references Updated Desktop Guide references Updated Desktop Guide references Updated Desktop Guide references Updated Desktop Guide references Updated Desktop Guide references Updated 1st Note & step 1 Updated Desktop Guide references, step 3s & 4 Updated step 1 of Watch Updated Desktop Guide references Updated Desktop Guide references Updated Desktop Guide references Updated QSE Override, QSE unable to Override, Backup/Alternate Control Center Transfer, QSE Issues & step Power System Stabilizers (PSS) & Automatic Voltage Regulators (AVR) | March 1, 2012 |
| 2.1 3.1 3.5 3.6 3.7 4.1 5.1 7.1 9.1 | 1.0 / 2 1.0 / 7 1.0 / 6 1.0 / 3 1.0 / 6 1.0 / 7 1.0 / 10 1.0 / 9 1.0 / 3 | Changed TSP/DP to TO Updated step Not Dispatchable to SCED Deleted Potential DCS Event, changed section number for System Failures Changed section number Changed section number & added step 3 Updated step 1 Updated information needed in e-mail Updated all step 1’s Changed Shift Engineer to Ops Support Engineer | May 1, 2012 |
| 3.3 3.4 | 1.0 / 8 1.0 / 11 | Updated to reflect changes in the TAC approved Non-Spin document Updated to reflect changes in the TAC approved Non-Spin document | May 14, 2012 |
| 7.2 7.3 | 1.0 / 7 1.0 / 7 | Updated EILS to ERS per NPRR 451 Updated EILS to ERS per NPRR 451 | June 1, 2012 |
| 1.3 4.1 6.1 7.1 7.2 7.3 8.2 | 1.0 / 1 1.0 / 8 1.0 / 2 1.0 / 10 1.0 / 8 1.0 / 8 1.0 / 4 | Removed ERCOT Shift Supervisor paragraph Added Desktop Guide to VDI reference Added Desktop Guide to VDI reference and updated Maintenance Level 2 and 3 outages Updated all step 1’s Added Desktop Guide to VDI reference, updated step 1 Implement EEA Level 2 and added ERS Updated step 1 Move from EEA Level 3 to EEA Level 2 Updated 4th note | July 16, 2012 |
| 3.1 7.2 | 1.0 / 8 1.0 / 9 | Updated step ONTEST Updated step 1 of Implement EEA Level 1 | August 29, 2012 |
| 2.2 7.2 8.1 | 1.0 / 1 1.0 / 10 1.0 / 4 | Added Hotline Call Communication Updated Implement EEA Level 1 step 2, Implement EEA Level 2 step 1 and ERS Business Hour Changes Updated 1st Note, step 1, 2 & 3. Added step 4 and Log All procedures in this manual have been reviewed. | November 1, 2012 |
| 3.3 3.4 3.6 3.7 4.1 5.1 7.3 | 1.0 / 9 1.0 /12 1.0 / 9 1.0 / 7 1.0 / 8 1.0 / 11 1.0 / 9 | Non-Spin deployment messages are now automated Non-Spin deployment messages are now automated Non-Spin deployment messages are now automated Non-Spin deployment messages are now automated Updated steps 1 & 2 Updated steps Note, Procurement Timeline & 1. Added new procedure, Daily Reconfiguration SASM Updated step 1 of Cancel Watch | March 1, 2013 |
| 3.3 3.5 5.1 5.2 7.1 7.2 7.3 8.1 9.1 | 1.0 / 10 1.0 / 4 1.0 / 12 1.0 / 4 1.0 / 11 1.0 / 11 1.0 / 10 1.0 / 5 1.0 / 4 | Removed notice builder reference Removed notice builder reference Updated steps 1 & 5 in ERCOT Increased the amount of A/S & steps in Daily Reconfiguration SASM Updated step 1 Updated Scripts Removed notice builder reference & Updated Scripts Removed notice builder reference Updated Script Updated Script | June 1, 2013 |
| 3.1 7.1 | 1.0 / 9 1.0 / 12 | Deleted 1st Note, added step Log, moved Not Dispatchable to SCED, Control Block Up/Down, & Real-Time RRS A/S Shortages to Real-Time procedure, deleted Manual Override Checks Updated step 1 in Watch & Emergency Notice | July 15, 2013 |
| 5.1 5.2 | 1.0 / 13 1.0 / 5 | Updated 1st Note for R4 changes, Daily SASM Timeline Updated 1st Note for R4 changes | August 9, 2013 |
| 5.1 6.1 | 1.0 / 14 1.0 / 3 | Updated 1st Note, Daily SASM Timeline Updated to reflect SCR770 changes | September 27, 2013 |
| 3.1 3.2 3.3 3.5 3.6 3.7 4.1 5.1 6.1 6.2 7.1 7.2 7.4 8.2 9.1 | 1.0 / 10 1.0 / 2 1.0 / 11 1.0 / 5 1.0 / 10 1.0 / 8 1.0 / 10 1.0 / 15 1.0 / 4 1.0 / 1 1.0 / 13 1.0 / 12 1.0 / 1 1.0 / 5 1.0 / 5 | Added Monitor QSE A/S Obligation Title Updated Evaluate Request Updated step Log Updated step Log Updated step Log Updated step Log Updated step 3 Updated step Log Updated Accept Maintenance Outage, Coordinate Maintenance Outage, Coordinate Maintenance Level 2 and 3 and Log Updated step Log Updated step Log Updated last step and added Log Updated step Log Updated step Log Updated and added step Log All procedures in this manual have been reviewed. | December 13, 2013 |
| 3.4 3.5 3.74.1 6.1 7.1 7.2 7.3 8.1 | 1.0 / 13 1.0 / 7 1.0 / 9 1.0 / 11 1.0 / 5 1.0 / 14 1.0 / 13 1.0 / 11 1.0 / 6 | Updated VDI information Updated for NPRR542 Updated VDI information Updated VDI information Updated VDI information Updated to incorporate NPRR542 Updated ERS, Media appeal, TCEQ, VDI language, and moved steps to RUC desk Updated Reserves and step 1 Updated step 1 & 3, added step 5 | April 4, 2014 |
| 2.2 3.1 3.3 3.4 4.1 5.1 5.2 7.1 | 1.0 / 2 1.0 / 11 1.0 / 12 1.0 / 14 1.0 / 12 1.0 / 16 1.0 / 6 1.0 / 15 | Added VDIs to Master QSEs Updated Monitor QSE AS Obligations steps Updated steps in Watch Updated title, step Deployment & Termination Updated step 1 & 2 Updated section titles & steps Updated Timeline Deviations Added Note, updated Advisory & Watch | June 1, 2014 |
| 3.1 3.4 3.6 3.7 4.1 5.1 6.1 7.2 7.3 | 1.0 / 12 1.0 / 15 1.0 / 11 1.0 / 10 1.0 / 13 1.0 / 17 1.0 / 6 1.0 / 14 1.0 / 12 | Updated Desktop references Updated Desktop references Updated Desktop references Updated Desktop references Updated Desktop reference Updated steps 1, 4-6 in Replacement of A/S due to infeasibility or failure to provide, & Desktop references Updated Forced Derate Updated Desktop references Updated Desktop references | August 1, 2014 |
| 7.1 | 1.0 / 16 | Updated Scripts | October 1, 2014 |
| 3.4 3.6 4.1 6.2 | 1.0 / 16 1.0 / 12 1.0 / 14 1.0 / 2 | Deleted Note & added Log Changed title & added Rio Grande Valley Re-worded procedure Added step 2 All procedures in this manual have been reviewed | December 15, 2014 |
| 5.1 | 1.0 / 18 | Added new procedure “Increasing A/S for Extreme Cold Weather and changed title for “Increasing A/S for other reasons and updated timeline | December 22, 2014 |
| 2.2 3.3 3.4 3.5 3.6 3.7 5.1 5.2 6.1 | 1.0 / 3 1.0 / 13 1.0 / 8 1.0 / 13 1.0 / 11 1.0 / 0 1.0 / 19 1.0 / 7 1.0 / 7 | Added Dispatch and VDI definitions Combined section 3.3 & 3.4 into one procedure Updated section number Updated section number Updated section number and Corrected VDI vs. Dispatch Instruction New, moved procedure from Shift Supervisor desk Added SASM Failure and reformatted Deleted procedure Corrected VDI vs. Dispatch Instruction | March 1, 2015 |
| 3.2 3.3 3.5 3.6 5.1 7.1 8.1 9.1 | 1.0 / 3 1.0 / 14 1.0 / 14 1.0 / 12 1.0 / 20 1.0 / 17 1.0 / 7 1.0 / 6 | Updated step Evaluate Request Combined step in Watch Updated GTL to GTC Updated step 2 Moved scripts to script procedure Moved scripts to script procedure Combined Note steps & moved scripts to script procedure Moved script to script procedure | May 1, 2015 |
| 5.1 | 1.0 / 21 | Added a “Q” for QSE scripts Updated per NPRR 682 | July 15, 2015 |
| 5.1 | 1.0 / 22 | Updated per NPRR 701 | September 9, 2015 |
| 5.1 | 1.0 / 23 | Updated Reconfiguration Supplemental Ancillary Service Market (RSASM) | October 1, 2015 |
| 3.5 | 1.0 / 15 | Updated to include calls for deployment and recalls of Load Resources. | October 30, 2015 |
| 3.3 3.4 3.7 5.1 7.1 7.2 7.3 8.1 9.1 | 1.0 / 15 1.0 / 9 1.0 / 1 1.0 / 24 1.0 / 18 1.0 / 15 1.0 / 13 1.0 / 8 1.0 / 7 | Updated Advisory step Issue Advisory Typical MIS Posting Updated Watch step Issue Watch & Deploy Off-Line Non-Spin Typical MIS Posting Updated Watch step Recall Non-Spin Typical MIS Posting Updated step 1 Typical MIS Posting Updated Unannounced Resource Testing step Testing Rules and Scripts Typical Script Updated Increasing Ancillary Services for Extreme Cold Weather step 1 & 2 Typical Scripts Updated Increasing Ancillary Services for other reasons step 1 & 2 Typical Scripts Updated Daily RSASM step 1 & 2 Typical MIS Postings Updated Operating Condition Script step Hotline Q#46 Updated Operating Condition Script step Hotline Cancellation Q#47 First Note, Updated Implement EEA Level 2 step 1, and Implement NPRR708 for EEA Updated Move from EEA Level 2 to EEA Level 1 step 1 Updated step 2 Q#75 Updated Courtesy Hotline Calls for ERCOT Application Issues step 1 Q#76 All procedures in this manual have been reviewed | December 31, 2015 |
| 2.1 3.6 5.1 7.2 8.1 | 1.0 / 3 1.0 / 13 1.0 / 25 1.0 / 6 1.0 / 9 | Updated System Operator Responsibilities and Authority Updated NERC Standard Reference Updated step WS-ERS Updated Replacement of Ancillary Service Due to Infeasibility or Failure to Provide step 1 with Hotline call Changed Business Hours to Time Periods Updated Alert Levels | February 1, 2016 February 10, 2016 |
| 1.3 5.1 | 1.0 / 2 1.0/ 26 | Removed Interchange Coordinator Updated Failure to Provide script title Q#72 | March 1, 2016 |
| 5.1 | 1.0 / 27 | Added Increasing Ancillary Services for Extreme Cold Weather step 1 MIS Posting Typical Script Added Increasing Ancillary Services for other reasons step 1 MIS Posting Typical Script | April 29, 2016 |
| 2.1 2.2 3.7 6.1 7.1 | 1.0 / 4 1.0 / 4 1.0 / 2 1.0 / 8 1.0 / 19 | Updated for COM-002-4 Updated for COM-002-4 Updated for COM-002-4 Updated for COM-002-4 Updated for COM-002-4 | June 30, 2016 |
| 9.1 | 1.0 / 8 | Added Real-Time Data Issues known by the QSE Deleted Telemetry Issues that could affect SCED and/or LMPs All procedures in this manual have been reviewed | December 30, 2016 |
| 1.3 2.1 7.1 7.2 | 1.0 / 3 1.0 / 5 1.0 / 20 1.0 / 17 | Deleted Roles/Responsbilities section Updated section Updated title and all 1st steps Added Implement EEA Level 3 step PRC < 1375 MW | March 31, 2017 |
| 5.1 7.2 | 1.0 / 28 1.0 / 18 | Updated Increasing Ancillary Services for Extreme Cold Weather step 1 Updated Implement EEA Level 3 step PRC <1375 | June 1, 2017 |
| 7.2 | 1.0 / 19 | Updated 1st Note and Implement EEA Level 3 steps | June 30, 2017 |
| 3.7 7.2 | 1.0 / 3 1.0 / 20 | Updated note Added note Implement EEA Level 2 and Level 3 | July 28, 2017 |
| 5.1 | 1.0 / 29 | Updated Replacement of Ancillary Service Due to Infeasibility or Failure to Provide steps | October 31, 2017 |
| 8.2 | 1.0 / 6 | All procedures in this manual have been reviewed Updated Primary Control Center 4th note | December 28, 2017 |
| 3.4 3.7 3.8 | 1.0/ 10 1.0 / 0 1.0 / 3 | Updated Procedure Purpose, added SCED/RLC/LFC (AGC) Failures heading and ICCP, MIS, and Outage Scheduler outages section Added new procedure Deploying Non-Spin for Critical Inertia Level for 3.7 Updated Unannounced Resource Testing procedure 3.7 to 3.8 | February 28, 2018 |
| 2.2 | 1.0 / 5 | Updated procedure purpose | May 1, 2018 |
| 3.8 | 1.0 / 4 | Added Notify and Log step Moved Unannounced Testing scripts to Scripts | August 31, 2018 |
| 7.3 | 1.0 / 14 | Added Log All procedures in this manual have been reviewed | December 28, 2018 |
| 7.3 8.1 | 1.0 / 15 1.0 / 10 | Updated Move from EEA Level 1 to EEA 0 step 1 Added steps | November 1, 2019 |
| 7.2 7.3 | 1.0 / 21 1.0 / 16 | Updated MSSC Updated MSSC All procedures in this manual have been reviewed | January 1, 2020 |
| 3.3 3.6 3.7 7.3 8.2 | 1.0 / 16 1.0 / 14 1.0 / 1 1.0 / 17 1.0 / 7 | Clarified RUC-commits/decommits Clarified RUC-commits/decommits Clarified RUC-commits/decommits Clarified RUC-commits/decommits Updated Primary Control Center steps 1 & 3 | January 31, 2020 |
| 8.2 | 1.0 / 8 | Updated Title and removed Alternate Control Center | February 28, 2020 |
| 2.1 6.1 7.1 | 1.0 / 6 1.0 / 9 1.0 / 21 | Added Advance Action Notice per NPRR930 Added Advance Action Notice section per NPRR930 Added Advance Action Notice section per NPRR930 | July 1, 2020 |
| 1.1 3.3 3.4 3.7 3.8 5.1 6.1 7.1 7.2 7.3 9.1 | 1.0 / 1 1.0 / 17 1.0 / 11 1.0 / 2 1.0 / 5 1.0 / 30 1.0 / 10 1.0 / 22 1.0 / 22 1.0 / 18 1.0 / 9 | Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 All procedures in this manual have been reviewed | December 31, 2020 |