- Power Operations Bulletin # 984

ERCOT has posted/revised the Reliability Risk Desk manual.

A copy of the procedure can be found at:

- http://www.ercot.com/mktrules/guides/procedures/index.html

## 4.6  Solar Forecast

Procedure Purpose:  To monitor Maxar Solar forecast during normal and abnormal operations. It is presumed that under normal operating conditions that the solar forecast override will very rarely be used. However, there are certain scenarios that might dictate an override.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 2 | Effective Date: June 16, 2021 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Maxar Solar Forecast |  |
| NOTE | If solar forecast is invalid or appears to have other discrepancies; - Contact Operations Analysis Engineer to do further analysis and determine if it is necessary to override Solar forecast; - Solar Forecast can only be overwritten by Maxar |
| Maxar Solar Forecast | IF: - The Maxar Solar Forecast seems invalid; THEN: - Notify an Operations Analysis Engineer for adjustments, - E-mail the information to: - 1 ERCOT Shift Supervisors - Operations Analysis Reference Display: Curtailment Tool Forecast section and other necessary displays. |
| NOTE | The projected solar ramp rate (PSRR) calculation is such that it will revert to using persistence (PSRR=0) if the actual solar HSL has been ramping in the opposite direction of the PSRR value for more than 35 minutes (7 intervals). RLC will set the PSRR to 0 to minimize the impact and then cancel the flag after the PSRR is forecasting the ramp to be the same as the actual ramp again. |
| Intra-Hour solar Forecast | IF: - Alarmed, make sure frequency isn’t rapidly declining and solar hasn’t turned direction and is ramping very fast (above 300-400 MW per 5 minutes and causing frequency to decline below 59.95 Hz). If frequency does drag and regulation is exhausted, notify the Real-Time Desk for manually running SCED. Watch the PSRR and solar ramp to help inform the Real-Time Desk; THEN: - Notify an Operations Analysis Engineer to do further analysis, - E-mail the information to: - Operations Analysis - 1 ERCOT Shift Supervisors |
| LOG | Log all actions. |

## 4.7  Weather Forecast Errors

Procedure Purpose:  Make corrections to errors in the weather forecast data (in EMS) to contribute to reliable system performance.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 1 | Effective Date: June 16, 2021 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Weather Forecast |  |
| Weather Forecast | IF: - The weather forecast seems invalid; THEN: - Notify the ERCOT Meteorologist and/or Load Forecasting team, - E-mail the information to: - 1 ERCOT EMMS Production - Load Forecasting Department - 1 ERCOT Shift Supervisors |
| LOG | Log all actions. |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Hartmann, Gaddy, Self, and Frosch | Preparers | January 24, 2017 |
| Hartmann, Gaddy and Frosch | Procedure writers and editors | March 27, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | May 26, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | June 23, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | July 24, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | September 27, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | December 22, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | February 22, 2018 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | March 26, 2018 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | April 27, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | May 25, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | August 24, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | December 21, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | January 25, 2019 |
| Hartmann, Gaddy and Pence | Procedure writers and editors | July 29, 2019 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | October 29, 2019 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | December 20, 2019 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | January 27, 2020 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | February 24, 2020 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | June 25, 2020 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | September 23, 2020 |
| Hartmann, Gaddy, Cyphers, and Sheets | Procedure writers and editors | December 23, 2020 |
| Hartmann, Gaddy, Cyphers, and Sheets | Procedure writers and editors | April 29, 2021 |
| Hartmann, Gaddy, Cyphers, and Sheets | Procedure writers and editors | June 11, 2021 |

Manual Change History

| Procedure | Ver/Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All | 1.0 / 0 | New procedures | January 30, 2017 |
| 2.1 3.1 4.4 5.1 7.1 7.2 9.1 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Updated System Operator Responsibility and Authority Updated Up Ramp Event step 2 Updated Panhandle Region Updated Reliability Risk Desk performs STNET Study Updated title and all 1st steps Updated Implement EEA Level 3 steps Updated Title | March 31, 2017 |
| 3.1 | 1.0 / 2 | Updated Down Ramp Event step 1, 2 & 3 Updated Up Ramp Event step 1 & 2 | June 1, 2017 |
| 3.1 7.2 | 1.0 / 3 1.0 / 2 | Updated Down Ramp Event step 2 Updated 1st note, step 1 changed to EEA Level 3 | June 30, 2017 |
| 7.2 | 1.0 / 3 | Added note Implement EEA Level 2 and Level 3 | July 28, 2017 |
| 7.2 | 1.0 / 4 | Updated Implement EEA Level 3 | September 29, 2017 |
| 8.1 | 1.0 / 1 | All procedures in this manual have been reviewed Updated Primary Control Center 4th note | December 28, 2017 |
| 3.3 | 1.0 / 1 | Updated Day Ahead RRS Sufficiency Monitoring, moved Real-time RRS Sufficiency Monitoring down, added Look Ahead Critical Inertia Level Sufficiency Monitoring and Real-time Critical Inertia Level Sufficiency Monitoring | February 28, 2018 |
| 9.1 | 1.0 / 2 | Updated Note | March 30, 2018 |
| 2.2 | 1.0 / 1 | Updated procedure purpose | May 1, 2018 |
| 5.1 | 1.0 / 2 | Added Phase Angles steps | May 31, 2018 |
| 5.1 | 1.0 / 3 | Updated and named step to Voltage contingencies | August 31, 2018 |
| 4.1 4.2 | 1.0 / 1 1.0 / 1 | Updated procedure purpose, added note and updated step Updated procedure purpose, added note and updated step All procedures in this manual have been reviewed | December 28, 2018 |
| 4.2 | 1.0 / 2 | Updated steps | January 31, 2019 |
| 3.1 4.1 | 1.0 / 3 1.0 / 2 | Deleted all steps Monitor Large Ramp Events Added Intra-Hour Wind Forecast and added Note Updated STWPF Selection Change due to forecast vs. output deviation and added Note | August 1, 2019 |
| 4.1 4.7 5.1 | 1.0 / 3 1.0 / 0 1.0 / 4 | Removed Weather Forecast Created section Weather Forecast Errors Updated Voltage Contingencies | November 1, 2019 |
| 7.2 7.3 | 1.0 / 5 1.0 / 1 | Updated MSSC Updated MSSC All procedures in this manual have been reviewed | January 1, 2020 |
| 3.3 5.1 7.3 8.1 | 1.0 / 2 1.0 / 5 1.0 / 2 1.0 / 2 | Clarified RUC-commits/decommits Clarified RUC-commits/decommits Clarified RUC-commits/decommits Updated Primary Control Center steps 1 & 3 | January 31, 2020 |
| 3.4 4.1 4.3 4.4 4.5 4.6 8.1 | 1.0 / 1 1.0 / 4 1.0 / 1 1.0 / 2 1.0 / 1 1.0 / 1 1.0 / 3 | Updated 3rd Note Updated 1st Note Updated Procedure Purpose & steps Updated Procedure Purpose & steps Updated Procedure Purpose Updated Procedure Purpose, Title & steps Updated Title and removed Alternate Control Center | February 28, 2020 |
| 2.1 7.1 | 1.0 / 2 1.0 / 2 | Added Advance Action Notice per NPRR930 Added Advance Action Notice section per NPRR930 | July 1, 2020 |
| 2.1 | 1.0 / 3 | Updated System Operator Responsibility and Authority | October 1, 2020 |
| 4.5 6.1 7.1 9.1 | 1.0 / 2 1.0 / 1 1.0 / 3 1.0 / 3 | Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 & added Note Updated for NPRR1039 All procedures in this manual have been reviewed | December 31, 2020 |
| 3.3 | 1.0 / 3 | Updated Real-time Critical Inertia Level Sufficiency Monitoring step 3 | May 6, 2021 |
| 4.6 4.7 | 1.0 / 2 1.0 / 1 | Updated for SCR 811 Updated Load Forecast email | June 16, 2021 |