- Power Operations Bulletin # 993

ERCOT has posted/revised the Reliability Unit Commitment manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

- http://www.ercot.com/mktrules/guides/procedures/index.html

## 2.3	Publish A/S Requirements and Review System Conditions

Procedure Purpose:  To publish and verify daily Ancillary Service requirements are posted to the market.

| Protocol Reference | 4.2.1.1(1) | 4.2.1.1(2) | 4.2.1.2(2) | 4.3(2) |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | BAL-002-2 R2 | EOP-011-1 R2, R2.1, R2.2, R2.2.3, R2.2.3.2, R2.2.3.3 | TOP-002-4 R4, R4.4 |  |

| Version: 1 | Revision: 18 | Effective Date: July 31, 2021 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - Review and update A/S Requirements must be completed prior to 0500. - The Shift Supervisor must verify the posted ancillary service requirements for the 1st day of the month. |
| ### Review Weather Data Information |  |
| 1 | REVIEW the Weather Data for the next operating day in the EMS. |
| 2 | REVIEW REFERENCE DISPLAY: EMS Applications>Weather Details>Real Time Displays>Weather Forecast Directory IF: - The Last Weather Source Update or Last Weather Read is less than one (1) hour old; THEN: - Using the usual sources, review the weather forecast for at least two days out. IF: - The data update or read is more than one (1) hour old; THEN: - Notify the Shift Supervisor and the Help Desk. |
| 3 | Evaluating the weather forecast for several days ahead is needed to help determine if there is a potential for fuel supply problems. The trigger will usually be an extreme weather event which will cause temperatures to be below freezing for an extended period of time, though there could be other reasons. It may be necessary to consider fuel switching and optimize fuel supply if a reliability issue exists. |
| Fuel Switching | IF: - Notified of fuel limitations; THEN: - Consult with Supervisor and determine if reliability concerns exits - Identify potential transmission issues - Identify potential capacity issues IF: - Reliability concerns exists; THEN: - Consider fuel switching options (gas to oil) if capability exists. |
| Optimize Fuel Supply | IF: - A particular fuel supply is at risk; THEN: - Consult with Supervisor and determine if reliability concerns exits - Identify potential transmission issues - Identify potential capacity issues IF: - Reliability concerns exists; THEN: - Consider RUC committing Resources with fuel that is not at risk. |
| ### Review and Select Load Forecast |  |
| 1 | - Review and Select load forecast for next day (Refer to Desktop Guide RUC Section 2.17. |
| 2 | IF: - There is a large difference between the load forecasts, AND - There is uncertainty on which load forecast is correct; THEN: - Call the Load Forecasting group for guidance on updating the weather or load forecast. |
| 3 | Notify by e-mail the following distribution lists of the issue: - Load Forecasting Department - 1 ERCOT Shift Supervisors |
| ### Publish A/S Requirements |  |
| 1 | REFERENCE DISPLAY: Market Participation > Physical Market > AS Market > AS Plan Before 04:00, verify the hourly ERCOT system total A/S requirements for each of the following, for each hour of the operating day: - Reg-Up; - RRS. - Reg-Down; - Non-Spin. |
| 2 | REFERENCE DISPLAY: Market Participation > Monitoring > Event Manager > Events Search / Filter for AS_OBLIGATION_CALC Before 06:00, verify the hourly ERCOT system total A/S requirements have been automatically published at 04:55: IF: - Status indicates complete, no further action is necessary, OR - Status indicates anything else; THEN: - Change status to start now and select submit to database poke point. |
| ### Increasing A/S Requirements before A/S Obligations Publish |  |
| NOTE | This procedure would be performed when it has been determined that additional A/S is needed, such as to support a weather event. |
| NOTE | If an Emergency Condition may exist that would adversely affect system reliability, ERCOT may change the percentage of Load Resources that are allowed to provide RRS from the monthly amounts determined previously. |
| NOTE | If the operation day D is identified as a High Forecast Variability Day on day D-2 (2-day advance). Two days prior to the OD identified as a High Variability Day, the GMS team will update NSRS quantities and the updated AS plan will be reflected in the DAM Ancillary Service Plan report. The Control room will be notified two days in advance of a High Variability Day and the corresponding AS plan. Before 04:00, verify the updated High Variability RRS and Non Spin quantities that will be applicable. Notify the GMS Production Support Team immediately if requirements are not correct in the AS Plan. |
| 1 | REFERENCE DISPLAY: Market Participation > Physical Market > AS Market > AS Plan Before 04:00, increase the hourly ERCOT system total A/S requirements for each requirement needed for each hour of the next operating day: - Reg-Up; - RRS. - Reg-Down; - Non-Spin. |
| 2 | REFERENCE DISPLAY: Market Participation > Monitoring > Event Manager > Events Search / Filter for AS_OBLIGATION_CALC Before 06:00, verify the hourly ERCOT system total A/S requirements have been automatically published at 04:55: IF: - Status indicates complete, no further action is necessary, OR - Status indicates anything else; THEN: - Change status to start now and select submit to database poke point. |
| 3 | IF: - The A/S requirements were increased, THEN: - The next day will copy the new A/S requirements unless you return the A/S requirements to the A/S Plan requirements for the month. REFERENCE DISPLAY: - Market Participation > Physical Market > AS Market > AS Plan Before 04:00 update the A/S requirements. |
| NOTE | Refer to the A/S requirements for the current month’s A/S Plan if no changes are required. |
| ### Priority Outages |  |
| 1 | A Priority Outage is one that affects generation. Prior to 1200: - Review the Outage Notes for the next Operating Day, make lists of Priority Outages, sorted by the affected TOs, - The file is located in P:\DAY AHEAD – TDSP PRIORITY OUTAGE NOTIFICATION, - Email the Priority Outages to the appropriate TO using the email addresses provided in the RUC Desktop Guide Section 2.22, - Copy and paste the information into the body of the email, - The Subject line should read “Priority Outages”, “<Company Name>”, “<Date>” - At the bottom of each email, be sure to include a Confidentiality Notice and your signature, - Ensure each document has a Note which states to notify ERCOT within 30 minutes of the Actual Start and Actual End times for the Priority Outages, - If email is unavailable, follow the same guidelines using the Fax Machine, - Place hard copies in Daily Log File. |
| ### Blackstart Availability |  |
| 1 | REFERENCE DISPLAY: Market Participation > Physical Market > Market Participant Submissions > Availability Plan ERCOT SharePoint > System Operations – Control Center > Documents > Blackstart Availability REVIEW: - Blackstart Availability Plan for next operating day (OD+1 tab) IF: - Blackstart Availability Plan for next operating day is missing THEN: - Call the QSE and request them to submit their Blackstart Availability Plan for next operating day - Update the Blackstart Availability spreadsheet located on SharePoint |
| Log | LOG when completed and any additional actions taken. |
| ### Verification of Published A/S Requirements |  |
| NOTE | This step may be completed after 0600. |
| 1 | VERIFY by spot-checking the following information posted to the ERCOT Website for the next operating day (or two days if two-day Ahead market is in effect) is posted. - Planned Transmission line and equipment outages for the operating day. - ERCOT Website; Grid; Transmission; Consolidated Transmission Outage Report - Weather assumptions used to provide the system conditions forecast. - ERCOT Website; Data Products; Markets; Weather assumptions - The hourly ERCOT System total Ancillary Service requirements for Regulation Down – REGDN, Regulation Up – REGUP, Responsive Reserve – RRS, and Non-spinning Reserve – NSPIN. - ERCOT Website; Data Products; Markets; DAM Ancillary Service Plan. |
| Log | LOG any significant problems including any action taken. |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Frosch, Hartmann, Barcalow, Lowrie, and Stone | Preparers | November 10, 2010 |
| Frosch and Hartmann | Procedure writers and editors | November 29, 2010 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2010 |
| Frosch and Hartmann | Procedure writers and editors | January 26, 2011 |
| Frosch and Hartmann | Procedure writers and editors | March 23, 2011 |
| Frosch and Hartmann | Procedure writers and editors | April 20, 2011 |
| Frosch and Hartmann | Procedure writers and editors | June 6, 2011 |
| Frosch and Hartmann | Procedure writers and editors | July 18, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 22, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 30, 2011 |
| Frosch and Hartmann | Procedure writers and editors | October 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 16, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | April 25, 2012 |
| Frosch and Hartmann | Procedure writers and editors | July 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | October 26, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 26, 2013 |
| Frosch and Hartmann | Procedure writers and editors | May 28, 2013 |
| Frosch and Hartmann | Procedure writers and editors | July 8, 2013 |
| Cheng, Frosch and Hartmann | Procedure writers and editors | August 7, 2013 |
| Frosch and Hartmann | Procedure writers and editors | December 11, 2013 |
| Frosch and Hartmann | Procedure writers and editors | December 20, 2013 |
| Frosch, Gaddy and Hartmann | Procedure writers and editors | April 1, 2014 |
| Frosch, Gaddy and Hartmann | Procedure writers and editors | May 27, 2014 |
| Frosch and Hartmann | Procedure writers and editors | September 29, 2014 |
| Frosch and Hartmann | Procedure writers and editors | December 10, 2014 |
| Frosch and Hartmann | Procedure writers and editors | February 25, 2015 |
| Frosch and Hartmann | Procedure writers and editors | April 29, 2015 |
| Hartmann and Gaddy | Procedure writers and editors | July 13, 2015 |
| Hartmann and Gaddy | Procedure writers and editors | September 25, 2015 |
| Hartmann and Gaddy | Procedure writers and editors | December 22, 2015 |
| Frosch, Hartmann and Gaddy | Procedure writers and editors | January 22, 2016 |
| Hartmann and Gaddy | Procedure writers and editors | February 23, 2016 |
| Frosch, Hartmann and Gaddy | Procedure writers and editors | June 24, 2016 |
| Hartmann and Gaddy | Procedure writers and editors | September 26, 2016 |
| Hartmann and Gaddy | Procedure writers and editors | October 31, 2016 |
| Hartmann and Gaddy | Procedure writers and editors | December 23, 2016 |
| Hartmann, Gaddy and Frosch | Procedure writers and editors | March 27, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | May 26, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | June 23, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | September 27, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | December 22, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | February 22, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | March 26, 2018 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | April 27, 2018 |
| Hartmann, Gaddy, Ballew | Procedure writers and editors | May 25, 2018 |
| Hartmann, Gaddy, Ballew | Procedure writers and editors | August 24, 2018 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | December 21, 2018 |
| Hartmann, Gaddy, Luker and Frosch | Procedure writers and editors | March 26, 2019 |
| Hartmann, Gaddy and Pence | Procedure writers and editors | May 13, 2019 |
| Hartmann, Gaddy and Pence | Procedure writers and editors | May 28, 2019 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | October 29, 2019 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | December 20, 2019 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | January 27, 2020 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | February 24, 2020 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | May 26, 2020 |
| Hartmann, Gaddy, Cyphers and Frosch | Procedure writers and editors | June 25, 2020 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | July 28, 2020 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | October 26, 2020 |
| Hartmann, Gaddy, Cyphers, and Sheets | Procedure writers and editors | December 23, 2020 |
| Hartmann, Gaddy, Cyphers, and Sheets | Procedure writers and editors | June 11, 2021 |
| Hartmann, Gaddy, Cyphers, and Sheets | Procedure writers and editors | July 8, 2021 |
| Hartmann, Gaddy, Cyphers, and Sheets | Procedure writers and editors | July 28, 2021 |

Manual Change History

| Procedure | Ver/Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All Sections | 1.0 / 0 | New procedures for all sections for Nodal implementation | November 28, 2010 |
| 2.3 2.4 3.2 3.3 4.3 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Added new procedure “Phase Shifter Tap Settings” Updated Note Updated step “Monitor” Updated steps “Commit/De-Commit”, “Violated Constraints” and “HRUC Committed” Updated step “Review”, “A/S Insufficiency from DAM” and “DRUC Committed” | December 1, 2010 |
| 2.3 4.2 4.3 4.4 | 1.0 / 2 1.0 / 1 1.0 / 2 1.0 / 1 | Updated “Review Weather Data Information” step 2 Added steps “DRUC Committed for Capacity Shortage” and “Projected Reserve Capacity Shortage” Updated steps “DAM Timeline Deviation, DAM Failure, DRUC Delay & Software Failure” change to step 1 | December 15, 2010 |
| 3.2 4.3 4.1 4.4 6.1 | 1.0 / 2 1.0 / 3 1.0 / 2 - / 2 1.0 / 1 | Updated step “HRUC Committed Units”, “Manual Commitment”, added steps “Excess Generation” and “Canceling RUC commitments” Updated step DRUC Committed Units”, “Manual Commitment, added steps “Excess Generation” and “Canceling RUC commitments” Updated step “DAM Timeline Deviation”, DAM Failure”, DRUC Delay” Updated scripts Updated script | January 31, 2011 |
| 3.2 3.3 3.5 4.3 4.4 6.1 | 1.0 / 3 1.0 / 2 - / 0 - /4 - / 3 1.0 / 2 | Updated step Canceling RUC Commitments Deleted HRUC Timeline Deviation and updated HRUC Failure/Timeline Deviation Added new section Updated step Canceling RUC Commitments Updated step DAM Timeline Deviation in DAM Timeline Deviation/Failure Timeline not Met in section DRUC Timeline Deviation/Failure Updated Watch and Emergency Notice | March 25, 2011 |
| 2.5 3.2 3.3 4.3 6.1 6.2 | 1.0 / 1 1.0 / 4 1.0 / 3 1.0 / 5 1.0 / 3 1.0 / 1 | Updated Monthly MIS Posting Updated step Canceling RUC Commitments Updated step Failure Updated step Canceling RUC Commitments Updated step 1 in Watch and Emergency Notice Updated step & removed step Market Notification | April 22, 2011 |
| 3.2 3.5 4.3 4.4 5.2 6.1 | 1.0 / 5 1.0 / 1 1.0 / 6 1.0 / 4 1.0 / 1 1.0 / 4 | Updated steps HRUC Committed Units and Approval Updated all steps Updated step Approval Updated step DAM Timeline Deviation Updated step Long Lead Times Updated all steps | June 8, 2011 |
| 2.3 3.1 3.2 3.5 4.2 4.3 4.4 4.5 | 1.0 / 3 1.0 / 1 1.0 / 6 1.0 / 2 1.0 / 2 1.0 / 7 1.0 / 5 1.0 / 1 | Added steps for Publish A/S Requirements Updated Load Forecast step Updated steps Excess Generation, A/S Insufficiency from SASM, Violated Constraints and Approval Corrected title to match TOC and updated 1st note Updated Load Forecast step Updated Approval step Added subtitles, step DRUC Delay & step 1 Moved section 2.6 to 4.5 | July 20, 2011 |
| 2.3 2.4 3.2 3.3 4.3 6.1 7.1 | 1.0 / 4 - / 1 1.0 / 7 1.0 / 4 1.0 / 8 1.0 / 5 1.0 / 1 | Added Note to Increasing A/S Requirements before A/S Obligations Publish Added information on RMR Resource Commitment Updated step Excess Generation, added RMR Resources, RMR Commitment and Canceling RUC Commitments Updated step Commit/Decommit Resources by VDI Updated step Canceling RUC Commitments Added Projected Reserve Capacity Shortage to Watch Updated 4th note | August 24, 2011 |
| 3.2 4.2 4.3 6.1 7.1 | 1.0 / 8 1.0 / 3 1.0 / 9 1.0 / 6 1.0 / 2 | Added Note, updated step Hotline, Post and added step Cancel Deleted step RMR, updated Manual Commitment, deleted Note Updated Note Added Extreme Hot Weather in Watch Updated 3rd note and step 1 | September 1, 2011 |
| 2.3 2.4 3.1 3.2 4.3 4.4 4.5 4.6 4.5 Original | 1.0 / 5 1.0 / 2 1.0 / 2 1.0 / 9 1.0 / 10 1.0 / 6 1.0/ 0 1.0 / 0 1.0 / 2 | Deleted Phase Shifter Tap Settings Deleted step Resources Updated step Manual Commitment in Tasks prior to execution of HRUC Updated step RMR Resources and Canceling RUC Commitments Updated step for Canceling RUC Commitments Moved A/S Insufficiency in DAM to section 4.5 & DAM Failure to section 4.6 Moved A/S Insufficiency in DAM to section 4.5 & deleted Increase A/S Capacity needs about Day-Ahead Requirements Moved from section 4.5 Deleted procedure (was section 4.5), duplicate | November 1, 2011 |
| 2.3 6.1 | - / 6 1.0 / 7 | Removed Invalid SPS/RAP due to Outage Updated Post in “Notifications” All procedures in this manual have been reviewed. | December 15, 2011 |
| 1.2 3.5 4.3 4.6 | 1.0 / 1 1.0 / 3 1.0 / 11 1.0 / 3 | Updated Scope Updated all steps Updated A/S Insufficiency from DAM Updated desktop guide section | January 19, 2012 |
| 2.1 2.3 2.5 3.1 3.2 3.3 3.7 4.2 4.3 4.4 4.5 4.6 5.2 6.1 7.1 | 1.0 / 1 1.0 / 7 1.0 / 2 1.0 / 3 1.0 / 10 1.0 / 5 1.0 / 0 1.0 / 4 1.0 / 12 - / 7 1.0 / 3 1.0 / 4 1.0 / 2 1.0 / 8 1.0 / 3 | Updated 4th Paragraph Updated Desktop Guide reference Updated Monthly MIS Posting Updated Desktop Guide reference Updated Desktop Guide references and step After Approval Added step Create Save Case Added new procedure Projected Capacity Reserve Shortage with no Market Solution Updated Desktop Guide references Updated Desktop Guide references and added step After Approval Added step 2 Updated Desktop Guide reference Updated Desktop Guide reference Added step Create Save Case Updated step 1 of Watch Updated Desktop Guide references | March 1, 2012 |
| 1.1 2.1 3.1 3.2 3.3 4.2 4.3 5.1 5.2 6.1 8.1 | 1.0 / 1 1.0 / 2 1.0 / 4 1.0 / 11 1.0 / 6 1.0 / 5 1.0 / 13 1.0 / 1 1.0 / 3 1.0 / 9 1.0 / 1 | Changed Shift Engineer to Operations Support Engineer Changed TSP,DSP to TO Changed Shift Engineer to Operations Support Engineer Changed Shift Engineer to Operations Support Engineer Changed Shift Engineer to Operations Support Engineer Changed Shift Engineer to Operations Support Engineer and added WRUC Changed Shift Engineer to Operations Support Engineer and Manual Commitment Changed Shift Engineer to Operations Support Engineer Changed Shift Engineer to Operations Support Engineer and updated step Long Lead Times for NPRR402 Updated OCN, Advisory, Watch, Emergency Notice sections Changed Shift Engineer to Operations Support Engineer | May 1, 2012 |
| 1.1 1.3 2.3 3.1 3.2 3.3 4.2 4.3 4.4 5.2 6.1 7.1 | 1.0 / 2 1.0 / 1 1.0 / 8 1.0 / 5 - / 12 - / 7 - / 6 - / 14 - / 8 1.0 / 4 1.0 / 10 1.0 / 4 | Updated last paragraph, HRUC Removed ERCOT Shift Supervisor paragraph Updated step 3, added Fuel Switching and Optimize Fuel Supply & 2nd note Changed Shift Engineer to Operations Support Engineer Updated HRUC Committed Units Updated Create Save Case Updated Manual Commitment on 14:30 each day Updated DRUC Committed Units Updated step 2 in Delay of DRUC Updated Create Save Case Updated all step 1’s Updated 4th note | July 16, 2012 |
| 2.2 3.2 4.3 | 1.0 / 1 1.0 / 13 1.0 / 15 | Added Hotline Call Communication Updated Manual Commitment and Validate Updated Manual Commitment and Validate All procedures in this manual have been reviewed. | November 1, 2012 |
| 2.3 4.3 4.6 | 1.0 / 9 1.0 / 16 1.0 / 5 | Added Blackstart Availability Updated Review Updated steps SASM not able to Procure all A/S Requested & Cancel Emergency Notice | March 1, 2013 |
| 3.1 3.2 3.3 3.5 3.7 4.3 4.4 4.5 4.6 5.2 6.1 | 1.0 / 6 1.0 / 14 1.0 / 8 1.0 / 4 1.0 / 1 1.0 / 17 1.0 / 9 1.0 / 4 1.0 / 6 1.0 / 5 1.0 / 11 | Updated step Deselect Contingencies Updated step Monitor, Excess Generation, Hotline, & Cancel Updated step Failure & Create Save Case Updated step REG/RRS Updated all steps Updated 1st Note, A/S Insufficiency from DAM, Excess Generation &DRUC Committed from Capacity Shortage Updated all steps Updated all steps Updated all steps Updated step Create Save Case Updated Notifications | June 1, 2013 |
| 3.5 4.3 4.4 4.6 6.1 | 1.0 / 5 1.0 / 18 1.0 / 10 1.0 / 7 1.0 / 12 | Correct typo in script Correct typo’s in scripts Updated Delay of DRUC steps Corrected reference in desktop guide Updated step 1 in Watch & Emergency Notice | July 15, 2013 |
| 3.2 3.3 | 1.0 / 15 1.0 / 9 | Updated step HRUC Committed Units, Manual Commitment, HRUC Decommitted Resources & Approval Updated step Create Save Case | August 9, 2013 |
| 3.2 4.3 5.1 5.2 | 1.0 / 16 1.0 / 19 1.0 / 2 1.0 / 6 | Updated steps Violated Constraints, HRUC Committed Units, RMR Commitment & Manual Commitment Updated steps Violated Constraints, DRUC Committed Units & Manual Commitment Updated titles Updated Violated Constraints, Disapprove & Log. Deleted Long Lead Times, All procedures in this manual have been reviewed. | December 13, 2013 |
| 3.3 4.4 4.6 6.1 | 1.0 / 10 1.0 / 11 1.0 / 8 1.0 / 13 | Updated for NPRR542 Updated for NPRR542 Updated for NPRR542 Updated for NPRR542 and 529 | January 1, 2014 |
| 2.3 3.2 3.3 3.6 4.3 6.2 6.3 | 1.0 / 10 1.0 / 17 - / 11 1.0 / 1 1.0 / 20 1.0 / 0 1.0 / 2 | Updated Review and Select Load Forecast Updated step System Summary, HRUC Committed Units & VDI information Updated VDI information Added Manual Commit of a Resource & Canceling RUC Commitments Updated VDI information Updated DRUC Committed Units & VDI information Added new EEA procedure Change section number from 6.2 to 6.3 | April 4, 2014 |
| 2.2 2.3 2.4 2.5 3.2 3.6 4.5 4.6 5.2 6.1 | 1.0 / 2 1.0 / 11 1.0 / 3 1.0 / 3 1.0 / 18 1.0 / 2 1.0 / 5 1.0 / 9 1.0 / 7 1.0 / 14 | Added VDIs to Master QSEs Added Note to Increasing A/S before Publishing Added Note Updated Monthly MIS Posting step Updated step A/S Infeasibility Updated step 1 Updated step A/S Insufficiency Offers Updated DAM Failure Updated step Disapprove Added Note, updated Advisory & Watch | June 1, 2014 |
| 3.2 6.1 | 1.0 / 19 1.0 / 15 | Updated Undeliverable A/S Capacity, added STNET Study and title change on VSAT and RUC perform AC Analysis Updated Generic Script | October 1, 2014 |
| 3.2 3.2 4.3 6.2 | 1.0 / 20 1.0 / 20 1.0 / 21 1.0 / 1 | Updated step STNET Study, HRUC Committed Units & Manual Commitment Updated STNET Study, HRUC Committed Units & Manual Commitment Updated step DRUC Committed Units & Manual Commitment Added step All procedures in this manual have been reviewed | December 15, 2014 |
| 2.2 2.3 3.2 3.3 3.6 4.3 4.4 6.2 | 1.0 / 3 1.0 / 12 1.0 / 21 1.0 / 12 1.0 / 3 1.0 / 22 1.0 / 12 1.0 / 2 | Added Dispatch & Verbal Dispatch Instruction Deleted Meterlogix number. Updated Priority Outages Corrected VDI vs. Dispatch Instruction and Manual Commitment Corrected VDI vs. Dispatch Instruction Corrected VDI vs. Dispatch Instruction Updated step Manual Commitment & corrected VDI vs. Dispatch Instruction Updated DAM Timeline Deviation Corrected VDI vs. Dispatch Instruction | March 1, 2015 |
| 3.2 3.3 3.5 3.6 3.7 4.3 4.4 4.5 4.6 6.1 | 1.0 / 22 1.0 / 13 1.0 / 6 1.0 / 4 1.0 / 2 1.0 / 23 1.0 / 13 1.0 / 6 1.0 / 10 1.0 / 16 | Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Updated to implement NPRR679 Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure | May 1, 2015 |
| All Sections 5.2 | 1.0 / 1 1.0 / 8 | Added a “Q” for QSE scripts Updated Disapprove with email notification | July 15, 2015 |
| 3.6 | 1.0 / 5 | Updated 1st note | October 1, 2015 |
| 2.5 3.3 3.5 3.7 4.3 4.4 4.5 4.6 6.1 | 1.0 / 4 1.0 / 14 1.0 / 7 1.0 / 3 1.0 / 24 1.0 / 14 1.0 / 7 1.0 / 11 1.0 / 17 | Updated Monthly MIS Posting Added step After 20th of the month Updated step Last Day of the Month Updated HRUC Failure/Timeline Deviation step Failure Q#79 & Q#80 Updated step REG/RRS – RUC Committed Shortages Q#81& Q#82 Updated step Hotline Q#83 Updated step Cancel Q#84 Updated step A/S Insufficiency from DAM Q#86 Updated step Excess Generation Typical Script Q#87 & Q#88 Updated DAM Timeline Deviation step DAM Timeline Deviation Q#92 Updated Title DRUC Delay Updated DRUC Delay step DRUC Completes By 18:00 Q#94 Updated DRUC Delay step 2 Typical Script Q#96 Updated step A/S Insufficiency Offers Q#97 Updated step DAM Complete with A/S Q#98 Updated step Cancel Watch Q#99 Updated step DAM Failure Q#100 Updated step Cancel Watch Q#101 Updated Title Operating Condition Script Updated Operating Condition Script step Hotline Q#46 Updated Operating Condition Script step Hotline Cancellation Q#47 All procedures in this manual have been reviewed | December 31, 2015 |
| 2.1 3.6 3.6 3.7 | 1.0 / 3 1.0 / 0 1.0 / 6 1.0 / 4 | Updated System Operator Responsibility and Authority Added new Assigning Ancillary Services procedure Change section number from 3.6 to 3.7 Change section number from 3.7 to 3.8 Updated Hotline Q#83 Updated Cancel Q#84 | February 10, 2016 |
| 1.3 5.2 | 1.0 / 2 1.0 / 9 | Removed Interchange Coordinator Added step EDI step | March 1, 2016 |
| 2.1 2.2 2.4 3.1 3.2 3.3 3.6 3.7 4.3 5.2 6.1 6.2 | 1.0 / 4 1.0 / 4 1.0 / 4 1.0 / 7 1.0 / 23 1.0 / 15 1.0 / 1 1.0 / 7 1.0 / 25 1.0 / 10 1.0 / 18 1.0 / 3 | Updated for COM-002-4 Updated for COM-002-4 Added steps Note, Resources, 1, 2, & 3 Updated RMR Consideration &Manual Commitment steps Updated for COM-002-4 Updated for COM-002-4 Updated for COM-002-4 Updated for COM-002-4 & noteUpdated for COM-002-4 Updated for COM-002-4 Updated for COM-002-4 Updated for COM-002-4 | June 30, 2016 |
| 3.4 | 1.0 / 1 | Added Resources Startup Time Less Than One Hour | September 30, 2016 |
| 6.2 | 1.0 / 5 | Deleted step 2 | November 2, 2016 |
|  |  | All procedures in this manual have been reviewed | December 30, 2016 |
| 1.3 2.1 2.5 3.7 5.2 6.1 6.3 8.1 | 1.0 / 3 1.0 / 5 1.0 / 5 1.0 / 8 1.0 / 11 1.0 / 19 1.0 / 3 1.0 / 2 | Deleted section 1.3 Updated for IRO-001-4 Updated procedure purpose Updated Monthly MIS Posting Updated note Updated Manual Dispatch to take a Unit Off-Line step 1 Updated note Updated Title and all 1st steps Updated Market Notifications steps Updated Note Updated Title and QSE Issues step 1 and step 3 | March 31, 2017 |
| 3.2 3.6 3.7 3.8 4.3 | 1.0 / 24 1.0 / 2 1.0 / 9 1.0 / 5 1.0 / 26 | Updated step Excess Generation Updated step OpsMon Display to Splunk Display Updated Manual Commit of a Resource step 1 Updated step Monitor Updated step Excess Generation | June 1, 2017 |
| 3.2 3.7 | 1.0 / 25 1.0 / 10 | Added Manual Commitment to bring a Combined Cycle On Line Updated 1st Note and Manual Dispatch to bring a Unit of a Combined Cycle On-line | June 30, 2017 |
| 3.7 | 1.0 / 11 | Added Manual Dispatch of an OFFQS Resource | September 29, 2017 |
| 2.4 7.1 | 1.0 / 5 1.0 / 5 | All procedures in this manual have been reviewed Removed Greens Bayou Unit 5 Updated Primary Control Center 4th note | December 28, 2017 |
| 3.7 | 1.0 / 12 | Updated Manual Commit of a Resource, Manual Dispatch of an OFFQS Resource and Manual Dispatch to bring a Unit of a Combined Cycle On-line | February 28, 2018 |
| 3.2 | 1.0 / 26 | Added EMR Resources step | March 28, 2018 |
| 2.2 3.5 | 1.0 / 5 1.0 / 8 | Updated procedure purpose Updated REG/RRS - RUC Committed Shortages | May 1, 2018 |
| 2.3 4.4 6.2 | 1.0 / 13 1.0 / 15 1.0 / 5 | Added Email to Priority Outages Subsection Updated step DRUC Delay Added SWGR language in procedure | May 31, 2018 |
| 3.7 | 1.0 / 13 | Updated Manual Dispatch of an OFFQS Resource | August 31, 2018 |
| 3.1 3.2 4.1 4.2 4.3 | 1.0 / 8 1.0 / 27 1.0 / 1 1.0 / 7 1.0 / 27 | Moved Deselect Contingencies to Desktop Guide Reliability Unit Commitment Desk Clarfication for step HRUC Committed Units Added note to clarify when an an OFF-LINE study is required Moved Deselect Contingencies to Desktop Guide Reliability Unit Commitment Desk Deleted Bad/Suspect Telemetry Clarfication for step DRUC Committed Units All procedures in this manual have been reviewed | December 28, 2018 |
| 3.2 4.3 | 1.0 / 28 1.0 / 28 | Updated step HRUC Committed Units Updated step Review | March 29, 2019 |
| 3.2 3.7 | 1.0 / 29 1.0 / 14 | Added step Post to Canceling RUC Commitments Added step Post to Canceling RUC Commitments | May 16, 2019 |
| 6.2 | 1.0 / 6 | Updated for NPRR901 | May 31, 2019 |
| 3.2 3.7 4.3 6.2 | 1.0 / 30 1.0 / 15 1.0 / 29 1.0 / 7 | Updated step Approval Updated NOTE Updated step Approval Updated steps and added SWGR Requested by ERCOT released back to SPP or MISO | November 1, 2019 |
| 3.2 4.3 6.2 | 1.0 / 31 1.0 / 30 1.0 / 8 | Updated step Monitor Updated step Review Updated step VDI All procedures in this manual have been reviewed | January 1, 2020 |
| 2.3 3.1 3.2 3.3 3.7 4.2 4.3 5.2 6.2 7.1 | 1.0 / 14 1.0 / 9 1.0 / 32 1.0 / 16 1.0 / 16 1.0 / 8 1.0 / 31 1.0 / 12 1.0 / 9 1.0 / 6 | Clarified RUC-commits/decommits Clarified RUC-commits/decommits Clarified RUC-commits/decommits Clarified RUC-commits/decommits Clarified RUC-commits/decommits Clarified RUC-commits/decommits Clarified RUC-commits/decommits Clarified RUC-commits/decommits Clarified RUC-commits/decommits Updated Primary Control Center steps 1 & 3 | January 31, 2020 |
| 7.1 | 1.0 / 7 | Updated Title and removed Alternate Control Center | February 28, 2020 |
| 3.7 6.2 | 1.0 / 17 1.0 / 10 | Added RUCAC to bring a Unit of a Combined Cycle On-line to a Higher Configuration for Addional Capacity Added VDI Combined Cycle | May 29, 2020 |
| 2.1 3.2 3.8 6.1 | 1.0 / 6 1.0 / 33 1.0 / 6 1.0 / 20 | Added Advance Action Notice per NPRR930 Updated STNET Study Added Advance Action Notice section per NPRR930 Added Advance Action Notice section per NPRR930 | July 1, 2020 |
| 3.7 5.2 | 1.0 / 18 1.0 / 13 | Updated Manual Dispatch to take a Unit of a Combined Cycle Off-line Added Do Not Approve step | July 31, 2020 |
| 3.2 4.3 | 1.0 / 34 1.0 / 32 | Updated Violated Constraints Updated Violated Constraints | October 31, 2020 |
| 2.3 2.5 3.2 3.3 3.5 3.6 3.7 3.8 4.3 4.4 4.5 4.6 6.1 8.1 | 1.0 / 15 1.0 / 6 1.0 / 35 1.0 / 17 1.0 / 9 1.0 / 3 1.0 / 19 1.0 / 7 1.0 / 33 1.0 / 16 1.0 / 8 1.0 / 12 1.0 / 21 1.0 / 3 | Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 & added Note for NPRR 1028 Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 & added Note Updated for NPRR1039 All procedures in this manual have been reviewed | December 31, 2020 |
| 2.3 3.2 | 1.0 / 16 1.0 / 36 | Updated Load Forecasting email Updated Load Forecasting email | June 16, 2021 |
| 2.3 3.2 6.1 | 1.0 / 17 1.0 / 37 1.0 / 22 | Updated for OBDRR031 Updated for OBDRR031 Updated for OBDRR031 | July 12, 2021 |
| 2.3 | 1.0 / 18 | Updated Increasing A/S Requirements before A/S Obligations Publish 3rd NOTE | July 31, 2021 |