- Power Operations Bulletin # 1024

ERCOT has posted/revised the Reliability Risk Desk manual.

A copy of the procedure can be found at:

- http://www.ercot.com/mktrules/guides/procedures/index.html

## 4.5  Severe Weather Operations

Procedure Purpose:  To monitor the wind forecast during operations with severe weather conditions.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | EOP-011-1 R1, R1.1, R1.2, R1.2.6, R2, R2.1, R2.2, R2.2.9 |  |  |  |

| Version: 1 | Revision: 3 | Effective Date: February 1, 2022 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Loss of Wind Farm Turbines due to Severe Weather |  |
| NOTE | Significant weather events can consist of, but are not limited to the following: - Tornados - Strong straight line winds - Flooding - Freezing precipitation |
| Manually Override Short Term Wind Power Forecast | The ERCOT Operator will contact the Operations Analysis Engineer to conduct further analysis and to override system: IF: - A severe weather related de-rate has occurred at a given wind farm, and - The telemetry, Outage Scheduler and COP have not been correctly updated by the QSE. Contact Operations Analysis Engineer to do further analysis and potentially override the forecast given the description above after checking the following: - Number of turbines online - Number of turbines offline - Outage scheduler - Telemetered wind speed (MPH) |
| NOTE | The QSE should: - Update wind generating unit’s telemetry to reflect the number of turbines lost. - NTON – number of turbines online - NTOF – number of turbines offline - NTUN – number of turbines unknown - Update ERCOT Outage Scheduler for updated HSL information that correctly reflects the number of turbines lost. This follows procedure for forced outages and should be done immediately. - Update unit’s COP in relation to the most recent forecast for the next hour(s) that pertains to the duration the turbines will be lost and accurately reflects the number of turbines lost. Notification to the QSE may be necessary if the above are not complete within the designated time frame. |
| Post | Coordinate with the Real-Time Operator for making hotline calls and the posting of the notices on the ERCOT Website. |
| Cancel Posting | Coordinate with the Real-Time Operator for the cancelation of the postings on the ERCOT Website and making hotline calls. |
| LOG | Log all actions. |
| ### High Wind Output Forecast with Forecasted Severe Weather in a Region |  |
| Manually Override Short Term Wind Power Forecast | The ERCOT Operator will contact the Operations Analysis Engineer to conduct further analysis and to override the system if all of the following conditions are met: - The wind forecast is persistently higher than the actual output (the over-forecast error will exceed 20% of installed capacity of wind farms affected or 1000 MW in a region) for a future period of time. - Weather forecasts from multiple sources indicate a winter/tropical storm will occur in the same time-line as the high forecasted output. |
| ACTION | Further analysis could potentially reduce the forecasted value of the region in question to a lower output. |
| EXAMPLE | Below is an example of the STWPF being much higher due to turbines freezing. You will see the light blue line much lower than the multiple colored lines that are forecasts. When the actual output begins to dip away from the forecast and icing conditions exist, it is likely an override is needed. |
| LOG | Log all actions. |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Hartmann, Gaddy, Self, and Frosch | Preparers | January 24, 2017 |
| Hartmann, Gaddy and Frosch | Procedure writers and editors | March 27, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | May 26, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | June 23, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | July 24, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | September 27, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | December 22, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | February 22, 2018 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | March 26, 2018 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | April 27, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | May 25, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | August 24, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | December 21, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | January 25, 2019 |
| Hartmann, Gaddy and Pence | Procedure writers and editors | July 29, 2019 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | October 29, 2019 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | December 20, 2019 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | January 27, 2020 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | February 24, 2020 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | June 25, 2020 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | September 23, 2020 |
| Hartmann, Gaddy, Cyphers, and Sheets | Procedure writers and editors | December 23, 2020 |
| Hartmann, Gaddy, Cyphers, and Sheets | Procedure writers and editors | April 29, 2021 |
| Hartmann, Gaddy, Cyphers, and Sheets | Procedure writers and editors | June 11, 2021 |
| Hartmann, Gaddy, Cyphers, and Sheets | Procedure writers and editors | August 27, 2021 |
| Hartmann, Gaddy, Cyphers and Frosch | Procedure writers and editors | December 17, 2021 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | January 27, 2022 |

Manual Change History

| Procedure | Ver/Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All | 1.0 / 0 | New procedures | January 30, 2017 |
| 2.1 3.1 4.4 5.1 7.1 7.2 9.1 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Updated System Operator Responsibility and Authority Updated Up Ramp Event step 2 Updated Panhandle Region Updated Reliability Risk Desk performs STNET Study Updated title and all 1st steps Updated Implement EEA Level 3 steps Updated Title | March 31, 2017 |
| 3.1 | 1.0 / 2 | Updated Down Ramp Event step 1, 2 & 3 Updated Up Ramp Event step 1 & 2 | June 1, 2017 |
| 3.1 7.2 | 1.0 / 3 1.0 / 2 | Updated Down Ramp Event step 2 Updated 1st note, step 1 changed to EEA Level 3 | June 30, 2017 |
| 7.2 | 1.0 / 3 | Added note Implement EEA Level 2 and Level 3 | July 28, 2017 |
| 7.2 | 1.0 / 4 | Updated Implement EEA Level 3 | September 29, 2017 |
| 8.1 | 1.0 / 1 | All procedures in this manual have been reviewed Updated Primary Control Center 4th note | December 28, 2017 |
| 3.3 | 1.0 / 1 | Updated Day Ahead RRS Sufficiency Monitoring, moved Real-time RRS Sufficiency Monitoring down, added Look Ahead Critical Inertia Level Sufficiency Monitoring and Real-time Critical Inertia Level Sufficiency Monitoring | February 28, 2018 |
| 9.1 | 1.0 / 2 | Updated Note | March 30, 2018 |
| 2.2 | 1.0 / 1 | Updated procedure purpose | May 1, 2018 |
| 5.1 | 1.0 / 2 | Added Phase Angles steps | May 31, 2018 |
| 5.1 | 1.0 / 3 | Updated and named step to Voltage contingencies | August 31, 2018 |
| 4.1 4.2 | 1.0 / 1 1.0 / 1 | Updated procedure purpose, added note and updated step Updated procedure purpose, added note and updated step All procedures in this manual have been reviewed | December 28, 2018 |
| 4.2 | 1.0 / 2 | Updated steps | January 31, 2019 |
| 3.1 4.1 | 1.0 / 3 1.0 / 2 | Deleted all steps Monitor Large Ramp Events Added Intra-Hour Wind Forecast and added Note Updated STWPF Selection Change due to forecast vs. output deviation and added Note | August 1, 2019 |
| 4.1 4.7 5.1 | 1.0 / 3 1.0 / 0 1.0 / 4 | Removed Weather Forecast Created section Weather Forecast Errors Updated Voltage Contingencies | November 1, 2019 |
| 7.2 7.3 | 1.0 / 5 1.0 / 1 | Updated MSSC Updated MSSC All procedures in this manual have been reviewed | January 1, 2020 |
| 3.3 5.1 7.3 8.1 | 1.0 / 2 1.0 / 5 1.0 / 2 1.0 / 2 | Clarified RUC-commits/decommits Clarified RUC-commits/decommits Clarified RUC-commits/decommits Updated Primary Control Center steps 1 & 3 | January 31, 2020 |
| 3.4 4.1 4.3 4.4 4.5 4.6 8.1 | 1.0 / 1 1.0 / 4 1.0 / 1 1.0 / 2 1.0 / 1 1.0 / 1 1.0 / 3 | Updated 3rd Note Updated 1st Note Updated Procedure Purpose & steps Updated Procedure Purpose & steps Updated Procedure Purpose Updated Procedure Purpose, Title & steps Updated Title and removed Alternate Control Center | February 28, 2020 |
| 2.1 7.1 | 1.0 / 2 1.0 / 2 | Added Advance Action Notice per NPRR930 Added Advance Action Notice section per NPRR930 | July 1, 2020 |
| 2.1 | 1.0 / 3 | Updated System Operator Responsibility and Authority | October 1, 2020 |
| 4.5 6.1 7.1 9.1 | 1.0 / 2 1.0 / 1 1.0 / 3 1.0 / 3 | Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 & added Note Updated for NPRR1039 All procedures in this manual have been reviewed | December 31, 2020 |
| 3.3 | 1.0 / 3 | Updated Real-time Critical Inertia Level Sufficiency Monitoring step 3 | May 6, 2021 |
| 4.6 4.7 | 1.0 / 2 1.0 / 1 | Updated for SCR 811 Updated Load Forecast email | June 16, 2021 |
| 7.2 | 1.0 / 6 | Updated 1st Note | September 1, 2021 |
| 2.2 7.1 7.2 | 1.0 / 2 1.0 / 4 1.0 / 7 | Updated step 1 Updated all steps Updated steps 1 & 2 All procedures in this manual have been reviewed | December 31, 2021 |
| 4.5 | 1.0 / 3 | Updated Note | February 1, 2022 |