- Power Operations Bulletin # 1036

ERCOT has posted/revised the Reliability Risk Desk manual.

A copy of the procedure can be found at:

- http://www.ercot.com/mktrules/guides/procedures/index.html

## 4.1	Responding to Wind Forecast Errors

Procedure Purpose:  Make corrections to errors in the weather forecast data (in EMS) and/or  switch between two wind forecasts needed to contribute to reliable system performance.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 5 | Effective Date: April 7, 2022 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | The wind forecasts produced provide enhanced situational awareness by additional means of validating the expected wind conditions. The selected wind forecast between two is sent to Wind QSEs to update their COP and used by the downstream EMS applications. |
| NOTE | Do not continuously switch between two wind forecasting services for a small gain in accuracy (i.e. “chasing the forecast”) |
| STWPF Selection Change due to forecast vs. output deviation | IF: - The end of adjustment period selected wind forecast which is currently in use has been greater than the actual wind HSL for more than 2000 MW for at least three hours or 3000 MW for at least one hour or reliability concern and the other vendor forecast has been more accurate; THEN: - Log the period of time for which the forecast has been underperforming and the accuracy of both forecasts. Inform the Shift Supervisor and potentially switch forecast selection to alternative wind forecast which has been more accurate, - E-mail the information to: - Operations Analysis - 1 ERCOT Shift Supervisors Reference Display: ERCOT EMP Applications>Wind Forecasting Service>Hourly EMS wind forecast and other necessary displays. |
| NOTE | The projected wind ramp rate (PWRR) calculation is such that it will revert to using persistence (PWRR=0) if the actual wind HSL has been ramping in the opposite direction of the PWRR value for more than 25 minutes (5 intervals). RLC will set the PWRR to 0 to minimize the impact and then cancel the flag after the PWRR is forecasting the ramp to be the same as the actual ramp again. |
| Intra-Hour wind Forecast | IF: - Alarmed, make sure frequency isn’t rapidly declining and wind hasn’t turned direction and is ramping very fast (really only need to be concerned when getting above 300-400 MW per 5 minutes and causing frequency to decline below 59.95 Hz). If frequency does drag and regulation is exhausted, the Real-Time Desk should follow their procedure for manually running SCED. Watch the PWRR and wind ramp to help inform the Real-Time Desk; THEN: - Notify an Operations Analysis Engineer to do further analysis, - E-mail the information to: - Operations Analysis - 1 ERCOT Shift Supervisors |
| LOG | Log all actions. |

# 4.2	Override during Normal Operations

Procedure Purpose:  To monitor wind forecasts during normal operations. It is presumed that under normal operating conditions that the wind forecast override will very rarely be used. However there are certain scenarios that might dictate an override.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 3 | Effective Date: April 7, 2022 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Wind Farm Forecast not Matching Output |  |
| NOTE | ERCOT can override the forecast: IF: - Forecasts are deviating from the actual output of a unit/region and have been consistently deviated for an extended period of time, or - A large over-forecast error is expected due to the unusual weather pattern which has not been captured in the past, or - Criteria has been met to determine a root cause for the deviation. |
| STWPF Override due to forecast vs. output deviation | Contact the Operations Analysis Engineer to do further analysis and potentially override the forecast given the description above after checking the following: - Number of turbines online - Number of turbines offline - Outage scheduler - Telemetered wind speed (MPH) - E-mail the information to: - Operations Analysis - 1 ERCOT Shift Supervisors Example A: If there is a high MPH and a high forecast, but low MW output. Example B: If there is a high output, but a low forecast and low HSL in outage scheduler. |
| Manually Override Short Term Wind Power Forecast | Contact the Operations Analysis Engineer to do further analysis override system: IF: - A severe weather related de-rate has occurred at a given wind farm, and - The telemetry, Outage Scheduler and COP have not been correctly updated by the QSE. - E-mail the information to: - Operations Analysis - 1 ERCOT Shift Supervisors The Operations Analysis Engineer will do further analysis and potentially override the forecast given the description above after checking the following: - Number of turbines online - Number of turbines offline - Outage scheduler - Telemetered wind speed (MPH) |
| LOG | Log all actions. |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Hartmann, Gaddy, Self, and Frosch | Preparers | January 24, 2017 |
| Hartmann, Gaddy and Frosch | Procedure writers and editors | March 27, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | May 26, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | June 23, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | July 24, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | September 27, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | December 22, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | February 22, 2018 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | March 26, 2018 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | April 27, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | May 25, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | August 24, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | December 21, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | January 25, 2019 |
| Hartmann, Gaddy and Pence | Procedure writers and editors | July 29, 2019 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | October 29, 2019 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | December 20, 2019 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | January 27, 2020 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | February 24, 2020 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | June 25, 2020 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | September 23, 2020 |
| Hartmann, Gaddy, Cyphers, and Sheets | Procedure writers and editors | December 23, 2020 |
| Hartmann, Gaddy, Cyphers, and Sheets | Procedure writers and editors | April 29, 2021 |
| Hartmann, Gaddy, Cyphers, and Sheets | Procedure writers and editors | June 11, 2021 |
| Hartmann, Gaddy, Cyphers, and Sheets | Procedure writers and editors | August 27, 2021 |
| Hartmann, Gaddy, Cyphers and Frosch | Procedure writers and editors | December 17, 2021 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | January 27, 2022 |
| Hartmann, Gaddy, Cyphers and Frosch | Procedure writers and editors | February 24, 2022 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | March 31, 2022 |

Manual Change History

| Procedure | Ver/Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All | 1.0 / 0 | New procedures | January 30, 2017 |
| 2.1 3.1 4.4 5.1 7.1 7.2 9.1 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Updated System Operator Responsibility and Authority Updated Up Ramp Event step 2 Updated Panhandle Region Updated Reliability Risk Desk performs STNET Study Updated title and all 1st steps Updated Implement EEA Level 3 steps Updated Title | March 31, 2017 |
| 3.1 | 1.0 / 2 | Updated Down Ramp Event step 1, 2 & 3 Updated Up Ramp Event step 1 & 2 | June 1, 2017 |
| 3.1 7.2 | 1.0 / 3 1.0 / 2 | Updated Down Ramp Event step 2 Updated 1st note, step 1 changed to EEA Level 3 | June 30, 2017 |
| 7.2 | 1.0 / 3 | Added note Implement EEA Level 2 and Level 3 | July 28, 2017 |
| 7.2 | 1.0 / 4 | Updated Implement EEA Level 3 | September 29, 2017 |
| 8.1 | 1.0 / 1 | All procedures in this manual have been reviewed Updated Primary Control Center 4th note | December 28, 2017 |
| 3.3 | 1.0 / 1 | Updated Day Ahead RRS Sufficiency Monitoring, moved Real-time RRS Sufficiency Monitoring down, added Look Ahead Critical Inertia Level Sufficiency Monitoring and Real-time Critical Inertia Level Sufficiency Monitoring | February 28, 2018 |
| 9.1 | 1.0 / 2 | Updated Note | March 30, 2018 |
| 2.2 | 1.0 / 1 | Updated procedure purpose | May 1, 2018 |
| 5.1 | 1.0 / 2 | Added Phase Angles steps | May 31, 2018 |
| 5.1 | 1.0 / 3 | Updated and named step to Voltage contingencies | August 31, 2018 |
| 4.1 4.2 | 1.0 / 1 1.0 / 1 | Updated procedure purpose, added note and updated step Updated procedure purpose, added note and updated step All procedures in this manual have been reviewed | December 28, 2018 |
| 4.2 | 1.0 / 2 | Updated steps | January 31, 2019 |
| 3.1 4.1 | 1.0 / 3 1.0 / 2 | Deleted all steps Monitor Large Ramp Events Added Intra-Hour Wind Forecast and added Note Updated STWPF Selection Change due to forecast vs. output deviation and added Note | August 1, 2019 |
| 4.1 4.7 5.1 | 1.0 / 3 1.0 / 0 1.0 / 4 | Removed Weather Forecast Created section Weather Forecast Errors Updated Voltage Contingencies | November 1, 2019 |
| 7.2 7.3 | 1.0 / 5 1.0 / 1 | Updated MSSC Updated MSSC All procedures in this manual have been reviewed | January 1, 2020 |
| 3.3 5.1 7.3 8.1 | 1.0 / 2 1.0 / 5 1.0 / 2 1.0 / 2 | Clarified RUC-commits/decommits Clarified RUC-commits/decommits Clarified RUC-commits/decommits Updated Primary Control Center steps 1 & 3 | January 31, 2020 |
| 3.4 4.1 4.3 4.4 4.5 4.6 8.1 | 1.0 / 1 1.0 / 4 1.0 / 1 1.0 / 2 1.0 / 1 1.0 / 1 1.0 / 3 | Updated 3rd Note Updated 1st Note Updated Procedure Purpose & steps Updated Procedure Purpose & steps Updated Procedure Purpose Updated Procedure Purpose, Title & steps Updated Title and removed Alternate Control Center | February 28, 2020 |
| 2.1 7.1 | 1.0 / 2 1.0 / 2 | Added Advance Action Notice per NPRR930 Added Advance Action Notice section per NPRR930 | July 1, 2020 |
| 2.1 | 1.0 / 3 | Updated System Operator Responsibility and Authority | October 1, 2020 |
| 4.5 6.1 7.1 9.1 | 1.0 / 2 1.0 / 1 1.0 / 3 1.0 / 3 | Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 & added Note Updated for NPRR1039 All procedures in this manual have been reviewed | December 31, 2020 |
| 3.3 | 1.0 / 3 | Updated Real-time Critical Inertia Level Sufficiency Monitoring step 3 | May 6, 2021 |
| 4.6 4.7 | 1.0 / 2 1.0 / 1 | Updated for SCR 811 Updated Load Forecast email | June 16, 2021 |
| 7.2 | 1.0 / 6 | Updated 1st Note | September 1, 2021 |
| 2.2 7.1 7.2 | 1.0 / 2 1.0 / 4 1.0 / 7 | Updated step 1 Updated all steps Updated steps 1 & 2 All procedures in this manual have been reviewed | December 31, 2021 |
| 4.5 | 1.0 / 3 | Updated Note | February 1, 2022 |
| 2.3 | 1.0 / 0 | New procedure section | March 1, 2022 |
| 4.1 4.2 | 1.0 / 5 1.0 / 3 | Updated Note Updated Note | April 7, 2022 |