- Power Operations Bulletin # 1045

ERCOT has posted/revised the Reliability Unit Commitment manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

- http://www.ercot.com/mktrules/guides/procedures/index.html

## 3.2	Review, Approve and Post HRUC Results

Procedure Purpose:  Monitor RUC applications to determine if systems are functioning properly.  Verify results and correct for any warning or error messages.  Review and approve final results for market posting.

| Protocol Reference | 4.4.8 | 5.1 | 5.3(3) | 5.5.1 |
| --- | --- | --- | --- | --- |
|  | 5.5.2 | 5.5.3 | 6.1(2) | 6.4.9.1.2 |
| Guide Reference |  |  |  |  |
| NERC Standard | EOP-011-1 R2, R2.2, R2.2.3, R2.2.3.1 | IRO-001-4 R1 | TOP-001-5 R1, R2 | TOP-002-4 R1, R2, R3, R4, R4.1, R4.4, R5 |

| Version: 1 | Revision: 39 | Effective Date: July 1, 2022 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | See Desktop Guide Common to Multiple Desks Section 2.16 if the savecase function fails when running RUC |
| Monitor | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>HRUC Displays>Workflow>HRUC Workflow Market Operation>Reliability Unit Commitment>HRUC Displays>Workflow>HRUC Workflow Messages - Monitor the HRUC Workflow display to determine when it is complete, ENSURE: - The workflow has completed before the study is approved and published. IF: - The study is approved before it completes, - Incorrect RUC deployments are sent to QSE’s THEN: - Make hotline call to notify QSE’s that deployments for HRUC are invalid, - Notify Director Control Room Operations and/or Designee, - ERCOT may use information from the DAM processes as decision support during the HRUC processes. |
| System Summary | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>UC Displays>Output Display Menu>System Outputs>Summary IF: - All load forecasts seem unreasonable; THEN: - Select the most reasonable forecast, AND - Call the Load Forecasting group for guidance on updating the weather or load forecast - Notify by e-mail the following distribution lists of the issue: - Load Forecasting Department - 1 ERCOT Shift Supervisors |
| Excess Generation | During periods of low load and excess generation: PERIODICALLY REVIEW: - Splunk Dashboard Viewer under the MOS_DEV folder: - “Last Approved HRUC Capacity” which is based on the last ran HRUC solution VERIFY: - TOTAL_LOAD is less than SS_LASL, IF: - Load forecast is reasonable AND the decision needs to be made in the near future, THEN: - Decommit generation from the HRUC next study, - Priority should be on WGR’s or Resources that resolve congestion; IF: - The decision needs to be made immediately, THEN: - Issue an electronic Dispatch Instruction confirmation - (priority should be given to WGRs and Resources that resolve congestion - Choose “DECOMMIT” as the Instruction Type from Resource tab - Enter “ERCOT requested RUC decommit/capacity surplus” in Other Information. When issuing a VDI or confirmation, ensure the use of three-part communication: - Issue the Operating Instruction - Receive a correct repeat back - Give an acknowledgement |
| A/S Infeasibility | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP Undeliverable Ancillary Service Capacity Summary Market Participation>Physical Market>SASM Market>AS Infeasibility Market Participation>Physical Market>SASM Market>AS Replacement IF: - Undeliverable Ancillary Service are indicated; THEN: - Determine if the infeasibility is valid IF: - Valid; THEN: - Notify the affected QSE for the following information - the amount of A/S that must be reduced, and - the start and stop times of the reduction. - The QSE can substitute or ERCOT can open a SASM IF: - The QSE elects to substitute; THEN: - Determine the feasibility of the substitution. - If deemed infeasible, a SASM can be opened - Notify the Resource Operator of possible infeasibility issue. |
| A/S Insufficiency from SASM | If a SASM market has been previously run, the following display will indicate if additional A/S Insufficiencies exist: REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP Decision Support for Ancillary Service Deployment IF: - A/S Insufficiency; THEN - If deemed necessary, RUC commit the necessary Resources that are qualified to provide the service that is deficient while honoring temporal constraints, - Refer to Desktop Guide RUC Section 2.18. |
| Undeliverable A/S Capacity | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP Undeliverable Ancillary Service Capacity Summary IF: - Undeliverable A/S due to transmission constraints; THEN: - Notify the Resource Operator. |
| STNET Study | The Risk operator has the primary responsibility to perform these voltage studies, however if needed as a backup this step is provided. Each hour run a STNET study for four hours out (example it is 0100, run study for 0500) to review voltage violations. IF: - Voltage contingencies exist; THEN: - Check “Voltage Tracking Issues” spreadsheet on SharePoint to ensure the contingency is not listed - If not listed, convey the voltage violations to the Transmission and Security Operator with the potential resolution - Create a savecase, use naming convention “SC_RUC(HE)_(DATE) - Make at least one detailed log entry per shift that the studies are being executed. If any new voltage violations are identified that do not have a solution, log the information and notify the Transmission and Security Operator of the new violation(s) - Update the “Voltage Tracking Issues” spreadsheet listing the new voltage violation with the contingency resolution. IF: - Unsolved contingencies exist; THEN: - Communicate any unsolved contingency to the Shift Engineer and Transmission Security Desk Operator with potential solutions. - Some potential solutions could be transmission switching, creation of a manual constraint, bringing on an additional Resource, returning a planned outage, or development of a CMP - Validate the resolution - Update the “Voltage Tracking Issues” spreadsheet listing the new unsolved contingency with the contingency resolution. |
| Violated Constraints | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP Binding Constraint Summary Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP Constraint Summary REVIEW: - Violated constraints. If needed, notify Operations Support Engineer to determine the validity; IF: - Invalid, no further action is required; IF: - Valid; AND - Related to a phase shifter tap settings, THEN: - Notify Operations Support Engineer to determine if adjusting a Phase Shifter would reduce the flow, - Create Suggestion Plan for Constraint, - Manually RUC commit resources as needed, IF: - Valid; AND no Suggestion Plan or Resource is available to commit within the timeframe of the violated constraint, THEN: - Notify the Operations Support Engineer and Transmission & Security Desk Operator to determine if an outage can be withdrawn within the timeframe, IF: - No outage can be withdrawn within the timeframe of the violated constraint, THEN: - Notify Operations Support Engineer to develop a Congestion Management Plan and provide it to the TO and Transmission & Security Desk Operator, Notify Shift Supervisor to contact the Director Control Room Operations and/or Designee of actions taken Refer to Desktop Guide RUC Section 2.14. |
| Capacity Reserve Margin | Monitor: - Available Committed Capacity Margin and the Available Capacity Margin columns. IF: - If the Available Committed Capacity Margin threshold is less than, OR; - If the Available Capacity Margin threshold is less than the minimum requirements: THEN: - Inform Shift Supervisor Refer to Desktop Guide RUC Section 2.24 |
| HRUC Committed Units | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>DSI Displays>External Input Data>MF Generator Parameter IF: - HRUC recommends the commitment of any unit; THEN: - Determine the validity, - Determine the temporal constraints for each of the unit’s recommendation. - Refer to Desktop Guide RUC Section 2.23. IF: - Temporal constraint exceedances at the same facility do not conflict, - The resource start-up time allows enough time to re-evaluate the need for its commitment in future HRUC Study Periods, and - There is no reliability reason requiring the resource commitment decision to be made immediately; THEN: - De-select the resource prior to approving the HRUC study by changing ‘Commit’ to ‘blank’ and list reason, IF: - Temporal constraint exceedances at the same facility, - There is a reliability reason requiring the resource commitment decision to be made immediately; - Resources returning from outages - Congestion or Capacity deficiencies that are creating HRUC performance issues THEN: - Log the reason for not de-selecting the resource. NOTE: A reason must be entered for commit, decommit, and uncommitting, otherwise a message window will pop up in DSP approval process. Examples below: - Evaluate later (should be used when waiting until the last possible hour to commit) - Short start (should be used for units that can start within 1 hour) - Voltage support - Valley import - Capacity - Constraint name (SLWSCRL5) * Do not use special characters When issuing a confirmation, ensure the use of three-part communication: - Issue the Operating Instruction - Receive a correct repeat back - Give an acknowledgement |
| EMR Resources | Resources with “EMR” Resource status can only be RUC committed during Emergency conditions. |
| RMR Resources | QSEs will show a COP status of OFF when Resources are available. RMR Resources will only be dispatched from the Hourly Reliability Unit Commitment (HRUC). |
| RMR Commitment | WHEN: - HRUC recommends a RMR unit, AND - A capacity reserve shortage is projected, and no market Resources are available to meet the projected system demand, and there is a risk of an EEA event; THEN: - Determine if an RMR Resource will need to be considered in HRUC Study Period; ISSUE: - Watch for projected reserve capacity shortage with no market solution; THEN: - Ensure COP status is “OFF” and the resource start-up time allows enough time to procure the RMR for the hours showing to be deficient with risk of an EEA event; SELECT: - Commit Resource before HRUC is approved - Commit Resource, - List reason (RMR for Capacity). Call QSE with any modification to the Delivery Plan as a result of a commitment. |
| Hotline | Q#77 - Typical Hotline Script for Watch for projected reserve capacity shortage Notify Transmission Operator to make Hotline call to TOs. |
| Post | Typical ERCOT Website posting: ERCOT issued a Watch for a projected reserve capacity shortage with no market solution available. HRUC recommended RMR Resources have been committed. |
| Cancel | WHEN: - Committed RMR Resources are off-line THEN: - Making hotline call to QSEs - Cancelling ERCOT Website posting - Notify Transmission Operator to make hotline call to TOs. Q#78 - Typical Hotline Script for canceling Watch for projected reserve capacity shortage |
| Manual Commitment | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP RUC Commitment/Decommitment Summary Market Operation>Reliability Unit Commitment>HRUC Displays>DSI Displays> External Input Data>MF Generator Parameters IF: - Additional resources are needed to solve for transmission issues (such as for voltage support) and were not picked up in the HRUC run; THEN: - RUC commit unit before HRUC is approved - Change ‘blank’ to ‘Commit’, - List reason RUC commit for (constraint name, valley import or voltage support), a message window will pop up in DSP approval process if no reason is provided. - Give courtesy call to QSE when commitments are made |
| Manual Commitment to bring a Unit of a Combined Cycle On-line | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays>DSP Combined Cycle Plant Suggestion Plan IF: - Additional resources are needed to solve for transmission issues and were not picked up in the HRUC run; THEN: - RUC commit higher configuration of a Combined Cycle before HRUC is approved - Determine the temporal constraints for the higher configuration. - Change ‘blank’ to ‘Commit’, - List reason RUC commit for (constraint name, valley import or voltage support), a message window will pop up in DSP approval process if no reason is provided. - Give courtesy call to QSE when commitments are made Refer to Desktop Guide Reliability Unit Commitment Desk 2.20 |
| NOTE | - Resources cannot be decommitted for just a portion of a DAM-Committed Interval, which is a one-hour interval. - ERCOT may only decommit a Resource to resolve transmission constraints that are otherwise unsolvable or to maintain the reliability of the ERCOT System. Qualifying Facilities (QFs) may be decommitted only after all other types of Resources have been assessed for decommitment. - If ERCOT communicates HRUC commitments and decommitments verbally to a QSE, then the same Resource attributes communicated programmatically must be communicated when ERCOT gives a verbal Resource commitment or decommitment. - QSE’s shall acknowledge the notice of commit or decommit by updating their COP. |
| HRUC Decommitted Resources | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP RUC Commitment/Decommitment Summary IF: - If HRUC recommends decommitments; Determine if: - Outage related, - Possible Network Model error/ Normal Breaker status variances, - COP error for Combine Cycle configurations / JOU, - Qualifying Facilities should be de-committed ONLY as a last resort, THEN: - If this is a true decommitment: - Confirm Decommitment - List reason (most likely reason is ‘transmission outage’), a message window will pop up in DSP approval process if no reason is provided - If Decommitment is error related: - No action is required |
| NOTE | Canceling unintended RUC Commits must be completed before additional RUC Commitments are issued on the same Resource(s). Doing it after the new RUC Commitment cancels all RUC Commitments for the resource. |
| Canceling RUC Commitments | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>DSI Displays>DSI Data Processes>DSI Operator Manual Commitment IF: - A Resource is RUC committed that needs to be canceled; - Only cancel RUC commits if the ERCOT Operator Resource commitment was unintended. THEN: - Issue electronic Dispatch Instruction to cancel the RUC instruction - Choose “CANCEL RUC COMMIT” as the Instruction Type - Enter “unintended commitment” in other information When issuing a VDI or confirmation, ensure the use of three-part communication: - Issue the Operating Instruction - Receive a correct repeat back - Give an acknowledgement |
| Post | Notice Type: Operational Information Notice Priority: Low Audience: Public Typical ERCOT Website posting: Cancelled RUC commitment at timestamp [Date & Time] for [resource] for [Date & Time] due to unintended commitment. |
| ### VSAT and RUC perform AC Analysis |  |
| NOTE | IF: - RUC cannot complete the process; THEN: - Notify the Transmission & Security Operator and additional personnel as required. |
| Validate | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>UC Displays>Output Display Menu>System Outputs>Summary VERIFY: - Input data - Updated Time - Results are reasonable |
| Approval | HRUC must be approved by XX:50 REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP Execution Control Parameters IF: - The HRUC results are reasonable and after all necessary modifications have been made; THEN: - Sort the RUC Commitment column before approving so it shows commitments at the top of the screen that currently may be lower in the table but not shown in the window; - Approve the results (all RUC commitment, operator manual commitment/decommit/blank out must have a reason, otherwise a message window will pop up), OR IF: - The results are unacceptable; THEN: - Click on Disapprove button, AND - Follow the Manage HRUC Timeline Failure in the next section. IF: - Disapprove button was selected in error; THEN: - Contact Helpdesk to open ticket for EMMS Production Support to correct it. |
| After Approval | AFTER: - Approval button is pushed; THEN: - Double check display Market Participation>Physical Market>Market Results>HRUC> HRUC Results, - Make sure the records in this display matches data in display Market Operation>Reliability Unit Commitment>HRUC Displays >DSP Displays>DSP RUC Commitment/Decommitment Summary. IF: - Displays are different, the RUC commitments thought to be blanked out were sent out; THEN: - Notify the Helpdesk to call the On-Call EMMS Production support, and - Issue electronic Dispatch Instructions to cancel RUC instructions When issuing a VDI or confirmation, ensure the use of three-part communication: - Issue the Operating Instruction - Receive a correct repeat back - Give an acknowledgement |
| Log | Log actions taken. |

## 3.7	Manual Dispatch of Resources

Procedure Purpose:  Manually Dispatch Resources as necessary to ensure system security when HRUC cannot be used.

| Protocol Reference | 5.1(12) | 5.5.2 | 5.5.3(3) | 6.5.9 (3) |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | EOP-011-1 R1, R1.1, R1.2, R1.2.4 |  |  |  |

| Version: 1 | Revision: 21 | Effective Date: July 1, 2022 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - ERCOT shall honor all Resource operating parameters in Dispatch Instruction / Operating Instructions under normal conditions and Emergency Condition. During Emergency Conditions, ERCOT may verbally request QSE’s to operate its Resources outside normal operating parameters. If such request is received by a QSE, the QSE shall discuss the request with ERCOT in good faith and may choose to comply with the request - A QSE can self-commit by setting the telemetered Resource Status to ONOPTOUT for the first SCED run that the Resource is On-Line and available for SCED dispatch during the first hour of a contiguous block of RUC-Committed Hours - If a QSE-committed Resource experiences a Forced Outage or Startup Loading Failure in an hour for which another Resource under the control of the same QSE is committed by a RUC instruction, the QSE may opt out of the RUC instruction by self-committing the Resource as described above - If a Resource is RUC committed from one operating day to the next operating day, new RUC commits will need to be sent for the new day. |
| ### Manual RUC Commit of a Resource |  |
| NOTE | QSEs are required to notify ERCOT of physical limitations on their Resources ability to start that are not able to be modeled in the RUC software. ERCOT expects QSEs to enter the shortest start-up time for each unit without consideration of dependencies. IF: - ERCOT has been notified that Resources cannot be brought on-line at the same time due to temporal constraint exceedances exist at the same facility; THEN: - Stagger the start times of resources when HRUC committing the resources at the same facility. See Desktop Guide Reliability Unit Commitment Desk Section 2.23 for information on Resource Facilities with Temporal Constraints. The QSE must provide the ERCOT Shift Supervisor notice of that limitation at least seven days prior to the Operating Day in which the instruction occurs. The QSE shall be excused from complying with the portion of the RUC Dispatch Instruction that it could not meet due to the identified limitation if the proper notifications were given. IF: - A QSE receives a RUC Dispatch Instruction that it cannot meet due to a physical limitation; THEN: - The QSE representing the Resource shall notify the ERCOT Operator of the inability to fully comply with the instruction and shall comply with the instruction to the best of the Resource’s ability. IF: - The QSE has provided the ERCOT Operator notice of that limitation at least seven days prior to the Operating Day in which the instruction occurs; THEN: - The QSE shall be excused from complying with the portion of the RUC Dispatch Instruction that it could not meet due to the identified limitation. IF: - A QSE provided notice pursuant to the above of a physical limitation that would delay the RUC-committed Resource’s ability to reach its LSL in accordance with a RUC Dispatch Instruction; THEN: - ERCOT shall extend the RUC Dispatch Instruction so that the Resource’s minimum run time is respected. However, if the Resource will not be available in time to address the issue for which it received the RUC instruction, ERCOT may instead cancel the RUC Dispatch Instruction. |
| 1 | IF: - It has been determined that a Resource is needed in real-time for a transmission condition or critical inertia level after the close of the Adjustment Period (Typically will be short start, Quick Start resources available or resources scheduled to come off within the operating hour); THEN: - Notify QSE an electronic Dispatch Instruction will be issued - Verify lead time with QSE - Issue an electronic Dispatch Instruction to RUC commit the Resource, - Choose “COMMIT” as the Instruction Type from Resource level - Enter reason, such as RUC commit for contingency name, capacity or critical inertia level in “other information” - Confirm with QSE that the electronic Dispatch Instruction was received - The same Resource attributes communicated programmatically must be communicated when giving a VDI. When issuing a VDI or confirmation, ensure the use of three-part communication: - Issue the Operating Instruction - Receive a correct repeat back - Give an acknowledgement See Desktop Guide Common to Multiple Desks Section 2.3 for additional information to submit a correct electronic Dispatch Instruction. |
| LOG | Log all actions. |
| ### Manual Dispatch of an OFFQS Resource |  |
| 1 | IF: - It has been determined that a OFFQS Resource is needed in real-time for a transmission condition; THEN: - Notify QSE an electronic Dispatch Instruction will be issued - Verify LSL when resource is generating to the grid - Issue an electronic Dispatch Instruction to RUC commit the Resource, - Verbal Dispatch Instructions [RUC Desk] - Notification Date/Time: This is the time the QSE was first notified. - Start Date/Interval(IE): This is the hour ending start time of the VDI - End Date/Interval(IE): This is the hour ending end time of the VDI (if known) - Resource Name: Name of OFFQS Resource being committed - Instruction Type: Choose “COMMIT” - Reason: Voltage Stability or critical inertia level - Enter reason, such as RUC commit for contingency name in “other information” - Confirm with QSE that the electronic Dispatch Instruction was received - The same Resource attributes communicated programmatically must be communicated when giving a VDI. When issuing a VDI or confirmation, ensure the use of three-part communication: - Issue the Operating Instruction - Receive a correct repeat back - Give an acknowledgement See Desktop Guide Common to Multiple Desks Section 2.3 for additional information to submit a correct electronic Dispatch Instruction. |
| LOG | Log all actions. |
| ### Manual Dispatch to take a Unit Off-Line |  |
| 1 | IF: - A manual dispatch instruction / Operating Instruction will result in the unit being dispatched off-line (i.e., less than the minimum operating limit for that Resource); THEN: - Issue an electronic Dispatch Instruction taking the Resource to zero until it can be released, - Choose “DECOMMIT” as the Instruction Type from Resource level - Enter RUC Decommit for contingency name in “other information” When issuing a VDI or confirmation, ensure the use of three-part communication: - Issue the Operating Instruction - Receive a correct repeat back - Give an acknowledgement - Ensure QSE updates telemetry. |
| ### Manual Dispatch to take a Unit of a Combined Cycle Off-line |  |
| 1 | IF: - System conditions require one unit of a Combined Cycle Plant to be manually dispatched off-line; THEN: - Contact the QSE and request which unit the QSE would like to shutdown, - Request the planned/current CC configuration and then the CC configuration that the Resource will need to be operating, - Issue an electronic Dispatch Instruction confirmation to “DECOMMIT” the QSE to their CC configuration. All data must be entered but pay attention to the following details. - Choose the proper QSE from the Participant name - Select the CC configuration that you are instructing the Resource to operate in from the Resource name - Choose “DECOMMIT” as the Instruction Type from Resource level - Enter RUC decommit for contingency name in “other information” When issuing a VDI or confirmation, ensure the use of three-part communication: - Issue the Operating Instruction - Receive a correct repeat back - Give an acknowledgement - Log the above information. |
| ### Manual Dispatch to bring a Unit of a Combined Cycle On-line |  |
| 1 | IF: - System conditions require a unit of a Combined Cycle Plant to be manually dispatched on-line; THEN: - Contact the QSE and notify which unit will be committed, - Request the planned/current CC configuration and then the CC configuration that the Resource will need to be operating, - Determine the temporal constraints for the CC configuration. - Issue an electronic Dispatch Instruction to “COMMIT” the QSE to their CC configuration. All data must be entered but pay attention to the following details. - Choose the proper QSE from the Participant name - Select the CC configuration that you are instructing the Resource to operate in from the Resource name - Choose “COMMIT” as the Instruction Type from Resource level - Enter RUC commit for contingency name or critical inertia level in “other information” When issuing a VDI or confirmation, ensure the use of three-part communication: - Issue the Operating Instruction - Receive a correct repeat back - Give an acknowledgement - Log the above information. |
| ### Manual RUCAC to bring a Unit of a Combined Cycle On-line to a Higher Configuration for Additional Capacity |  |
| 1 | IF: - System conditions require a higher configuration of a Combined Cycle Plant to be manually dispatched on-line for additional capacity; THEN: - Contact the QSE and notify which higher configuration will be committed, - Request the planned/current CC configuration and then the CC configuration that the Resource will need to be operating, - Issue an electronic Dispatch Instruction to “RUC COMMIT” the QSE to their CC configuration. All data must be entered but pay attention to the following details. - From RUCAC VDI tab - Choose QSE in the “QSE Name” dropdown list - VDIs need a start/stop time - Choose the Combined Cycle Train in the “CCT Name” dropdown list - Choose the original QSE-committed Combined Cycle Generation Resource in “QSE CCGR” dropdown list - Choose the new configuration to be committed in “RUC CCGR” dropdown list - Once the CCGRs have been selected and commitment block is entered, the HSL and Status fields should automatically be populated - Choose “COMMIT” as the “Instruction Type” - Choose “System Capacity” from dropdown list as the “Reason” - Enter RUC commit for capacity in “other information” When issuing a VDI or confirmation, ensure the use of three-part communication: - Issue the Operating Instruction - Receive a correct repeat back - Give an acknowledgement - Log the above information. |
| ### Canceling RUC Commitments |  |
| NOTE | Canceling unintended RUC Commits must be completed before additional RUC Commitments are issued on the same Resource(s). Doing it after the new RUC Commitment cancels all RUC Commitments for the resource. |
| 1 | IF: - A Resource is RUC committed that needs to be canceled; - Only cancel RUC commits if the ERCOT Operator Resource commitment was unintended. THEN: - Issue an electronic Dispatch Instruction to cancel the RUC instruction - Choose “CANCEL RUC COMMIT” as the Instruction Type - Enter “unintended RUC commitment” in other information |
| Post | Notice Type: Operational Information Notice Priority: Low Audience: Public Typical ERCOT Website posting: Cancelled RUC commitment at timestamp [Date & Time] for [resource] for [Date & Time] due to unintended commitment. |
| LOG | Log all actions. |

## 4.3	Review, Approve and Post DRUC Results

Procedure Purpose:  To work collaboratively with Market Operations Support Personnel in reviewing, and if necessary, modifying DRUC data, to approve and post the final DRUC results.

| Protocol Reference | 4.4.8 | 5.1 (9) | 5.3(3) | 5.5.1(9) |
| --- | --- | --- | --- | --- |
|  | 5.5.2 | 5.5.3(2) | 6.4.9.1(3) |  |
| Guide Reference |  |  |  |  |
| NERC Standard | IRO-008-2 R1, R2, R3 | TOP-002-4 R1, R2, R3, R4, R4.1, R4.4, R5 |  |  |

| Version: 1 | Revision: 34 | Effective Date: July 1, 2022 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | See Desktop Guide Common to Multiple Desks Section 2.16 if the savecase function fails when running RUC |
| Monitor | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>DRUC Displays>Workflow>DRUC Workflow Market Operation>Reliability Unit Commitment>DRUC Displays>Workflow>DRUC Workflow Messages |
| Review | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>DRUC Displays>UC Displays>Output Display Menu>System Outputs>Summary When DRUC has completed. If necessary, work with Market Operations and Operations Support Engineer to review the results. - Monitor the DRUC Workflow display to determine when it is complete, ENSURE: - The workflow has completed before the study is approved and published, IF: - The study is approved before it completes, - Incorrect RUC deployments are sent to QSE’s THEN: - Make hotline call to notify QSE’s that deployments for DRUC are invalid, - Notify the Director Control Room Operations and/or Designee immediately, - Abnormal system condition in the summary display after IUC (Initial Unit Commitment component of MMS) and NCUC (Network Constrained Unit Commitment component of MMS). - For Under Generation, prepare for following “DRUC Committed Units” section of this procedure - For Over generation, check for COP or Load Forecast errors - For System Lambda greater than $10, check intermediate NSM (Network Security Manager Component of MMS) results for constraint violation. For abnormal constraints in the NSM outputs and abnormal commitments in IUC and NCUC outputs, refer to Desktop Guide RUC Section 2.6, step 5. |
| NOTE | - Resources with NO Current Operating Plan (COP) entry are considered as “Unavailable” in RUC. - Resources with “EMR” Resource status can only be RUC committed during Emergency conditions. |
| System Summary | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>DRUC Displays>UC Displays>Output Display Menu>System Outputs>Summary Market Operation>Reliability Unit Commitment>DRUC Displays>UC Displays>Output Display Menu>System Outputs>Summary Line Flow DETERMINE IF: - The load forecast is reasonable for each hour, - Any under/over generation; THEN: - Be aware of these when running HRUC. |
| A/S Insufficiency from DAM | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP Decision Support for Ancillary Service Deployment Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP RUC Commitment/Decommitment Summary IF: - Notified from Market Operations of A/S Insufficiency from DAM; THEN - Issue a Watch to QSEs - Notify Transmission Operator to make Hotline call to TOs - Verify Market Operations has posted message on the ERCOT Website - Refer to Desktop Guide RUC Section 2.1. Q#85 - Typical Hotline Script for Watch for A/S insufficiency in DAM, procuring in DRUC WHEN: - A/S offers are committed in DRUC; THEN: - Making hotline call to QSEs - Cancelling ERCOT Website posting - Notify Transmission Operator to make hotline call to TOs. Q#86 - Typical Hotline Script Cancel Watch for A/S insufficiency in DAM |
| Undeliverable A/S Capacity | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP Undeliverable Ancillary Service Capacity Summary IF: - Undeliverable A/S due to Transmission Constraints and Reliability issues exist; THEN: - Notify the QSEs and provide the following information: - The amount of its Resource capacity that does not qualify to provide A/S - The projected hours - Notify the Resource Desk Operator. |
| Violated Constraints | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP Binding Constraint Summary Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP Constraint Summary REVIEW: - Violated constraints. If needed, notify Operations Support Engineer to determine the validity; IF: - Invalid, no further action is required, - Valid; THEN - Locate the constraint on the DSP Constraint Summary display, - Create a Suggestion Plan for the identified violated constraint - Review the temporal constraints of the suggested resources - If resource start-up time allows enough time to re-evaluate the need for its commitment, be aware of these conditions when running HRUC, - RUC commit resources as needed prior to DRUC approval if needed due to temporal constraints. IF: - Valid; AND no Suggestion Plan or Resource is available to commit within the timeframe of the violated constraint, THEN: - Notify Operations Support Engineer and Transmission & Security Desk Operator to determine if an outage can be withdrawn within the timeframe, IF: - No outage can be withdrawn within the timeframe, THEN: - Notify Operations Support Engineer to develop a Congestion Management Plan and provide it to the TDSP and Transmission & Security Desk Operator, - Notify Shift Supervisor to contact the Director Control Room Operations and/or Designee of actions taken Refer to Desktop Guide RUC Section 2.6. |
| NOTE | RUC Operators can decide to postpone a commitment if the startup time is well into the future. It will be left up to future HRUC solutions to commit the unit. |
| DRUC Committed Units | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>DRUC Displays>DSI Displays>External Input Data>MF Generator Parameter Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays>DSP RUC Commitment/Decommitment Summary IF: - DRUC recommends the commitment of any unit; THEN: - Determine the validity, - Determine the temporal constraints for each of the units, IF: - The resource start-up time allows enough time to re-evaluate the need for its commitment in future HRUC Study Period, AND - There is no reliability reason requiring the resource commitment decision to be made immediately; THEN: - De-select the resource prior to approving the DRUC study by changing ‘Commit’ to ‘blank’ and list reason. IF: - There is reliability reason requiring the resource commitment decision to be made immediately; - Resources with long start-up times - Resources returning from outages - Congestion or Capacity deficiencies that may create HRUC performance issues THEN: - Log the reason for not de-selecting the resource. NOTE: A reason must be entered for commit, decommit, uncommitting, examples below: - Evaluate later (should be used when waiting until the last possible hour to commit) - Short start (should be used for units that can start within 1 hour) - Voltage support - Valley import - Constraint name (SLWSCRL5) * Do not use special characters When issuing a confirmation, ensure the use of three-part communication: - Issue the Operating Instruction - Receive a correct repeat back - Give an acknowledgement |
| Excess Generation | During periods of low load and excess generation: PERIODICALLY REVIEW: - Splunk Dashboard Viewer under the MOS_DEV folder: - “6 DRUC Capacity” which is based on the last ran DRUC VERIFY: - TOTAL_LOAD is less than SS_LASL, IF: - Load forecast is reasonable AND the decision can be made in the future, THEN: - Issue OCN for Excess Reserve Capacity - Notify Transmission Operator to make Hotline call to TOs - Post message on the ERCOT Website Q#87 - Typical Hotline Script for OCN for Excess Capacity Typical ERCOT Website Posting: ERCOT issued an OCN due to a projected excess reserve capacity for [HE XX – HE XX]. WHEN: - Projected excess reserve capacity; THEN: - Making hotline call to QSEs - Cancelling ERCOT Website posting - Notify Transmission Operator to make hotline call to TOs. Q#88 - Typical Hotline Script to Cancel OCN for Excess Capacity |
| DRUC Committed For Capacity Shortage | IF: - DRUC recommends Resource(s) for capacity; THEN - Determine if start-up time allows enough time to re-evaluate, and - De-select the Resource(s) prior to approving the DRUC, After DRUC is approved: - Issue an OCN for projected reserve capacity shortage - Notify Transmission Operator to make Hotline call to TOs - Post message on the ERCOT Website Q#89 - Typical Hotline Script for OCN for committing capacity in DRUC Typical ERCOT Website Posting: ERCOT issued an OCN due to a projected capacity shortage for [HE XX – HE XX]. WHEN: - Projected reserve capacity shortage no longer exists; THEN: - Making hotline call to QSEs - Cancel ERCOT Website posting - Notify Transmission Operator to make hotline call to TOs. Q#90 - Typical Hotline Script cancellation for OCN for committing capacity in DRUC |
| Manual Commitment | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP RUC Commitment/Decommitment Summary IF: - Additional resources are needed to solve for transmission issues (such as voltage support) and were not picked up in the DRUC run, - The resource start-up time doesn’t allow enough time to re-evaluate the need for its commitment in the HRUC Study Period, OR - A Resource was given a WRUC instruction and chose not to self-commit for all hours needed; THEN: - Change ‘blank’ to ‘Commit’ - List reason (capacity, constraint name or voltage issue). - Give courtesy call to QSE when commitments are made |
| NOTE | Resources cannot be decommitted for just a portion of a DAM-Committed Interval, which is a one-hour interval. ERCOT may only decommit a Resource to resolve transmission constraints that otherwise cannot be resolved. Qualifying Facilities (QFs) may be decommitted only after all other types of Resources have been assessed for decommitment. |
| DRUC Decommitted Resources | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP RUC Commitment/Decommitment Summary IF: - If RUC recommends commitments/decommitments; DETERMINE IF: - Outage related’ - Possible Network Model error’ - COP error for Combine Cycle configurations / JOU, - Qualifying Facilities should be de-committed ONLY as a last resort; THEN: - If this is a true decommitment: - Confirm Decommitment - List reason (most likely reason is ‘transmission outage’) - If Decommitment is error related: - No action is required |
| NOTE | Once you have completed your review of DRUC, consult with Market Operations to ensure they see no issues before approving. |
| Validate | REVIEW REFERENCE DISPLAY: Market Participation>Physical Market>SASM Market>AS Responsibility - QSE Market Operation>Reliability Unit Commitment>DRUC Displays>UC Displays>Output Display Menu>System Outputs>Summary VERIFY: - Input data - Updated Time - Results are reasonable |
| Approval | DRUC must be approved by 1600 REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP Execution Control Parameters IF: - The DRUC results are reasonable after all necessary modifications have been made; THEN: - Sort the RUC Commitment column before approving so it shows commitments at the top of the screen that currently may be lower in the table but not shown in the window; - Approve the results, OR IF: - The results are unacceptable; THEN: - Click on Disapprove button - Follow the Manage DRUC Failure/Timeline Deviation procedure. IF: - Disapprove button was selected in error; THEN: - Contact Helpdesk to open ticket for EMMS Production Support to correct it. |
| NOTE | If the Operator disapproves the results, the results will be saved in the database for future analysis and will not be published to the MPs. |
| After Approval | AFTER: - Approval button is pushed; THEN: - Double check display Market Participation>Physical Market>Market Results>DRUC> DRUC Results, - Make sure the records in this display matches data in display Market Operation>Reliability Unit Commitment>DRUC Displays >DSP Displays>DSP RUC Commitment/Decommitment Summary. IF: - Displays are different, the RUC commitments thought to be blanked out were sent out; THEN: - Notify the Helpdesk to call the On-Call EMMS Production support, and - Issue VDIs to cancel RUC instructions When issuing a VDI or confirmation, ensure the use of three-part communication: - Issue the Operating Instruction - Receive a correct repeat back - Give an acknowledgement |
| Canceling RUC Commitments | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>DSI Displays>DSI Data Processes>DSI Operator Manual Commitment IF: - A Resource is RUC committed and needs to be canceled; - Only cancel RUC commits if the ERCOT Operator Resource commitment was unintended. THEN: - Issue an electronic Dispatch Instruction confirmation to cancel the RUC instruction - Choose “CANCEL RUC COMMIT” as the Instruction Type - Enter “unintended commitment” in other information When issuing a VDI or confirmation, ensure the use of three-part communication: - Issue the Operating Instruction - Receive a correct repeat back - Give an acknowledgement |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Frosch, Hartmann, Barcalow, Lowrie, and Stone | Preparers | November 10, 2010 |
| Frosch and Hartmann | Procedure writers and editors | November 29, 2010 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2010 |
| Frosch and Hartmann | Procedure writers and editors | January 26, 2011 |
| Frosch and Hartmann | Procedure writers and editors | March 23, 2011 |
| Frosch and Hartmann | Procedure writers and editors | April 20, 2011 |
| Frosch and Hartmann | Procedure writers and editors | June 6, 2011 |
| Frosch and Hartmann | Procedure writers and editors | July 18, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 22, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 30, 2011 |
| Frosch and Hartmann | Procedure writers and editors | October 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 16, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | April 25, 2012 |
| Frosch and Hartmann | Procedure writers and editors | July 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | October 26, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 26, 2013 |
| Frosch and Hartmann | Procedure writers and editors | May 28, 2013 |
| Frosch and Hartmann | Procedure writers and editors | July 8, 2013 |
| Cheng, Frosch and Hartmann | Procedure writers and editors | August 7, 2013 |
| Frosch and Hartmann | Procedure writers and editors | December 11, 2013 |
| Frosch and Hartmann | Procedure writers and editors | December 20, 2013 |
| Frosch, Gaddy and Hartmann | Procedure writers and editors | April 1, 2014 |
| Frosch, Gaddy and Hartmann | Procedure writers and editors | May 27, 2014 |
| Frosch and Hartmann | Procedure writers and editors | September 29, 2014 |
| Frosch and Hartmann | Procedure writers and editors | December 10, 2014 |
| Frosch and Hartmann | Procedure writers and editors | February 25, 2015 |
| Frosch and Hartmann | Procedure writers and editors | April 29, 2015 |
| Hartmann and Gaddy | Procedure writers and editors | July 13, 2015 |
| Hartmann and Gaddy | Procedure writers and editors | September 25, 2015 |
| Hartmann and Gaddy | Procedure writers and editors | December 22, 2015 |
| Frosch, Hartmann and Gaddy | Procedure writers and editors | January 22, 2016 |
| Hartmann and Gaddy | Procedure writers and editors | February 23, 2016 |
| Frosch, Hartmann and Gaddy | Procedure writers and editors | June 24, 2016 |
| Hartmann and Gaddy | Procedure writers and editors | September 26, 2016 |
| Hartmann and Gaddy | Procedure writers and editors | October 31, 2016 |
| Hartmann and Gaddy | Procedure writers and editors | December 23, 2016 |
| Hartmann, Gaddy and Frosch | Procedure writers and editors | March 27, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | May 26, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | June 23, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | September 27, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | December 22, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | February 22, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | March 26, 2018 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | April 27, 2018 |
| Hartmann, Gaddy, Ballew | Procedure writers and editors | May 25, 2018 |
| Hartmann, Gaddy, Ballew | Procedure writers and editors | August 24, 2018 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | December 21, 2018 |
| Hartmann, Gaddy, Luker and Frosch | Procedure writers and editors | March 26, 2019 |
| Hartmann, Gaddy and Pence | Procedure writers and editors | May 13, 2019 |
| Hartmann, Gaddy and Pence | Procedure writers and editors | May 28, 2019 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | October 29, 2019 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | December 20, 2019 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | January 27, 2020 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | February 24, 2020 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | May 26, 2020 |
| Hartmann, Gaddy, Cyphers and Frosch | Procedure writers and editors | June 25, 2020 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | July 28, 2020 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | October 26, 2020 |
| Hartmann, Gaddy, Cyphers, and Sheets | Procedure writers and editors | December 23, 2020 |
| Hartmann, Gaddy, Cyphers, and Sheets | Procedure writers and editors | June 11, 2021 |
| Hartmann, Gaddy, Cyphers, and Sheets | Procedure writers and editors | July 8, 2021 |
| Hartmann, Gaddy, Cyphers, and Sheets | Procedure writers and editors | July 28, 2021 |
| Hartmann, Gaddy, Cyphers, and Sheets | Procedure writers and editors | August 27, 2021 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | November 29, 2021 |
| Hartmann, Gaddy, Cyphers and Frosch | Procedure writers and editors | December 17, 2021 |
| Hartmann, Gaddy, Cyphers and Frosch | Procedure writers and editors | February 24, 2022 |
| Hartmann, Gaddy, Cyphers and Frosch | Procedure writers and editors | March 31, 2022 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | June 27, 2022 |

Manual Change History

| Procedure | Ver/Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All Sections | 1.0 / 0 | New procedures for all sections for Nodal implementation | November 28, 2010 |
| 2.3 2.4 3.2 3.3 4.3 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Added new procedure “Phase Shifter Tap Settings” Updated Note Updated step “Monitor” Updated steps “Commit/De-Commit”, “Violated Constraints” and “HRUC Committed” Updated step “Review”, “A/S Insufficiency from DAM” and “DRUC Committed” | December 1, 2010 |
| 2.3 4.2 4.3 4.4 | 1.0 / 2 1.0 / 1 1.0 / 2 1.0 / 1 | Updated “Review Weather Data Information” step 2 Added steps “DRUC Committed for Capacity Shortage” and “Projected Reserve Capacity Shortage” Updated steps “DAM Timeline Deviation, DAM Failure, DRUC Delay & Software Failure” change to step 1 | December 15, 2010 |
| 3.2 4.3 4.1 4.4 6.1 | 1.0 / 2 1.0 / 3 1.0 / 2 - / 2 1.0 / 1 | Updated step “HRUC Committed Units”, “Manual Commitment”, added steps “Excess Generation” and “Canceling RUC commitments” Updated step DRUC Committed Units”, “Manual Commitment, added steps “Excess Generation” and “Canceling RUC commitments” Updated step “DAM Timeline Deviation”, DAM Failure”, DRUC Delay” Updated scripts Updated script | January 31, 2011 |
| 3.2 3.3 3.5 4.3 4.4 6.1 | 1.0 / 3 1.0 / 2 - / 0 - /4 - / 3 1.0 / 2 | Updated step Canceling RUC Commitments Deleted HRUC Timeline Deviation and updated HRUC Failure/Timeline Deviation Added new section Updated step Canceling RUC Commitments Updated step DAM Timeline Deviation in DAM Timeline Deviation/Failure Timeline not Met in section DRUC Timeline Deviation/Failure Updated Watch and Emergency Notice | March 25, 2011 |
| 2.5 3.2 3.3 4.3 6.1 6.2 | 1.0 / 1 1.0 / 4 1.0 / 3 1.0 / 5 1.0 / 3 1.0 / 1 | Updated Monthly MIS Posting Updated step Canceling RUC Commitments Updated step Failure Updated step Canceling RUC Commitments Updated step 1 in Watch and Emergency Notice Updated step & removed step Market Notification | April 22, 2011 |
| 3.2 3.5 4.3 4.4 5.2 6.1 | 1.0 / 5 1.0 / 1 1.0 / 6 1.0 / 4 1.0 / 1 1.0 / 4 | Updated steps HRUC Committed Units and Approval Updated all steps Updated step Approval Updated step DAM Timeline Deviation Updated step Long Lead Times Updated all steps | June 8, 2011 |
| 2.3 3.1 3.2 3.5 4.2 4.3 4.4 4.5 | 1.0 / 3 1.0 / 1 1.0 / 6 1.0 / 2 1.0 / 2 1.0 / 7 1.0 / 5 1.0 / 1 | Added steps for Publish A/S Requirements Updated Load Forecast step Updated steps Excess Generation, A/S Insufficiency from SASM, Violated Constraints and Approval Corrected title to match TOC and updated 1st note Updated Load Forecast step Updated Approval step Added subtitles, step DRUC Delay & step 1 Moved section 2.6 to 4.5 | July 20, 2011 |
| 2.3 2.4 3.2 3.3 4.3 6.1 7.1 | 1.0 / 4 - / 1 1.0 / 7 1.0 / 4 1.0 / 8 1.0 / 5 1.0 / 1 | Added Note to Increasing A/S Requirements before A/S Obligations Publish Added information on RMR Resource Commitment Updated step Excess Generation, added RMR Resources, RMR Commitment and Canceling RUC Commitments Updated step Commit/Decommit Resources by VDI Updated step Canceling RUC Commitments Added Projected Reserve Capacity Shortage to Watch Updated 4th note | August 24, 2011 |
| 3.2 4.2 4.3 6.1 7.1 | 1.0 / 8 1.0 / 3 1.0 / 9 1.0 / 6 1.0 / 2 | Added Note, updated step Hotline, Post and added step Cancel Deleted step RMR, updated Manual Commitment, deleted Note Updated Note Added Extreme Hot Weather in Watch Updated 3rd note and step 1 | September 1, 2011 |
| 2.3 2.4 3.1 3.2 4.3 4.4 4.5 4.6 4.5 Original | 1.0 / 5 1.0 / 2 1.0 / 2 1.0 / 9 1.0 / 10 1.0 / 6 1.0/ 0 1.0 / 0 1.0 / 2 | Deleted Phase Shifter Tap Settings Deleted step Resources Updated step Manual Commitment in Tasks prior to execution of HRUC Updated step RMR Resources and Canceling RUC Commitments Updated step for Canceling RUC Commitments Moved A/S Insufficiency in DAM to section 4.5 & DAM Failure to section 4.6 Moved A/S Insufficiency in DAM to section 4.5 & deleted Increase A/S Capacity needs about Day-Ahead Requirements Moved from section 4.5 Deleted procedure (was section 4.5), duplicate | November 1, 2011 |
| 2.3 6.1 | - / 6 1.0 / 7 | Removed Invalid SPS/RAP due to Outage Updated Post in “Notifications” All procedures in this manual have been reviewed. | December 15, 2011 |
| 1.2 3.5 4.3 4.6 | 1.0 / 1 1.0 / 3 1.0 / 11 1.0 / 3 | Updated Scope Updated all steps Updated A/S Insufficiency from DAM Updated desktop guide section | January 19, 2012 |
| 2.1 2.3 2.5 3.1 3.2 3.3 3.7 4.2 4.3 4.4 4.5 4.6 5.2 6.1 7.1 | 1.0 / 1 1.0 / 7 1.0 / 2 1.0 / 3 1.0 / 10 1.0 / 5 1.0 / 0 1.0 / 4 1.0 / 12 - / 7 1.0 / 3 1.0 / 4 1.0 / 2 1.0 / 8 1.0 / 3 | Updated 4th Paragraph Updated Desktop Guide reference Updated Monthly MIS Posting Updated Desktop Guide reference Updated Desktop Guide references and step After Approval Added step Create Save Case Added new procedure Projected Capacity Reserve Shortage with no Market Solution Updated Desktop Guide references Updated Desktop Guide references and added step After Approval Added step 2 Updated Desktop Guide reference Updated Desktop Guide reference Added step Create Save Case Updated step 1 of Watch Updated Desktop Guide references | March 1, 2012 |
| 1.1 2.1 3.1 3.2 3.3 4.2 4.3 5.1 5.2 6.1 8.1 | 1.0 / 1 1.0 / 2 1.0 / 4 1.0 / 11 1.0 / 6 1.0 / 5 1.0 / 13 1.0 / 1 1.0 / 3 1.0 / 9 1.0 / 1 | Changed Shift Engineer to Operations Support Engineer Changed TSP,DSP to TO Changed Shift Engineer to Operations Support Engineer Changed Shift Engineer to Operations Support Engineer Changed Shift Engineer to Operations Support Engineer Changed Shift Engineer to Operations Support Engineer and added WRUC Changed Shift Engineer to Operations Support Engineer and Manual Commitment Changed Shift Engineer to Operations Support Engineer Changed Shift Engineer to Operations Support Engineer and updated step Long Lead Times for NPRR402 Updated OCN, Advisory, Watch, Emergency Notice sections Changed Shift Engineer to Operations Support Engineer | May 1, 2012 |
| 1.1 1.3 2.3 3.1 3.2 3.3 4.2 4.3 4.4 5.2 6.1 7.1 | 1.0 / 2 1.0 / 1 1.0 / 8 1.0 / 5 - / 12 - / 7 - / 6 - / 14 - / 8 1.0 / 4 1.0 / 10 1.0 / 4 | Updated last paragraph, HRUC Removed ERCOT Shift Supervisor paragraph Updated step 3, added Fuel Switching and Optimize Fuel Supply & 2nd note Changed Shift Engineer to Operations Support Engineer Updated HRUC Committed Units Updated Create Save Case Updated Manual Commitment on 14:30 each day Updated DRUC Committed Units Updated step 2 in Delay of DRUC Updated Create Save Case Updated all step 1’s Updated 4th note | July 16, 2012 |
| 2.2 3.2 4.3 | 1.0 / 1 1.0 / 13 1.0 / 15 | Added Hotline Call Communication Updated Manual Commitment and Validate Updated Manual Commitment and Validate All procedures in this manual have been reviewed. | November 1, 2012 |
| 2.3 4.3 4.6 | 1.0 / 9 1.0 / 16 1.0 / 5 | Added Blackstart Availability Updated Review Updated steps SASM not able to Procure all A/S Requested & Cancel Emergency Notice | March 1, 2013 |
| 3.1 3.2 3.3 3.5 3.7 4.3 4.4 4.5 4.6 5.2 6.1 | 1.0 / 6 1.0 / 14 1.0 / 8 1.0 / 4 1.0 / 1 1.0 / 17 1.0 / 9 1.0 / 4 1.0 / 6 1.0 / 5 1.0 / 11 | Updated step Deselect Contingencies Updated step Monitor, Excess Generation, Hotline, & Cancel Updated step Failure & Create Save Case Updated step REG/RRS Updated all steps Updated 1st Note, A/S Insufficiency from DAM, Excess Generation &DRUC Committed from Capacity Shortage Updated all steps Updated all steps Updated all steps Updated step Create Save Case Updated Notifications | June 1, 2013 |
| 3.5 4.3 4.4 4.6 6.1 | 1.0 / 5 1.0 / 18 1.0 / 10 1.0 / 7 1.0 / 12 | Correct typo in script Correct typo’s in scripts Updated Delay of DRUC steps Corrected reference in desktop guide Updated step 1 in Watch & Emergency Notice | July 15, 2013 |
| 3.2 3.3 | 1.0 / 15 1.0 / 9 | Updated step HRUC Committed Units, Manual Commitment, HRUC Decommitted Resources & Approval Updated step Create Save Case | August 9, 2013 |
| 3.2 4.3 5.1 5.2 | 1.0 / 16 1.0 / 19 1.0 / 2 1.0 / 6 | Updated steps Violated Constraints, HRUC Committed Units, RMR Commitment & Manual Commitment Updated steps Violated Constraints, DRUC Committed Units & Manual Commitment Updated titles Updated Violated Constraints, Disapprove & Log. Deleted Long Lead Times, All procedures in this manual have been reviewed. | December 13, 2013 |
| 3.3 4.4 4.6 6.1 | 1.0 / 10 1.0 / 11 1.0 / 8 1.0 / 13 | Updated for NPRR542 Updated for NPRR542 Updated for NPRR542 Updated for NPRR542 and 529 | January 1, 2014 |
| 2.3 3.2 3.3 3.6 4.3 6.2 6.3 | 1.0 / 10 1.0 / 17 - / 11 1.0 / 1 1.0 / 20 1.0 / 0 1.0 / 2 | Updated Review and Select Load Forecast Updated step System Summary, HRUC Committed Units & VDI information Updated VDI information Added Manual Commit of a Resource & Canceling RUC Commitments Updated VDI information Updated DRUC Committed Units & VDI information Added new EEA procedure Change section number from 6.2 to 6.3 | April 4, 2014 |
| 2.2 2.3 2.4 2.5 3.2 3.6 4.5 4.6 5.2 6.1 | 1.0 / 2 1.0 / 11 1.0 / 3 1.0 / 3 1.0 / 18 1.0 / 2 1.0 / 5 1.0 / 9 1.0 / 7 1.0 / 14 | Added VDIs to Master QSEs Added Note to Increasing A/S before Publishing Added Note Updated Monthly MIS Posting step Updated step A/S Infeasibility Updated step 1 Updated step A/S Insufficiency Offers Updated DAM Failure Updated step Disapprove Added Note, updated Advisory & Watch | June 1, 2014 |
| 3.2 6.1 | 1.0 / 19 1.0 / 15 | Updated Undeliverable A/S Capacity, added STNET Study and title change on VSAT and RUC perform AC Analysis Updated Generic Script | October 1, 2014 |
| 3.2 3.2 4.3 6.2 | 1.0 / 20 1.0 / 20 1.0 / 21 1.0 / 1 | Updated step STNET Study, HRUC Committed Units & Manual Commitment Updated STNET Study, HRUC Committed Units & Manual Commitment Updated step DRUC Committed Units & Manual Commitment Added step All procedures in this manual have been reviewed | December 15, 2014 |
| 2.2 2.3 3.2 3.3 3.6 4.3 4.4 6.2 | 1.0 / 3 1.0 / 12 1.0 / 21 1.0 / 12 1.0 / 3 1.0 / 22 1.0 / 12 1.0 / 2 | Added Dispatch & Verbal Dispatch Instruction Deleted Meterlogix number. Updated Priority Outages Corrected VDI vs. Dispatch Instruction and Manual Commitment Corrected VDI vs. Dispatch Instruction Corrected VDI vs. Dispatch Instruction Updated step Manual Commitment & corrected VDI vs. Dispatch Instruction Updated DAM Timeline Deviation Corrected VDI vs. Dispatch Instruction | March 1, 2015 |
| 3.2 3.3 3.5 3.6 3.7 4.3 4.4 4.5 4.6 6.1 | 1.0 / 22 1.0 / 13 1.0 / 6 1.0 / 4 1.0 / 2 1.0 / 23 1.0 / 13 1.0 / 6 1.0 / 10 1.0 / 16 | Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Updated to implement NPRR679 Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure | May 1, 2015 |
| All Sections 5.2 | 1.0 / 1 1.0 / 8 | Added a “Q” for QSE scripts Updated Disapprove with email notification | July 15, 2015 |
| 3.6 | 1.0 / 5 | Updated 1st note | October 1, 2015 |
| 2.5 3.3 3.5 3.7 4.3 4.4 4.5 4.6 6.1 | 1.0 / 4 1.0 / 14 1.0 / 7 1.0 / 3 1.0 / 24 1.0 / 14 1.0 / 7 1.0 / 11 1.0 / 17 | Updated Monthly MIS Posting Added step After 20th of the month Updated step Last Day of the Month Updated HRUC Failure/Timeline Deviation step Failure Q#79 & Q#80 Updated step REG/RRS – RUC Committed Shortages Q#81& Q#82 Updated step Hotline Q#83 Updated step Cancel Q#84 Updated step A/S Insufficiency from DAM Q#86 Updated step Excess Generation Typical Script Q#87 & Q#88 Updated DAM Timeline Deviation step DAM Timeline Deviation Q#92 Updated Title DRUC Delay Updated DRUC Delay step DRUC Completes By 18:00 Q#94 Updated DRUC Delay step 2 Typical Script Q#96 Updated step A/S Insufficiency Offers Q#97 Updated step DAM Complete with A/S Q#98 Updated step Cancel Watch Q#99 Updated step DAM Failure Q#100 Updated step Cancel Watch Q#101 Updated Title Operating Condition Script Updated Operating Condition Script step Hotline Q#46 Updated Operating Condition Script step Hotline Cancellation Q#47 All procedures in this manual have been reviewed | December 31, 2015 |
| 2.1 3.6 3.6 3.7 | 1.0 / 3 1.0 / 0 1.0 / 6 1.0 / 4 | Updated System Operator Responsibility and Authority Added new Assigning Ancillary Services procedure Change section number from 3.6 to 3.7 Change section number from 3.7 to 3.8 Updated Hotline Q#83 Updated Cancel Q#84 | February 10, 2016 |
| 1.3 5.2 | 1.0 / 2 1.0 / 9 | Removed Interchange Coordinator Added step EDI step | March 1, 2016 |
| 2.1 2.2 2.4 3.1 3.2 3.3 3.6 3.7 4.3 5.2 6.1 6.2 | 1.0 / 4 1.0 / 4 1.0 / 4 1.0 / 7 1.0 / 23 1.0 / 15 1.0 / 1 1.0 / 7 1.0 / 25 1.0 / 10 1.0 / 18 1.0 / 3 | Updated for COM-002-4 Updated for COM-002-4 Added steps Note, Resources, 1, 2, & 3 Updated RMR Consideration &Manual Commitment steps Updated for COM-002-4 Updated for COM-002-4 Updated for COM-002-4 Updated for COM-002-4 & note Updated for COM-002-4 Updated for COM-002-4 Updated for COM-002-4 Updated for COM-002-4 | June 30, 2016 |
| 3.4 | 1.0 / 1 | Added Resources Startup Time Less Than One Hour | September 30, 2016 |
| 6.2 | 1.0 / 5 | Deleted step 2 | November 2, 2016 |
|  |  | All procedures in this manual have been reviewed | December 30, 2016 |
| 1.3 2.1 2.5 3.7 5.2 6.1 6.3 8.1 | 1.0 / 3 1.0 / 5 1.0 / 5 1.0 / 8 1.0 / 11 1.0 / 19 1.0 / 3 1.0 / 2 | Deleted section 1.3 Updated for IRO-001-4 Updated procedure purpose Updated Monthly MIS Posting Updated note Updated Manual Dispatch to take a Unit Off-Line step 1 Updated note Updated Title and all 1st steps Updated Market Notifications steps Updated Note Updated Title and QSE Issues step 1 and step 3 | March 31, 2017 |
| 3.2 3.6 3.7 3.8 4.3 | 1.0 / 24 1.0 / 2 1.0 / 9 1.0 / 5 1.0 / 26 | Updated step Excess Generation Updated step OpsMon Display to Splunk Display Updated Manual Commit of a Resource step 1 Updated step Monitor Updated step Excess Generation | June 1, 2017 |
| 3.2 3.7 | 1.0 / 25 1.0 / 10 | Added Manual Commitment to bring a Combined Cycle On Line Updated 1st Note and Manual Dispatch to bring a Unit of a Combined Cycle On-line | June 30, 2017 |
| 3.7 | 1.0 / 11 | Added Manual Dispatch of an OFFQS Resource | September 29, 2017 |
| 2.4 7.1 | 1.0 / 5 1.0 / 5 | All procedures in this manual have been reviewed Removed Greens Bayou Unit 5 Updated Primary Control Center 4th note | December 28, 2017 |
| 3.7 | 1.0 / 12 | Updated Manual Commit of a Resource, Manual Dispatch of an OFFQS Resource and Manual Dispatch to bring a Unit of a Combined Cycle On-line | February 28, 2018 |
| 3.2 | 1.0 / 26 | Added EMR Resources step | March 28, 2018 |
| 2.2 3.5 | 1.0 / 5 1.0 / 8 | Updated procedure purpose Updated REG/RRS - RUC Committed Shortages | May 1, 2018 |
| 2.3 4.4 6.2 | 1.0 / 13 1.0 / 15 1.0 / 5 | Added Email to Priority Outages Subsection Updated step DRUC Delay Added SWGR language in procedure | May 31, 2018 |
| 3.7 | 1.0 / 13 | Updated Manual Dispatch of an OFFQS Resource | August 31, 2018 |
| 3.1 3.2 4.1 4.2 4.3 | 1.0 / 8 1.0 / 27 1.0 / 1 1.0 / 7 1.0 / 27 | Moved Deselect Contingencies to Desktop Guide Reliability Unit Commitment Desk Clarification for step HRUC Committed Units Added note to clarify when an OFF-LINE study is required Moved Deselect Contingencies to Desktop Guide Reliability Unit Commitment Desk Deleted Bad/Suspect Telemetry Clarification for step DRUC Committed Units All procedures in this manual have been reviewed | December 28, 2018 |
| 3.2 4.3 | 1.0 / 28 1.0 / 28 | Updated step HRUC Committed Units Updated step Review | March 29, 2019 |
| 3.2 3.7 | 1.0 / 29 1.0 / 14 | Added step Post to Canceling RUC Commitments Added step Post to Canceling RUC Commitments | May 16, 2019 |
| 6.2 | 1.0 / 6 | Updated for NPRR901 | May 31, 2019 |
| 3.2 3.7 4.3 6.2 | 1.0 / 30 1.0 / 15 1.0 / 29 1.0 / 7 | Updated step Approval Updated NOTE Updated step Approval Updated steps and added SWGR Requested by ERCOT released back to SPP or MISO | November 1, 2019 |
| 3.2 4.3 6.2 | 1.0 / 31 1.0 / 30 1.0 / 8 | Updated step Monitor Updated step Review Updated step VDI All procedures in this manual have been reviewed | January 1, 2020 |
| 2.3 3.1 3.2 3.3 3.7 4.2 4.3 5.2 6.2 7.1 | 1.0 / 14 1.0 / 9 1.0 / 32 1.0 / 16 1.0 / 16 1.0 / 8 1.0 / 31 1.0 / 12 1.0 / 9 1.0 / 6 | Clarified RUC-commits/decommits Clarified RUC-commits/decommits Clarified RUC-commits/decommits Clarified RUC-commits/decommits Clarified RUC-commits/decommits Clarified RUC-commits/decommits Clarified RUC-commits/decommits Clarified RUC-commits/decommits Clarified RUC-commits/decommits Updated Primary Control Center steps 1 & 3 | January 31, 2020 |
| 7.1 | 1.0 / 7 | Updated Title and removed Alternate Control Center | February 28, 2020 |
| 3.7 6.2 | 1.0 / 17 1.0 / 10 | Added RUCAC to bring a Unit of a Combined Cycle On-line to a Higher Configuration for Additional Capacity Added VDI Combined Cycle | May 29, 2020 |
| 2.1 3.2 3.8 6.1 | 1.0 / 6 1.0 / 33 1.0 / 6 1.0 / 20 | Added Advance Action Notice per NPRR930 Updated STNET Study Added Advance Action Notice section per NPRR930 Added Advance Action Notice section per NPRR930 | July 1, 2020 |
| 3.7 5.2 | 1.0 / 18 1.0 / 13 | Updated Manual Dispatch to take a Unit of a Combined Cycle Off-line Added Do Not Approve step | July 31, 2020 |
| 3.2 4.3 | 1.0 / 34 1.0 / 32 | Updated Violated Constraints Updated Violated Constraints | October 31, 2020 |
| 2.3 2.5 3.2 3.3 3.5 3.6 3.7 3.8 4.3 4.4 4.5 4.6 6.1 8.1 | 1.0 / 15 1.0 / 6 1.0 / 35 1.0 / 17 1.0 / 9 1.0 / 3 1.0 / 19 1.0 / 7 1.0 / 33 1.0 / 16 1.0 / 8 1.0 / 12 1.0 / 21 1.0 / 3 | Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 & added Note for NPRR 1028 Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 & added Note Updated for NPRR1039 All procedures in this manual have been reviewed | December 31, 2020 |
| 2.3 3.2 | 1.0 / 16 1.0 / 36 | Updated Load Forecasting email Updated Load Forecasting email | June 16, 2021 |
| 2.3 3.2 6.1 | 1.0 / 17 1.0 / 37 1.0 / 22 | Updated for OBDRR031 Updated for OBDRR031 Updated for OBDRR031 | July 12, 2021 |
| 2.3 | 1.0 / 18 | Updated Increasing A/S Requirements before A/S Obligations Publish 3rd NOTE | July 31, 2021 |
| 3.5 | 1.0 / 10 | Updated bullet for REG/ RRS - RUC Committed Shortages | September 1, 2021 |
| 3.8 4.5 | 1.0 / 8 1.0 / 9 | Updated Advance Action Notice (AAN) Update A/S Still Insufficient | December 1, 2021 |
| 2.2 2.3 6.1 | - / 6 - / 19 - / 23 | Updated step 1 Updated step 3 & Fuel Switching Updated all steps All procedures in this manual have been reviewed | December 31, 2021 |
| 2.6 4.2 5.1 | 1.0 / 0 1.0 / 9 1.0 / 3 | New procedure section Added Note Added Note | March 1, 2022 |
| 3.2 3.3 3.7 | 1.0 / 38 1.0 / 18 1.0 / 20 | Added Note Added Note Added Note & updated step 1 | April 7, 2022 |
| 3.2 3.7 4.3 | 1.0 / 39 1.0 / 21 1.0 / 34 | Updated Canceling RUC Commitments Updated Canceling RUC Commitments Updated Canceling RUC Commitments | July 1, 2022 |