- Power Operations Bulletin # 1054

ERCOT has posted/revised the Reliability Risk Desk manual.

A copy of the procedure can be found at:

- http://www.ercot.com/mktrules/guides/procedures/index.html

## 4.1	Responding to Wind Forecast Errors

Procedure Purpose:  Make corrections to errors in the weather forecast data (in FPP Tool) and/or  switch between two wind forecasts needed to contribute to reliable system performance.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 6 | Effective Date: September 1, 2022 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | The wind forecasts produced provide enhanced situational awareness by additional means of validating the expected wind conditions. The selected wind forecast between two is sent to Wind QSEs to update their COP and used by the downstream EMS applications. |
| NOTE | Do not continuously switch between two wind forecasting services for a small gain in accuracy (i.e. “chasing the forecast”) |
| STWPF Selection Change due to forecast vs. output deviation | IF: - The end of adjustment period selected wind forecast which is currently in use has been greater than the actual wind HSL for more than 2000 MW for at least three hours or 3000 MW for at least one hour or reliability concern and the other vendor forecast has been more accurate; THEN: - Log the period of time for which the forecast has been underperforming and the accuracy of both forecasts. Inform the Shift Supervisor and potentially switch forecast selection to alternative wind forecast which has been more accurate, - E-mail the information to: - Operations Analysis - 1 ERCOT Shift Supervisors Reference Display: FPP (Taylor or Bastrop) Desktop Icon>Hourly Wind FPP (Taylor or Bastrop) and other necessary displays. |
| NOTE | The projected wind ramp rate (PWRR) calculation is such that it will revert to using persistence (PWRR=0) if the actual wind HSL has been ramping in the opposite direction of the PWRR value for more than 25 minutes (5 intervals). RLC will set the PWRR to 0 to minimize the impact and then cancel the flag after the PWRR is forecasting the ramp to be the same as the actual ramp again. |
| Intra-Hour wind Forecast | IF: - Alarmed, make sure frequency isn’t rapidly declining and wind hasn’t turned direction and is ramping very fast (really only need to be concerned when getting above 300-400 MW per 5 minutes and causing frequency to decline below 59.95 Hz). If frequency does drag and regulation is exhausted, the Real-Time Desk should follow their procedure for manually running SCED. Watch the PWRR and wind ramp to help inform the Real-Time Desk; THEN: - Notify an Operations Analysis Engineer to do further analysis, - E-mail the information to: - Operations Analysis - 1 ERCOT Shift Supervisors |
| LOG | Log all actions. |

## 4.6  Solar Forecast

Procedure Purpose:  To monitor solar forecasts during normal and abnormal operations. Make corrections to errors in the solar forecast data (in FPP Tool) and/or  switch between two solar forecasts needed to contribute to reliable system performance.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 3 | Effective Date: September 1, 2022 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Solar Forecast |  |
| NOTE | The solar forecasts produced provide enhanced situational awareness by additional means of validating the expected solar conditions. The selected solar forecast between two is sent to Solar QSEs to update their COP and used by the downstream EMS applications. |
| NOTE | Do not continuously switch between two solar forecasting services for a small gain in accuracy (i.e. “chasing the forecast”) |
| NOTE | If the solar forecast is invalid or appears to have other discrepancies; - Contact Operations Analysis Engineer to do further analysis and determine if it is necessary to override Solar forecast; - Solar Forecast can only be overwritten by Maxar |
| STWPF Selection Change due to forecast vs. output deviation | IF: - The selected solar forecast which is currently in use has been greater than the actual solar HSL causing a reliability concern and the other vendor forecast has been more accurate; THEN: - Log the period of time for which the forecast has been underperforming and the accuracy of both forecasts. Inform the Shift Supervisor and potentially switch forecast selection to alternative solar forecast which has been more accurate, - E-mail the information to: - Operations Analysis - 1 ERCOT Shift Supervisors Reference Display: FPP (Taylor or Bastrop) Desktop Icon>Hourly Wind FPP (Taylor or Bastrop) and other necessary displays. |
| NOTE | The projected solar ramp rate (PSRR) calculation is such that it will revert to using persistence (PSRR=0) if the actual solar HSL has been ramping in the opposite direction of the PSRR value for more than 35 minutes (7 intervals). RLC will set the PSRR to 0 to minimize the impact and then cancel the flag after the PSRR is forecasting the ramp to be the same as the actual ramp again. |
| Intra-Hour solar Forecast | IF: - Alarmed, make sure frequency isn’t rapidly declining and solar hasn’t turned direction and is ramping very fast (above 300-400 MW per 5 minutes and causing frequency to decline below 59.95 Hz). If frequency does drag and regulation is exhausted, notify the Real-Time Desk for manually running SCED. Watch the PSRR and solar ramp to help inform the Real-Time Desk; THEN: - Notify an Operations Analysis Engineer to do further analysis, - E-mail the information to: - Operations Analysis - 1 ERCOT Shift Supervisors |
| LOG | Log all actions. |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Hartmann, Gaddy, Self, and Frosch | Preparers | January 24, 2017 |
| Hartmann, Gaddy and Frosch | Procedure writers and editors | March 27, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | May 26, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | June 23, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | July 24, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | September 27, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | December 22, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | February 22, 2018 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | March 26, 2018 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | April 27, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | May 25, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | August 24, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | December 21, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | January 25, 2019 |
| Hartmann, Gaddy and Pence | Procedure writers and editors | July 29, 2019 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | October 29, 2019 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | December 20, 2019 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | January 27, 2020 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | February 24, 2020 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | June 25, 2020 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | September 23, 2020 |
| Hartmann, Gaddy, Cyphers, and Sheets | Procedure writers and editors | December 23, 2020 |
| Hartmann, Gaddy, Cyphers, and Sheets | Procedure writers and editors | April 29, 2021 |
| Hartmann, Gaddy, Cyphers, and Sheets | Procedure writers and editors | June 11, 2021 |
| Hartmann, Gaddy, Cyphers, and Sheets | Procedure writers and editors | August 27, 2021 |
| Hartmann, Gaddy, Cyphers and Frosch | Procedure writers and editors | December 17, 2021 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | January 27, 2022 |
| Hartmann, Gaddy, Cyphers and Frosch | Procedure writers and editors | February 24, 2022 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | March 31, 2022 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | August 29, 2022 |

Manual Change History

| Procedure | Ver/Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All | 1.0 / 0 | New procedures | January 30, 2017 |
| 2.1 3.1 4.4 5.1 7.1 7.2 9.1 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Updated System Operator Responsibility and Authority Updated Up Ramp Event step 2 Updated Panhandle Region Updated Reliability Risk Desk performs STNET Study Updated title and all 1st steps Updated Implement EEA Level 3 steps Updated Title | March 31, 2017 |
| 3.1 | 1.0 / 2 | Updated Down Ramp Event step 1, 2 & 3 Updated Up Ramp Event step 1 & 2 | June 1, 2017 |
| 3.1 7.2 | 1.0 / 3 1.0 / 2 | Updated Down Ramp Event step 2 Updated 1st note, step 1 changed to EEA Level 3 | June 30, 2017 |
| 7.2 | 1.0 / 3 | Added note Implement EEA Level 2 and Level 3 | July 28, 2017 |
| 7.2 | 1.0 / 4 | Updated Implement EEA Level 3 | September 29, 2017 |
| 8.1 | 1.0 / 1 | All procedures in this manual have been reviewed Updated Primary Control Center 4th note | December 28, 2017 |
| 3.3 | 1.0 / 1 | Updated Day Ahead RRS Sufficiency Monitoring, moved Real-time RRS Sufficiency Monitoring down, added Look Ahead Critical Inertia Level Sufficiency Monitoring and Real-time Critical Inertia Level Sufficiency Monitoring | February 28, 2018 |
| 9.1 | 1.0 / 2 | Updated Note | March 30, 2018 |
| 2.2 | 1.0 / 1 | Updated procedure purpose | May 1, 2018 |
| 5.1 | 1.0 / 2 | Added Phase Angles steps | May 31, 2018 |
| 5.1 | 1.0 / 3 | Updated and named step to Voltage contingencies | August 31, 2018 |
| 4.1 4.2 | 1.0 / 1 1.0 / 1 | Updated procedure purpose, added note and updated step Updated procedure purpose, added note and updated step All procedures in this manual have been reviewed | December 28, 2018 |
| 4.2 | 1.0 / 2 | Updated steps | January 31, 2019 |
| 3.1 4.1 | 1.0 / 3 1.0 / 2 | Deleted all steps Monitor Large Ramp Events Added Intra-Hour Wind Forecast and added Note Updated STWPF Selection Change due to forecast vs. output deviation and added Note | August 1, 2019 |
| 4.1 4.7 5.1 | 1.0 / 3 1.0 / 0 1.0 / 4 | Removed Weather Forecast Created section Weather Forecast Errors Updated Voltage Contingencies | November 1, 2019 |
| 7.2 7.3 | 1.0 / 5 1.0 / 1 | Updated MSSC Updated MSSC All procedures in this manual have been reviewed | January 1, 2020 |
| 3.3 5.1 7.3 8.1 | 1.0 / 2 1.0 / 5 1.0 / 2 1.0 / 2 | Clarified RUC-commits/decommits Clarified RUC-commits/decommits Clarified RUC-commits/decommits Updated Primary Control Center steps 1 & 3 | January 31, 2020 |
| 3.4 4.1 4.3 4.4 4.5 4.6 8.1 | 1.0 / 1 1.0 / 4 1.0 / 1 1.0 / 2 1.0 / 1 1.0 / 1 1.0 / 3 | Updated 3rd Note Updated 1st Note Updated Procedure Purpose & steps Updated Procedure Purpose & steps Updated Procedure Purpose Updated Procedure Purpose, Title & steps Updated Title and removed Alternate Control Center | February 28, 2020 |
| 2.1 7.1 | 1.0 / 2 1.0 / 2 | Added Advance Action Notice per NPRR930 Added Advance Action Notice section per NPRR930 | July 1, 2020 |
| 2.1 | 1.0 / 3 | Updated System Operator Responsibility and Authority | October 1, 2020 |
| 4.5 6.1 7.1 9.1 | 1.0 / 2 1.0 / 1 1.0 / 3 1.0 / 3 | Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 & added Note Updated for NPRR1039 All procedures in this manual have been reviewed | December 31, 2020 |
| 3.3 | 1.0 / 3 | Updated Real-time Critical Inertia Level Sufficiency Monitoring step 3 | May 6, 2021 |
| 4.6 4.7 | 1.0 / 2 1.0 / 1 | Updated for SCR 811 Updated Load Forecast email | June 16, 2021 |
| 7.2 | 1.0 / 6 | Updated 1st Note | September 1, 2021 |
| 2.2 7.1 7.2 | 1.0 / 2 1.0 / 4 1.0 / 7 | Updated step 1 Updated all steps Updated steps 1 & 2 All procedures in this manual have been reviewed | December 31, 2021 |
| 4.5 | 1.0 / 3 | Updated Note | February 1, 2022 |
| 2.3 | 1.0 / 0 | New procedure section | March 1, 2022 |
| 4.1 4.2 | 1.0 / 5 1.0 / 3 | Updated Note Updated Note | April 7, 2022 |
| 4.1 4.6 | 1.0 / 6 1.0 / 3 | Updated section Updated section | September 1, 2022 |