- Power Operations Bulletin # 1064

ERCOT has posted/revised the DC Tie manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

- http://www.ercot.com/mktrules/guides/procedures/index.html

## 3.1	Approve E-Tags for the SPP DC Ties

Procedure Purpose: An E-Tag received in the OATI WebTrans regarding DC Tie flows into or out of ERCOT will be validated for accuracy.

| Protocol Reference | 4.4.4 | 4.4.4.1 | 4.4.4.2 |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 2.1(4)(e) |  |  |  |
| NERC Standard | INT-006-5 R1, R1.1, R2, R4, R5, R5.1, R5.2, R5.3, R5.4, R5.5 | INT-009-3 R3 |  |  |

| Version: 1 | Revision: 33 | Effective Date: December 30, 2022 |
| --- | --- | --- |

| Step |  | Action |  |
| --- | --- | --- | --- |
| NOTE |  | - AEP TOP located in Ohio is the DC Tie Operator (AEP DC TIE) for the DC_E (East tie) and DC_N (North tie) - If either DC Tie is over-scheduled, contact the SPP Operator (SPP RTBM) |  |
| NOTE |  | ERCOT has analyzed the ramping capability of its Interconnection and is capable of ramping at a greater rate than the maximum ramp rate schedule on any of the DC-Ties. |  |
| NOTE |  | Timing requirements can be found in NERC Standard INT-006-5 Attachment 1, the OATI software incorporates these timing requirements into the tool and actions cannot be taken outside the timing requirements. |  |
| 1 |  | Automatic validation in WebTrans for each new or updated E-Tag will display ‘pass’ or ‘fail’. The criteria used to automatically validate E-Tags is: - ERCOT Market Information field must have QSE information - TSP (Transmission Service Provider) must have ERCO specified in the Physical Path - Tag Transaction Type must not be a Dynamic Schedule IF: - Either of the above validations fail; THEN: - The E-Tag will be automatically denied. IF: - You feel an E-Tag failed validation erroneously; THEN: Go to the list of approved ERCOT Registered QSE’s at the following website: https://wiki.ercot.com/pages/viewpageattachments.action?pageId=186982491 - Select “View” of the most recent post of “ERCOT QSE DC Tie Scheduling List” to view the ERCOT Registered QSE’s., IF: - The QSE name is on the list but was denied by WebTrans; THEN: - Approve the E-Tag and inform the ERCOT help desk and OATI help desk if needed. WebTrans Reference Display: Validation > Tag Validation Monitor |  |
| 2 |  | When a New or Updated E-Tag is received in WebTrans system: Manually validate the following: - Contact Information must be the QSE information and not ERCOT - “ERCO” must not be listed as a PSE in Tag Information - “ERCO” must not be listed as a PSE in the Physical Path - Time Zone should be CS (central standard), CD (central daylight) or CP (central prevailing) during time change - “Transaction type” must be “Energy or Normal” - “ERCOT-E” or “ERCOT-N” must be selected for the correct POR (Point-of-Receipt) or POD (Point of Delivery) in the Physical Path - “ERCOT-E” or “ERCOT-N” must be selected for the correct POR (Point-of-Receipt) or POD (Point of Delivery) on the ERCO TSP Row - Do not allow same tie on the same row for the POR and POD, example: “ERCOTN to “ERCOTN” - There are no losses (MW) in the ERCOT Control Area. This would be either to or from SPP as shown on the “Energy and Transmission Profiles” section, loss accounting may be blank, financial, or in-kind for ERCOT - Tags are permitted to be submitted within the COP time frame (up to seven days in advance), but a separate tag for each day must be submitted and the Start Time and Stop Time MUST NOT cross the midnight hour - If ERCOT is the sink BA, it is our responsibility to ensure FERC is cc’d on the e-Tag. - If Tag comes in with a Late status, deny the Tag (unless it is a curtailment). IF: - Any of the above information is incorrect; THEN: - Deny the E-Tag, otherwise proceed below. IF: - An E-Tag is received for a time period when the DC-Tie will be unavailable; THEN: - Deny the E-Tag. IF: - One or more E-Tags are submitted that will cause the DC Tie to be overscheduled; THEN: - Contact SPP Tariff (SPP Tariff) approximately 30 minutes prior to the schedule start time to ensure they also see the over-schedule; they will take action to correct the over-schedule. If the correction is not in place by 20 minutes before the over-schedule will occur, ERCOT will curtail the E-Tag to zero (0) based on the criteria of “Last in – First out” until the over schedule is alleviated. IF: - ERCOT curtails an E-Tag due to an over-schedule that was not corrected in time; THEN: - Contact the source/sink control area to ensure the curtailment will be implemented as soon as possible. WebTrans Reference Displays: Scheduling>Interchange>BTF Checkout |  |
| NOTE |  | If verification needs to be made in the current day HRUC will be used unless it is a current hour tag. If verification needs to be made for the next day DRUC will be used. |  |
| NOTE |  | Webtrans and MMS (MOI) utilize a different sign convention (positive and negative numbers) between the two systems. OATI: - (-) Imports - (+) Exports MMS: - (+) Imports - (-) Exports |  |
| COP E-Tags |  | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment> HRUC Displays> DSI Displays> DSI Data Processes> DSI DC Tie Schedule Market Operation>Reliability Unit Commitment> HRUC Displays> DSI Displays> External Input Data> MI COP Verify that E-tags are being imported into the MMS by going to the MI COP display and filter ‘ERCOT’ as the QSE name. |  |
| ### East HVDC Tie Voltage Limits |  |  |  |
| NOTE | The East HVDC tie has voltage limits depending on the tie condition. See Desktop Guide Transmission Desk 2.19 |  |  |
| 1 | WHEN: - Notified by AEP TOP that Reactors have been placed in/out of service on the East DC tie THEN: - Notify the Transmission desk operator |  |  |
| LOG | Log all actions. |  |  |

## 3.3	Approve E-Tags for the CENACE DC Ties

Procedure Purpose: An E-Tag received in the OATI WebTrans regarding DC Tie flows into or out of ERCOT will be validated for accuracy.

| Protocol Reference | 4.4.4 | 4.4.4.1 | 4.4.4.2(1) |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 2.1(4)(e) |  |  |  |
| NERC Standard | INT-006-5 R1, R1.1, R2, R4, R5, R5.1, R5.2, R5.3, R5.4, R5.5 | INT-009-3 R3 |  |  |

| Version: 1 | Revision: 37 | Effective Date: December 30, 2022 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - AEP TO in Corpus Christi is the DC Tie Operator (AEP TO) for the DC_L (Laredo VFT) - ONCOR TO in Dallas is the DC Tie Operator (ONCOR DC TIE) for the DC_R (Railroad DC Tie) - All communications will be with the DC-Tie Operator, and they will communicate with CENACE |
| NOTE | ERCOT will not allow an E-Tag to flow from CENACE to SPP or from SPP to CENACE. This will require two separate E-Tags. E-Tags are not calculated in our ACE equation, DC Tie schedules are seen by our EMMS as a generator (import) or load (export). |
| NOTE | - ERCOT has analyzed the ramping capability of its Interconnection and is capable of ramping at a greater rate than the maximum ramp rate schedule on any of the DC Ties - The Railroad DC Tie has a 15 MW minimum flow requirement when E-Tags are scheduled - Approximately one hour before start of schedule, notify the ERCOT Transmission & Security Operator with scheduled MW, Tie and direction of flow and duration. |
| NOTE | Timing requirements can be found in NERC Standard INT-006-5 Attachment 1, the OATI software incorporates these timing requirements into the tool and actions cannot be taken outside the timing requirements. |
| 1 | Automatic validation in WebTrans for each new or updated E-Tag will display ‘pass’ or ‘fail’. The criteria ERCOT uses to validate E-Tags is: - ERCOT Market Information fields must have QSE information - TSP (Transmission Service Provider) must have ERCO, and CEN specified in the Physical Path - Tag Transaction Type must not be a Dynamic Schedule If either of the above validations fail, the E-Tag will be automatically denied. If you believe an E-Tag failed validation erroneously, the list of approved ERCOT Registered QSE’s can be found at the following website: https://wiki.ercot.com/pages/viewpageattachments.action?pageId=186982491 Select “View” of the most recent post of “ERCOT QSE DC Tie Scheduling List” to view the ERCOT Registered QSE’s. If the QSE name is on the list but was denied by WebTrans, approve the E-Tag, and inform the ERCOT help desk and OATI help desk if needed. Another point of reference is to view the “QSE Contracts” in WebTrans. Each QSE is associated with each DC-Tie individually. WebTrans Reference Display: Tag Validation Summary Data>QSE Contracts |
| 2 | When a New or Updated E-Tag is received in the WebTrans system: Manually validate the following: - PSE Contact Information must be the QSE information and not ERCOT - “ERCO” must not be listed as a PSE in the Tag Information - “ERCO” must not be listed as a PSE in the Physical Path - Time Zone should be CS (central standard), CD (central daylight) or CP (central prevailing) during time change - “Transaction type” must be “Energy or Normal” - ERCO, AEPT and CEN must be included as the TSP (Transmission Service Provider) in the Physical Path and ERCO as a Scheduling Entity on the AEPT TSP row in the Physical Path for DC_L - ERCO, ONC and CEN must be included as the TSP in the Physical Path and ERCO as a Scheduling Entity on the ONC TSP row in the Physical Path for the DC_R - ERCOT and CFE/CEN must be listed as the Source and Sink under POR (Point-of-Receipt) and POD (Point of Delivery). - There are no losses (MW) in the ERCOT Control Area. This should be to or from AEPT or ONC as shown on the “Energy and Transmission Profiles” section, loss accounting may be blank, financial, or in-kind for ERCOT - A separate tag for each day must be submitted and the Start Time and Stop Time MUST NOT cross the midnight hour - If Tag comes in with a Late status, deny the Tag (unless it is a curtailment) - The sum of E-Tags is submitted that will cause the DC Tie to exceed the physical capacity for the tie - The Railroad DC Tie has a 15 MW minimum flow requirement. Ensure the net of the E-Tags are not less than 15 MW - Only ERCO and CEN are allowed as BA in the Physical Path, IF: - Any of the above information is incorrect on the E-Tag; THEN: - Deny the E-Tag. IF: - An E-Tag is denied due to another entity other than ERCO or CEN as BA in the Physical Path; THEN: - Post the appropriate Preformatted DCTCN Notice to the ERCOT Website and - Use the canned message, - Send email to SysOpsMgrs to coordinate a Market Notice. WebTrans Reference Displays: Scheduling>Interchange>BTF Checkout |
| 3 | The ramp rate for DC_R will be 50 MW per minute due to reactive issues on the CENACE side. DC_L has no ramp limitations. - Ramp Duration should be filled out on DC_R E-Tags only - Deny any Railroad DC-Tie E-Tag that does not have a ramp duration entered. - DC_L ramp duration can remain blank which is the default for a 10-minute ramp. |
| NOTE | Webtrans and MMS (MOI) utilize a different sign convention (positive and negative numbers) between the two systems. WebTrans: - (-) Imports - (+) Exports MMS: - (+) Imports - (-) Exports |
| COP E-Tags | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment> HRUC Displays> DSI Displays> DSI Data Processes> DSI DC Tie Schedule Market Operation>Reliability Unit Commitment> HRUC Displays> DSI Displays> External Input Data> MI COP - Verify that E-tags are being imported into the MMS by going to the MI COP display and filter ‘ERCOT’ as the QSE name |

## 4.4	Loss of Primary Control Center Functionality

Procedure Purpose: Provide instructions for responding to conditions that cause the primary control center to become inoperable or uninhabitable while continuing to meet its obligations with regard to the reliable operations of the ERCOT system and ensuring the safety of control center personnel.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | EOP-008-2 R1, R1.2, R1.2.1, R1.4 R1.6, R1.6.1, R1.6.2, 1.6.3, R4 | TOP-001-5 R9 |  |  |

| Version: 1 | Revision: 35 | Effective Date: December 30, 2022 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Contact Security | IF: - Unable to reach any Operator at the PCC (also trying Alternative Interpersonal Communication capability); THEN: - Check the control center video camera to determine the status of the PCC and personnel, - Contact Security at the ACC - Notify them of the situation AND - Have them attempt to make contact with Security at PCC. - Have them contact you with information acquired OR IF: - Notified by the PCC that they are evacuating and/or transferring sites OR - control center video and Security confirms evacuation; THEN: - Continue with procedure. |
| North – Houston Import IROL | The North – Houston VSAT voltage stability limit is an IROL; the actual flow MUST NOT exceed its limit. If necessary, the System Operator has the authority to direct load shedding before this IROL has been exceeded. |
| Valley Import IROL | The Valley Import stability limit is an IROL; the actual flow MUST NOT exceed its limit. If necessary, the System Operator has the authority to direct load shedding before this IROL has been exceeded. |
| West Texas Export IROL | The West Texas Export stability limit is an IROL; the actual flow MUST NOT exceed its limit. If necessary, the System Operator has the authority to instruct removing generation before this IROL has been exceeded. |
| Panhandle Export IROL | The Panhandle Export stability limit is an IROL; the actual flow MUST NOT exceed its limit. If necessary, the System Operator has the authority to instruct removing generation before this IROL has been exceeded. |
| McCamey Export IROL | The McCamey Export stability limit is an IROL; the actual flow MUST NOT exceed its limit. If necessary, the System Operator has the authority to instruct removing generation before this IROL has been exceeded. |
| 3-Part | When issuing an Operating Instruction, follow three-part communication: - Issue the Operating Instruction - Receive a correct repeat back - Give an acknowledgement |
| ### Systems are Functional |  |
| Call in Additional Operators | Activate the NXT scenario to call in additional shift personnel, which includes a Shift Supervisor. SELECT: - SO Loss of Control Room at Taylor, OR; - SO Loss of Control Room at Bastrop. - An email will be received after 10 minutes with a report of who has responded along with their estimated time of arrival. |
| QSE Hotline Call | - Q#106 - Typical Hotline Script Emergency Notice Loss of Primary Control Center (Systems are Functional) |
| TO Hotline Call | - T#91 - Typical Hotline Script Emergency Notice Loss of Primary Control Center (Systems are Functional) |
| Additional Notifications | - The Director Control Room Operations and/or Designee will notify the following: - Help Desk (to notify GMS Support and IT Infrastructure (Telecommunications and Data Center) - Engineering Support - These phone numbers are also programmed into the control room cell phone. |
| ERCOT Website Posting | - As time permits, post the Emergency Notice on the ERCOT Website. - Typical Posting Script: - ERCOT has issued an Emergency Notice for the loss of the primary control center, all systems are functioning. |
| Respond to QSEs | Monitor frequency and re-run SCED/use (manual offset) as needed. IF: - QSEs call in with questions about operational timelines or non real-time issues; THEN: - Notify the QSE that timelines and non real-time issues will be addressed when additional staff arrive, - Document QSE calls to pass along to the appropriate Operators as they arrive. |
| Real-time Contingency Analysis (RTCA) | Operations Support will assist in monitoring the RTCA functionality including results and may communicate suggested actions as needed. |
| Respond to TOs Thermal/ Voltage Limits Reached (SOL) | IF: - Thermal limits have reached their continuous rating, OR - Notified by Operations Support or a TO that thermal limits have reached their continuous rating; THEN: - Activate associated constraint, OR - Seek a recommendation from Operations Support or the appropriate TO as to what actions will alleviate the situation, - Issue unit specific Operating Instructions as necessary to QSE. (Follow-up with electronic Dispatch Instruction confirmation as time permits), - Continue to monitor to determine the effect of the plan. ERCOT Nominal Voltage Levels are 345kV, 230kV, 138kV, 115kV and 69kV. The general voltage guidelines are as follows (listed in kV): Nominal Voltage; Normal Operating Limits; Emergency Operating Limits; Ideal Voltage Range. 345; 327.75 – 362.25; 310.5 – 379.5; 345 – 359. 230; 218.5 – 241.5; 207 – 253; 230 – 240. 138; 131.1 – 144.9; 124.2 – 151.8; 138 – 144. 115; 109.25 – 120.75; 103.5 – 126.5; 115 – 120. 69; 65.55 – 72.45; 62.1 – 75.9; 69 – 71.5. Some TOs utilize different Normal (Basecase) and Emergency (Post-Contingency) voltage operating limits than the general voltage guidelines. These limits can be seen under the Network Limits display. WHEN: - Indicated by SCADA alarms, OR - Notified by Operations Support or a TO of voltage concerns; THEN: - Initiate a solution in collaboration with Operations Support and the appropriate TO and QSE in the area. WHEN: - TOs have utilized all Static Reactive Power Resources (capacitors, reactors, change in transformer taps) and a voltage issue still remains; THEN: - Instruct a QSE to raise or lower bus voltage, - The QSE should complete the requested in no more than five minutes. Typical Script: “This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is instructing [QSE] to [raise or lower] voltage at [specify bus] by [+1 or 2kV or -1 or 2kV] for a target of [target kV]. [QSE] please repeat this instruction back to me. That is correct, thank you.” |
| GTCs | IF: - Any of the GTCs is approaching 85%, OR - Notified by Operations Support or a TO that a GTC (this includes the IROL) is approaching 85%; THEN: - Activate the associated “BASECASE” constraint in TCM - Update RTMONI with new limit each time it changes |
| DC Tie Tags | Make every attempt to handle all DC Tie tags. If the workload makes it impossible to keep up with, the tags will be passively denied. |
| Log | Make log entry of events. |
| ### Systems are not Functional |  |
| NOTE | Market Participants must be notified of unplanned outages of 30 minutes or more, of telemetering, monitoring and assessment capabilities, and associated communication channels between affected entities. |
| Monitor Frequency | The ability to view an adequate Frequency source may be limited during a site-failover, database load, or if AGC is temporarily unavailable. To view the System Frequency during these conditions you may monitor the following sources. - ERCOT control room digital wall frequency displays - PI ProcessBook → ERCOT → TrueTime Frequency (Taylor) and/or - PI ProcessBook → ERCOT → TrueTime Frequency (Bastrop) It may be necessary to reload the PI ProcessBook “ERCOT Main Summary” display to show the historical data. |
| Constant Frequency | IF: - The loss of PCC involves the loss of EMS (LFC and RLC); THEN: - Instruct a QSE to go on Constant Frequency - Q#114 – Typical Script to Instruct a QSE on Constant Frequency for LRC/SCED Failure - Refer to Real-time desk procedure section 3.3, EMMS (LFC and RLC/SCED) Failure |
| Call in Additional Operators | Activate the NXT scenario to call in additional shift personnel, which includes a Shift Supervisor. SELECT: - SO Loss of Control Room at Taylor, OR; - SO Loss of Control Room at Bastrop. - An email will be received after 10 minutes with a report of who has responded along with their estimated time of arrival. |
| QSE Hotline Call | - Q#107 - Typical Hotline Script Emergency Notice Loss of Primary Control Center (Systems are NOT Functional) - If either Hotlines are inoperable, phone numbers can be found on SharePoint under OPX & LD Numbers. |
| TO Hotline Call | - T#92 - Typical Hotline Script Emergency Notice Loss of Primary Control Center (Systems are NOT Functional) - If either Hotlines are inoperable, phone numbers can be found on SharePoint under OPX & LD Numbers. |
| ERCOT Website Posting | As time permits, post the Emergency Notice on the ERCOT Website. - Typical Posting Script: ERCOT has issued an Emergency Notice for the loss of the primary control center, systems are not functioning. |
| Additional Notifications | - The Director Control Room Operations and/or Designee will notify the following: - Help Desk (to notify GMS Support and IT Infrastructure (Telecommunications and Data Center) - Engineering Support These phone numbers are also programmed into the control room cell phone. |
| Respond to QSEs | IF: - The QSE that is put on constant frequency needs assistance controlling frequency; THEN: - Issue a unit specific Operating Instruction to another QSE to help with Regulation. (Follow-up with electronic Dispatch Instruction as time permits) OR - Put a different QSE on constant frequency (Remember to take the first QSE off constant frequency). |
| Real-time Contingency Analysis (RTCA) | Operations Support will be responsible for the State Estimator and RTCA functionality and ensuring an RTA is performed at least every 30 minutes. They will communicate results and any suggested actions as needed. |
| Respond to TOs Thermal/ Voltage Limits Reached (SOL) | IF: - Notified by Operations Support or a TO that thermal limits have reached their continuous rating; THEN: - Seek a recommendation from Operations Support or the appropriate TO as to what actions will alleviate the situation, and issue unit specific Operating Instructions to appropriate QSE. - Continue to monitor to determine the effect of the plan. ERCOT Nominal Voltage Levels are 345kV, 230kV, 138kV, 115kV and 69kV. The general voltage guidelines are as follows (listed in kV): Nominal Voltage; Normal Operating Limits; Emergency Operating Limits; Ideal Voltage Range. 345; 327.75 – 362.25; 310.5 – 379.5; 345 – 359. 230; 218.5 – 241.5; 207 – 253; 230 – 240. 138; 131.1 – 144.9; 124.2 – 151.8; 138 – 144. 115; 109.25 – 120.75; 103.5 – 126.5; 115 – 120. 69; 65.55 – 72.45; 62.1 – 75.9; 69 – 71.5. Some TOs utilize different Normal (Basecase) and Emergency (Post-Contingency) voltage operating limits than the general voltage guidelines. These limits can be seen under the Network Limits display. WHEN: - Notified by Operations Support or a TO of voltage concerns; THEN: - Initiate a solution in collaboration with Operations Support and the appropriate TO and QSE in the area. WHEN: - TOs have utilized all Static Reactive Power Resources (capacitors, reactors, change in transformer taps) and a voltage issue still remains; THEN: - Instruct the appropriate QSE to raise or lower bus voltage, - The QSE should complete the requested in no more than five minutes. Typical Script: “This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is instructing [QSE] to [raise or lower] voltage at [specify bus] by [+1 or 2kV or -1 or 2kV] for a target of [target kV]. [QSE] please repeat this instruction back to me. That is correct, thank you.” |
| GTCs | IF: - Notified by Operations Support or a TO that a GTCs (which includes the IROL) is approaching 85% and is continuing to trend upward; THEN: - Seek a recommendation from Operations Support or the appropriate TO as to what actions will alleviate the situation, - Issue unit specific Operating Instructions as necessary to QSE, (Follow-up with electronic Dispatch Instructions as time permits). - Continue to monitor to determine the effect of the plan. |
| Thermal Limits Reached (SOL) | IF: - Notified by Operations Support or a TO that thermal limits have reached their emergency rating and are continuing to trend upward, THEN: - Seek a recommendation from Operations Support or the appropriate TO as to what actions will alleviate the situation, and issue unit specific Operating Instructions as necessary (Follow-up with electronic Dispatch Instruction as time permits) - Continue to monitor to determine the effect of the plan. |
| DC Tie Tags | Make every attempt to handle all DC Tie tags. If the workload makes it impossible to keep up with, the tags will be passively denied. |
| Electronic Dispatch Instruction | Follow-up with electronic Dispatch Instructions where appropriate when systems are functional or as time permits (See Desktop Guide Common to Multiple Desks section 2.3). When issuing a VDI or confirmation, ensure the use of three-part communication: - Issue the Operating Instruction - Receive a correct repeat back - Give an acknowledgement |
| Log | - Make log entry of events. |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Frosch, Hartmann, Stone, and Barcalow | Preparers | November 10, 2010 |
| Frosch and Hartmann | Procedure writers and editors | November 27, 2010 |
| Frosch and Hartmann | Procedure writers and editors | January 26, 2011 |
| Frosch and Hartmann | Procedure writers and editors | March 23, 2011 |
| Frosch and Hartmann | Procedure writers and editors | April 20, 2011 |
| Frosch and Hartmann | Procedure writers and editors | June 6, 2011 |
| Frosch and Hartmann | Procedure writers and editors | June 16, 2011 |
| Frosch and Hartmann | Procedure writers and editors | July 18, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 30, 2011 |
| Frosch and Hartmann | Procedure writers and editors | September 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | October 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 16, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | April 25, 2012 |
| Frosch and Hartmann | Procedure writers and editors | July 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | August 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | October 26, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 26, 2013 |
| Frosch and Hartmann | Procedure writers and editors | May 28, 2013 |
| Frosch and Hartmann | Procedure writers and editors | June 27, 2013 |
| Frosch and Hartmann | Procedure writers and editors | July 9, 2013 |
| Frosch and Hartmann | Procedure writers and editors | August 28, 2013 |
| Frosch and Hartmann | Procedure writers and editors | December 11, 2013 |
| Frosch and Hartmann | Procedure writers and editors | January 27, 2014 |
| Frosch and Hartmann | Procedure writers and editors | February 18, 2014 |
| Frosch and Hartmann | Procedure writers and editors | February 26, 2014 |
| Frosch, Gaddy and Hartmann | Procedure writers and editors | April 1, 2014 |
| Frosch, Gaddy and Hartmann | Procedure writers and editors | May 27, 2014 |
| Frosch, Gaddy and Hartmann | Procedure writers and editors | July 27, 2014 |
| Frosch and Hartmann | Procedure writers and editors | September 29, 2014 |
| Frosch Hartmann and Lopez | Procedure writers and editors | December 10, 2014 |
| Frosch and Hartmann | Procedure writers and editors | February 25, 2015 |
| Frosch and Hartmann | Procedure writers and editors | April 29, 2015 |
| Frosch, Hartmann and Gaddy | Procedure writers and editors | July 13, 2015 |
| Hartmann and Gaddy | Procedure writers and editors | December 22, 2015 |
| Hartmann, Gaddy and Frosch | Procedure writers and editors | February 23, 2016 |
| Hartmann, Gaddy and Frosch | Procedure writers and editors | April 22, 2016 |
| Hartmann, Gaddy and Frosch | Procedure writers and editors | June 24, 2016 |
| Hartmann and Gaddy | Procedure writers and editors | September 26, 2016 |
| Hartmann and Gaddy | Procedure writers and editors | October 31, 2016 |
| Hartmann and Gaddy | Procedure writers and editors | December 23, 2016 |
| Hartmann, Gaddy and Frosch | Procedure writers and editors | March 27, 2017 |
| Hartmann and Gaddy | Procedure writers and editors | April 5, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | May 26, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | September 27, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | October 27, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | December 22, 2017 |

| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | February 22, 2018 |
| --- | --- | --- |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | February 22, 2018 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | April 27, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | May 25, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | August 24, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | September 26, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | October 29, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | December 21, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | January 25, 2019 |
| Hartmann, Gaddy, Luker and Frosch | Procedure writers and editors | March 25, 2019 |
| Hartmann, Gaddy and Pence | Procedure writers and editors | May 13, 2019 |
| Hartmann, Gaddy and Pence | Procedure writers and editors | May 28, 2019 |
| Hartmann, Gaddy and Pence | Procedure writers and editors | July 29, 2019 |
| Hartmann, Gaddy, Cyphers and Frosch | Procedure writers and editors | October 29, 2019 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | December 20, 2019 |
| Hartmann, Gaddy, Cyphers and Frosch | Procedure writers and editors | June 25, 2020 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | September 23, 2020 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | October 26, 2020 |

| Hartmann, Gaddy, Cyphers and Sheets | Procedure writers and editors | December 23, 2020 |
| --- | --- | --- |
| Hartmann, Gaddy, Cyphers, Frosch and Sheets | Procedure writers and editors | March 26, 2021 |
| Hartmann, Gaddy, Cyphers and Sheets | Procedure writers and editors | April 29, 2021 |
| Hartmann, Gaddy, Cyphers and Sheets | Procedure writers and editors | June 28, 2021 |
| Hartmann, Gaddy, Cyphers and Frosch | Procedure writers and editors | December 17, 2021 |
| Hartmann, Gaddy, Cyphers and Frosch | Procedure writers and editors | February 24, 2022 |
| Hartmann, Gaddy, Cyphers and Frosch | Procedure writers and editors | March 31, 2022 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | July 26, 2022 |
| Hartmann, Gaddy, Cyphers and Frosch | Procedure writers and editors | December 22, 2022 |

Manual Change History

| Procedure | Ver/Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All Sections | 1.0 / 0 | New procedures for all sections for Nodal implementation | November 30, 2010 |
| 3.1 3.3 3.12 3.13 3.14 3.16 3.17 4.1 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Updated step 1 Updated step 1 Updated step 1 and added Log Updated step 4 Updated step 3 Updated step 1 and added Log Updated step 3 Updated Constant Frequency, Respond to QSE’s, Stability Limits Reached and Thermal Limits Reached | December 1, 2010 |
| 2.3 3.4 4.1 4.2 4.3 | 1.0 / 0 1.0 / 1 1.0 / 2 1.0 / 1 1.0 / 1 | Added new procedure Updated step 1 Updated steps “Constant Frequency”, “QSE Hotline Call”, “TO Hotline Call”, “Respond to QSEs” “Respond to TOs”, “Stability Limits” and added “Nuclear Plants” Updated Note and “Additional Operators” Updated Hotline in “Notifications” | January 31, 2011 |
| 2.3 3.1 3.2 3.3 3.7 4.1 4.2 4.3 4.4 4.5 4.6 4.7 4.8 4.9 | 1.0 / 1 1.0 / 2 1.0 / 1 1.0 / 2 1.0 / 1 - / 2 1.0 / 2 - / 2 1.0 / 1 1.0 / 2 1.0 / 2 1.0 / 3 - / 2 1.0 / 2 | Updated NXT Test Updated 4th Note and step 1 Updated step 2 Updated 5th note, step 1, deleted step 4 and 6th Note Updated all sections Section number changed from 3.12 and updated all steps Section number changed from 3.13 and updated all steps Section number changed from 3.14 and updated all steps Section number changed from 3.15 and updated all steps Section number changed from 3.16 and updated step 1 Section number changed from 3.17 and updated step 1 Section number changed from 4.1 & updated multiple steps Section number changed from 4.2 & Note Section number changed from 4.3 | March 25, 2011 |
| 1.1 2.3 3.1 3.2 3.3 3.4 3.5 3.6 3.7 3.8 3.9 3.10 4.1 4.2 4.3 4.4 4.5 4.6 4.7 4.9 | 1.0 / 1 1.0 / 2 1.0 / 3 1.0 / 2 1.0 / 3 1.0 / 2 1.0 / 1 1.0 / 1 - / 2 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 3 1.0 / 3 1.0 / 3 1.0 / 2 1.0 / 3 1.0 / 3 1.0 / 4 1.0 / 3 | Updated text Updated step “Beginning of each Shift” Updated 1st & 3rd note and step 1, deleted 2nd note and added 5th note Updated 1st note and step 2 Updated 1st & 4th note, step 1 & 2, deleted 2nd and added 5th note Updated 1st & step 1 Updated steps 1, 2 and 3 Updated “Import” step 1 and “Export” steps 1 & 2 Updated all sections Updated all sections Updated all sections Updated 1st & 2nd note and step 1 and 2 Updated 1st note and step 1 Updated 1st note Updated 1st note Updated step 3 Updated step 1 Updated step 2 Updated step QSE Hotline Call Updated step 1 in Watch and Emergency Notice | April 22, 2011 |
| 3.1 3.2 3.3 3.4 3.5 3.6 3.73.8 3.9 3.10 3.11 4.1 4.2 4.3 4.4 4.5 4.6 4.7 4.9 | 1.0 / 4 1.0 / 3 1.0 / 4 1.0 / 3 1.0 / 2 1.0 / 2 1.0 / 31.0 / 2 1.0 / 1 1.0 / 2 1.0 / 1 1.0 / 4 1.0 / 4 1.0 / 3 1.0 / 3 1.0 / 4 1.0 / 4 - / 5 1.0 / 4 | Updated all steps Updated all steps Updated all steps Updated step 1 Updated step 1, 2, 3 & added 2nd note Updated step 1 and 2 Updated all steps Updated all steps Updated all steps Updated 3rd note and step 1 Updated all steps Updated all steps Updated all steps Updated all steps Updated all steps Updated step 1 Updated steps 2 & 3 Updated steps Call in Additional Operators and Respond to QSEs Updated all steps | June 8, 2011 |
| 3.1 3.3 3.7 3.9 4.2 | 1.0 / 5 1.0 / 5 1.0 / 4 1.0 / 2 1.0 / 5 | Changed 3rd Note to step 1, updated step 1 & 2 Updated step 1 Updated all steps in DC Tie Trips, step 1 in Transmission Issues within ERCOT & step 1 & 2 in Transmission Issues within CFE Updated webtrans references Updated step 1 | June 17, 2011 |
| 3.1 3.3 3.6 3.7 3.9 3.11 4.1 4.2 4.3 4.4 4.5 4.6 4.7 4.8 | 1.0 / 6 1.0 / 6 1.0 / 3 1.0 / 5 1.0 / 3 1.0 / 2 1.0 / 6 1.0 / 4 1.0 / 5 1.0 / 5 1.0 / 5 1.0 / 5 1.0 / 2 1.0 / 5 | Updated 1st Note and step 1 & 2 Updated step 1 Updated all steps Split procedure out, changed title and moved Transmission Issue within ERCOT to 4.5 Updated step 2 Updated steps 2, 4 and 5 Updated step 1, added steps 2 - 4 Updated all steps, added new step 3 Updated Turret phone label for SPP Tariff and all steps Changed section number from 4.4 to 4.3 and updated all steps Changed section number from 4.5 to 4.4 and updated all steps Changed section number from 4.6 to 4.5, updated all steps and moved Transmission Issues from 3.7 to 4.5 Changed section number from 4.7 to 4.6 Changed section number from 4.8 to 4.7 Changed section number from 4.9 to 4.8 and updated step 1 in Watch | July 20, 2011 |
| 2.3 3.1 3.2 3.3 3.6 3.7 3.8 3.9 3.11 4.1 4.2 4.3 4.5 4.6 4.8 | 1.0 / 3 1.0 / 7 1.0 / 4 1.0 / 7 1.0 / 4 1.0 / 6 1.0 / 3 1.0 / 4 1.0 / 3 1.0 / 7 1.0 / 5 1.0 / 6 1.0 / 6 1.0 / 6 1.0 / 6 | Updated step “Beginning of each Shift” Updated 1st note Updated steps 1, 2 & 3 Updated 1st, 4th note and step 1 Updated step 1 “Imports” and step 2 “Exports” Updated Steps 1, 2 and 4 in “CFE DC-Ties” Updated 2nd note and steps 1-3 Updated steps 1-3 Updated steps 1 and 2 Updated all steps Updated all steps Updated all steps Updated all steps Removed reference of Austin Control Room Added projected reserve capacity shortage and Extreme Hot Weather in Watch | September 1, 2011 |
| 3.1 3.3 4.1 4.2 4.3 | 1.0 / 8 1.0 / 8 1.0 / 8 1.0 / 6 1.0 / 7 | Updated step 2 Updated step 1 Updated Turret Phone, step 3a in Comision Federal de Electricidad (CFE) and step 5b to implement NPRR 379 Updated Turret Phone and step 3a in Comision Federal de Electricidad (CFE) Updated step 3 | October 1, 2011 |
| 4.6 | 1.0 / 7 | Updated step TO Hotline Call | November 1, 2011 |
| 3.1 3.3 4.6 4.8 | - / 9 1.0 / 9 1.0 / 8 1.0 / 7 | Updated step 2 Updated step 1 Added new section and updated all steps Updated Post in “Notifications” All procedures in this manual have been reviewed. | December 15, 2011 |
| 1.2 3.1 3.3 4.6 | 1.0 / 1 1.0 / 10 1.0 / 10 1.0 / 9 | Updated Scope Updated step 2 Updated step 1 Updated Hotline call scripts | January 19, 2012 |
| 2.1 2.3 3.1 3.2 3.7 4.1 4.2 4.3 4.5 4.8 | 1.0 / 1 1.0 / 4 1.0 / 11 1.0 / 5 1.0 / 7 1.0 / 9 1.0 / 7 1.0 / 8 1.0 / 7 1.0 / 8 | Added dispatch instructions paragraph Updated Desktop Guide reference Added 3rd Note Changed Shift Engineer to Operations Support Updated Desktop Guide references Updated Desktop Guide references Updated Desktop Guide references Updated Desktop Guide references Updated 2nd Note & all steps 1 – 3 Updated step 1 of Watch | March 1, 2012 |
| 3.1 3.3 3.7 3.8 3.9 4.54.6 4.8 | 1.0 / 12 1.0 / 11 1.0 / 8 1.0 / 4 1.0 / 5 1.0 / 8 1.0 / 10 1.0 / 9 | Updated step 2 Updated 3rd Note and step 1 Added posting and cancelling messages Updated overview Updated overview Updated procedure based on NPRR405 Updated W-N or N-H steps Updated OCN, Advisory, Watch and Emergency Notice for Cold Weather and Extreme Cold Weather | May 1, 2012 |
| 1.3 3.2 3.8 3.9 4.5 4.6 4.8 | 1.0 / 1 1.0 / 6 1.0 / 5 1.0 / 6 1.0 / 9 1.0 / 11 1.0 / 10 | Removed ERCOT Shift Supervisor paragraph Updated step 1 Updated step 4 Updated step 4 Added step Turret Phone & 1st Note, updated step 4 Updated several steps based on lessons learned from classroom training and simulation Updated all step 1’s | July 16, 2012 |
| 3.1 | 1.0 / 13 | Updated step 2 | August 29, 2012 |
| 2.2 3.2 4.5 4.6 | 1.0 / 1 1.0 / 7 1.0 / 10 1.0 / 12 | Added Hotline Call Communication Updated 1st Note Updated 1st and 2nd Note Updated steps West to North & North to Houston(IROL) All procedures in this manual have been reviewed. | November 1, 2012 |
| 3.1 3.10 4.6 | 1.0 / 14 1.0 / 3 1.0 / 13 | Updated step 2 Updated 2nd note Updated Additional Notifications on Systems Functional and Systems are not Functional | March 1, 2013 |
| 3.1 3.2 3.7 3.11 4.6 | 1.0 / 15 1.0 / 8 1.0 / 9 1.0 / 4 1.0 / 14 | Updated step 2 Updated step 1, deleted steps 2 & 3 Updated scripts Updated script Updated scripts, West to North & step North to Houston | June 1, 2013 |
| 3.6 4.3 4.4 4.5 4.6 | 1.0 / 5 1.0 / 9 1.0 / 6 1.0 / 11 1.0 / 15 | Updated Exports, step 1 Updated step 1 & 3 Updated step 1 Deleted 2nd Note, updated step 1, 2 & 4 Added Monitor Frequency and updated Constant Frequency | July 1, 2013 |
| 3.1 3.3 3.11 4.8 | 1.0 / 16 1.0 / 12 1.0 / 5 1.0 / 11 | Updated step 1 Updated 4th note Updated step 1 Updated step 1 in Watch & Emergency Notice | July 15, 2013 |
| 3.7 4.6 | 1.0 / 10 1.0 / 16 | Added CFE DC-Tie Derates and AEP DC-Tie Derates Removed HHGT TO reference | August 30, 2013 |
| 1.1 3.3 3.4 3.5 3.6 3.8 3.9 3.11 4.1 4.2 4.5 | 1.0 / 2 1.0 / 13 1.0 / 4 1.0 / 3 1.0 / 6 1.0 / 6 1.0 / 7 1.0 / 6 1.0 / 10 1.0 / 8 1.0 / 12 | Changed “Security” to “Reliability” Updated step 2 Updated both steps Updated last Note and step 3 Updated the Notes and step 1 and 2 Updated step 2 Updated step 2 New Loss of DC-Tie Operator E-tagging Updated step 6b Updated step 6b Added note to Transmission Issues within CFE All procedures in this manual have been reviewed. | December 13, 2013 |
| 3.8 4.1 4.2 4.3 4.4 4.5 4.8 | 1.0 / 7 1.0 / 11 1.0 / 9 1.0 / 10 1.0 / 7 1.0 / 13 1.0 / 13 | Updated step 2 Updated step Turret Phone, 3a, 6b, Note, & 7b Updated step Turret Phone, 3a, 6b, Note, & 7b Updated step 3 Updated step 2 Updated step Turret Phone & 4 Updated all step 1’s | January 29, 2014 |
| 3.3 3.6 3.7 3.9 3.10 3.11 3.12 4.1 4.2 4.3 4.5 | 1.0 / 14 1.0 / 7 1.0 / 11 1.0 / 8 1.0 / 0 1.0 / 4 1.0 / 7 1.0 / 12 1.0 / 10 1.0 / 11 1.0 / 14 | Updated 1st & 4th Note & step 1 to include Sharyland as Tie Operator Updated steps 1 & 2 Updated steps 1, 2, 3 & Cancel Message Updated 1st Note, step 2, 3 & 5 New procedure Updated section number Updated section number & step 2 Updated Turret Phone, 1st Note, CFE & SPP sections Updated Turret Phone, 1st Note, CFE & SPP sections Updated 1st None, steps 1, 2 & 3 Updated to include Sharyland change | February 25, 2014 |
| 3.1 3.4 3.5 3.7 3.8 3.9 3.10 3.11 3.12 4.1 4.24.3 4.4 4.5 4.6 4.7 4.8 | 1.0 / 17 1.0 / 5 1.0 / 4 1.0 / 12 1.0 / 8 1.0 / 9 1.0 / 1 1.0 / 5 - / 8 - / 13 - / 11 1.0 / 12 1.0 / 7 1.0 / 15 1.0 / 17 1.0 / 3 1.0 / 14 | Updated 1st Note Updated step 1 Updated steps 2 and 3 Updated step Post Message Updated steps Note through 5 Updated step 5 Updated step 5 Updated 1st Note, steps 1 to CFE DC-Ties and 2 to SPP DC-Ties Updated steps 2, 4 & 5 on Loss of ERCOT E-Tagging and step 1 on Loss of DC Tie Operator E-Tagging Updated steps Turret Phone, Note, 2b, 3b, 4b & 6b on Southwest Power Pool (SPP) Deleted ERCOT Declares EEA 2 or 3 Re-numbered procedure to 4.2 Delete Emergency Energy to SPP procedures Re-numbered procedure to 4.3 Re-numbered procedure to 4.4 Re-numbered procedure to 4.5 Re-numbered procedure to 4.6 | March 1, 2014 |
| 3.1 3.2 4.1 4.2 4.3 4.4 | 1.0 / 18 1.0 / 9 1.0 / 14 - / 13 - / 16 - / 18 | Updated step 2 Updated step 1 & 2 Updated VDI information Updated VDI information Updated VDI information Updated VDI information & Updated Guide Reference | April 4, 2014 |
| 2.2 3.1 3.3 3.8 3.9 3.10 4.1 4.6 | 1.0 / 2 1.0 / 19 1.0 / 15 1.0 / 9 1.0 / 10 1.0 / 2 1.0 / 15 1.0 / 15 | Added VDIs to Master QSEs Updated step 2 Updated step 1 Updated Monitor, deleted step Caution & added step 5 Updated Monitor & deleted step Caution Updated Monitor & deleted step Caution Updated title Added Note, updated Advisory & Watch | June 1, 2014 |
| 3.1 3.3 3.8 4.3 | 1.0 / 20 1.0 / 16 1.0 / 10 1.0 / 17 | Updated step 2 Updated step 1 & 2 Updated 2nd Note Updated step 4 in Emergency Condition within CFE | August 1, 2014 |
| 3.1 3.3 4.2 4.3 4.6 | 1.0 / 21 1.0 / 17 1.0 / 14 1.0 / 18 1.0 / 16 | Updated step 2 Updated step 1 Spilt step 3 into two steps for clarification Spilt step 4 into two steps for clarification Updated Generic Script | October 1, 2014 |
| 3.8 3.9 3.10 4.1 4.2 4.3 4.4 | 1.0 / 11 1.0 / 11 1.0 / 3 1.0 / 16 1.0 / 15 1.0 / 19 1.0 / 19 | Updated step 6 Updated step 5 Updated step 5 Updated step EEA Updated step Note Updated step 2nd Note Updated TO scripts, delete W-Ns & revised GTLs All procedures in this manual have been reviewed | December 15, 2014 |
| 2.2 3.8 4.1 4.2 4.3 4.4 | 1.0 / 3 1.0 / 12 1.0 / 17 1.0 / 16 1.0 / 20 1.0 / 20 | Added Dispatch and VDI definition Correction to step 5 Reformatted section Reformatted section Corrected VDI/Dispatch Instruction language Reformatted section | March 1, 2015 |
| 3.8 4.1 4.4 | 1.0 / 13 1.0 / 18 1.0 / 21 | Correction to step 2 Updated step 2 & 4 on DC-Ties with Southwest Power Pool (SPP) Updated GTL to new term GTC | May 1, 2015 |
| 3.1 3.3 | 1.0 / 22 1.0 / 18 | Updated step 2 Updated 4th Note and step 1 | July 15, 2015 |
| 4.1 | 1.0 / 19 | Added step 3, 4, and Log to DC-Ties with Comisión Federal de Electricidad (CFE) All procedures in this manual have been reviewed | December 31, 2015 |
| 1.3 2.1 | 1.0 / 2 1.0 / 2 | Removed Interchange Coordinator Updated System Operator Responsibility and Authority | March 1, 2016 |
| 3.1 3.2 3.3 3.4 3.5 | 1.0 / 23 1.0 / 10 1.0 / 19 1.0 / 6 1.0 / 5 | Added Note 4 Updated steps 1, 2 & 3 Added Note 4, & renumbered steps Updated step 1 Updated steps 1, 2 & 3, deleted 2nd Note | April 29, 2016 |
| 2.1 2.2 4.1 4.2 4.3 4.4 4.6 | 1.0 / 3 1.0 / 4 1.0 / 20 1.0 / 17 1.0 / 21 1.0 / 22 1.0 / 17 | Updated for COM-002-4 Updated for COM-002-4 Updated for COM-002-4 Updated Step Electronic Dispatch Instruction Updated for COM-002-4 Updated Step Electronic Dispatch Instruction Updated for COM-002-4 Updated Step Electronic Dispatch Instruction Updated for COM-002-4 Updated for COM-002-4 | June 30, 2016 |
| 3.2 3.3 3.6 3.12 | 1.0 / 11 1.0 / 20 1.0 / 8 1.0 / 9 | Updated Note, Step 1 and Step 2. Removed Step 3 Updated Step 2 Updated Exports Step 1 Moved Exports step 2 to step 3 Added Exports Step 2 Updated Step 3 | September 30, 2016 |
| 3.2 3.3 | 1.0 / 12 1.0 / 21 | Updated Procedure Purpose Updated step Note Added step Adjustment Period Updated step 1 & 2 Updated step 2 | November 2, 2016 |
|  |  | All procedures in this manual have been reviewed | December 30, 2016 |
| 1.3 2.1 2.3 3.2 3.3 3.6 3.7 3.9 3.10 3.11 4.1 4.2 4.3 4.6 | 1.0 / 3 1.0 / 4 1.0 / 5 1.0 / 13 1.0 / 22 1.0 / 9 1.0 / 13 1.0 / 12 1.0 / 4 1.0 / 6 1.0 / 21 1.0 / 18 1.0 / 22 1.0 / 18 | Deleted section 1.3 Updated for IRO-001-4 Updated step NXT Updated CFE to CENACE Updated CFE to CENACE Updated CFE to CENACE Updated CFE to CENACE Updated CFE to CENACE Updated CFE to CENACE Updated CFE to CENACE Updated CFE to CENACE Updated CFE to CENACE Updated CFE to CENACE Updated heading title and OCN step 1 | March 31, 2017 |
| 4.3 | 1.0 / 23 | Transmission Watch Issued for Post-Contingency Overloads on the South DC Ties Added section Transmission Watch Issued for the Rio Grande Valley Import | April 6, 2017 |
| 3.2 3.7 3.10 4.2 4.3 | 1.0 / 14 1.0 / 14 1.0 / 5 1.0 / 19 1.0 / 24 | Updated all steps Updated step 1 & 2 Updated step 1 Updated step 1 Updated second note and step 4 in Emergency Condition within CENACE | June 1,2017 |
| 3.1 | 1.0 / 24 | Added East HVDC Tie Voltage Limits | September 29, 2017 |
| 3.3 | 1.0 / 23 | Moved step 4 to step 2 and deleted step 4 | October 31, 2017 |
|  |  | All procedures in this manual have been reviewed | December 28, 2017 |
| 3.5 4.1 | 1.0 / 6 1.0 / 22 | Updated steps Added new step #4 and updated step #4 to #5 | February 28, 2018 |
| 3.3 | 1.0 / 24 | Updated for NPRR861 | March 30, 2018 |
| 2.2 3.3 3.8 3.9 3.10 | 1.0 / 5 1.0 / 25 1.0 / 14 1.0 / 13 1.0 / 6 | Updated procedure purpose Updated step 2 Updated steps 2, 3, 4 & 6 Updated steps 3, 4, & 5 Updated steps 3, 4, & 5 | May 1, 2018 |
| 4.1 4.2 4.3 | 1.0 / 23 1.0 / 20 1.0 / 25 | Updated Electronic Dispatch Instruction steps Updated Electronic Dispatch Instruction steps Updated Emergency Condition within ERCOT step 5 | May 31, 2018 |
| 3.1 3.3 4.1 4.2 4.3 | 1.0 / 25 1.0 / 26 1.0 / 24 1.0 / 21 1.0 / 26 | Updated step 1 Updated step 1 Updated steps Electronic Dispatch Instruction Updated steps Electronic Dispatch Instruction Updated second note and Updated Emergency Condition within ERCOT step 5 | August 31, 2018 |
| 3.2 3.3 3.5 3.6 3.7 3.10 4.1 4.2 4.3 | 1.0 / 15 1.0 / 27 1.0 / 7 1.0 / 10 1.0 / 15 1.0 / 7 1.0 / 25 1.0 / 22 1.0 / 27 | Updated for NPRR825 Updated for NPRR825 Updated for NPRR825 Updated for NPRR825 Updated for NPRR825 Updated for NPRR825 Updated for NPRR825 Updated for NPRR825 Updated for NPRR825 | October 1, 2018 |
| 3.6 3.7 4.1 4.2 4.3 | 1.0 / 11 1.0 / 16 1.0 / 26 1.0 / 23 1.0 / 28 | Added step to cancel message Added steps to cancel message Added steps to post and cancel messages Added step to cancel message Added steps to post and cancel messages | November 1, 2018 |
|  |  | All procedures in this manual have been reviewed | December 28, 2018 |
| 3.3 | 1.0 / 28 | Updated step 2 | January 31, 2019 |
| 3.3 3.6 3.8 4.4 | 1.0 / 29 1.0 / 12 1.0 / 15 1.0 / 23 | Updated step 2 Added step Note Updated SPP Interchange to SPP Balancing Updated step Contact Security | March 29, 2019 |
| 3.3 3.6 3.10 3.12 4.1 4.2 4.3 | 1.0 / 30 1.0 / 13 1.0 / 8 1.0 / 10 1.0 / 27 1.0 / 24 1.0 / 29 | Updated SHARYLAND to ONCOR Updated SHARYLAND to ONCOR Updated SHARYLAND to ONCOR Updated SHARYLAND to ONCOR Updated SHARYLAND to ONCOR Updated SHARYLAND to ONCOR Updated SHARYLAND to ONCOR | May 16, 2019 |
| 3.1 3.3 | 1.0 / 26 1.0 / 31 | Updated step 1 & 2 Updated step 1 & 2 | May 31, 2019 |
| 4.1 4.4 | 1.0 / 28 1.0 / 24 | Added Note DC-Ties with Southwest Power Pool (SPP) Moved Typical Hotline Scripts to Scripts | August 1, 2019 |
| 4.4 | 1.0 / 25 | Updated steps | November 1, 2019 |
| 3.11 4.4 | 1.0 / 7 1.0 / 26 | Updated Note Updated Additional Notifications All procedures in this manual have been reviewed | January 1, 2020 |
| 2.1 3.2 3.3 3.7 3.9 4.1 4.3 4.4 | 1.0 / 5 1.0 / 16 1.0 / 32 1.0 / 17 1.0 / 14 1.0 / 29 1.0 / 30 1.0 / 27 | Added Advance Action Notice per NPRR930 Deleted Eagle Pass DC_S due to retirement Deleted Eagle Pass DC_S due to retirement Deleted Eagle Pass DC_S due to retirement Deleted Eagle Pass DC_S due to retirement Deleted Eagle Pass DC_S due to retirement Deleted Eagle Pass DC_S due to retirement Updated steps | July 1, 2020 |
| 3.1 4.4 | 1.0 / 27 1.0 / 28 | Updated step 2 Updated with new IROL’s | October 1, 2020 |
| 4.4 | 1.0 / 29 | Updated IROL’s | October 31, 2020 |
| 3.1 3.2 3.3 3.5 3.6 3.7 3.8 3.10 3.12 4.1 4.2 4.3 4.4 4.6 | 1.0 / 28 1.0 / 17 1.0 / 33 1.0 / 8 1.0 / 14 1.0 / 18 1.0 / 16 1.0 / 9 1.0 / 11 1.0 / 30 1.0 / 25 1.0 / 31 1.0 / 30 1.0 / 19 | Updated 1st note contact Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 Updated SPP Balancing to SPP RTBM Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 & added Note All procedures in this manual have been reviewed | December 31, 2020 |
| 3.1 3.8 3.9 3.10 4.4 | 1.0 / 29 1.0 / 17 1.0 / 15 1.0 / 10 1.0 / 31 | Removed Oklaunion exemption Organization change Organization change Organization change Organization change | April 1, 2021 |
| 4.6 | 1.0 / 20 | Changed Notice Builder to Grid Conditions Communications (GCC) Notices | May 6, 2021 |
| 3.1 3.3 4.4 | 1.0 / 30 1.0 / 34 1.0 / 32 | Updated Note Updated Note Deleted McCamey Export IROL | July 1, 2021 |
| 2.2 4.3 4.4 4.6 | 1.0 / 6 1.0 / 32 1.0 / 33 1.0 / 21 | Updated step 1 Updated steps 1, 2, & 4 Added McCamey Export IROL Updated all steps All procedures in this manual have been updated | December 31, 2021 |
| 2.4 3.1 3.3 3.5 | 1.0 / 0 1.0 / 31 1.0 / 35 1.0 / 9 | New procedure section Updated step 1 Updated step 1 Add TLR note | March 1, 2022 |
| 4.4 | 1.0 / 34 | Added Note | April 7, 2022 |
| 3.1 3.3 | 1.0 / 32 1.0 / 36 | Updated step 1 Updated step 1 | July 29, 2022 |
| 3.1 3.3 4.4 | 1.0 / 33 1.0 / 37 1.0 / 35 | Updated 5th note Updated 5th note Updated Voltage tables All procedure in this manual have been reviewed | December 30, 2022 |