- Power Operations Bulletin # 1091

ERCOT has posted/revised the Real Time manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

- http://www.ercot.com/mktrules/guides/procedures/index.html

## 3.1	Frequency Control Operating Procedure

Procedure Purpose: To control frequency within defined limits.

| Protocol Reference | 6.5.7.6.2.2(7),(16) | 6.5.9.1(1)(b) |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 2.2.4 | 2.2.8 | 2.3.1.2 | 4.8.1 |
| NERC Standard | BAL-001-2 R2 | IRO-001-4 R1 | NUC-001-4 R4, R4.1, R4.2, R9, R9.2, R9.2.1, R9.4, R9.4.1, R9.4.2 | TOP-001-5 R2, R11 |

| Version: 1 | Revision: 41 | Effective Date: June 30, 2023 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Maintain System Frequency |  |
| Objective | - Frequency should be maintained within +/- 0.03 Hz of schedule - Attempt to maintain CPS1 scores over 100 - Operate within the BAAL - Frequency Bias set to 895 MW/0.1Hz |
| CPS1 less than 100 | IF: - Performance drops below 100 for over three consecutive hours; THEN: - LOG the event and the possible cause of the poor performance. |
| BAAL | Corrective action shall be taken whenever the clock-minute average ACE is outside its clock-minute average Balancing Authority ACE Limit (BAAL). This is to ensure that the Balancing Authority ACE does not remain outside the BAAL for more than 30 consecutive clock-minutes. |
| Caution | NEVER (unless directed by GMS Support or Support Engineer): - Change other tuning parameters (including QSE ramp rates, dead bands, thresholds, gains, time constraints) |
| Base Point Deviation | REVIEW REFERENCE DISPLAY: EMP Applications>Generation Area Status>Related Displays>Expected Generation and Load Details Not-Tracking Units tab IF: - A QSE has a Resource with a large Base Point deviation (not tracking unit flag), AND - Their generation is not moving in the proper direction to correct their Base Point Deviation; THEN: - Notify the QSE of the issue. |
| Frequency Deviations | IF: - Frequency deviations are equal to or greater than +/- 0.10 Hz, OR - Sudden loss of generation greater than 450 MW; THEN: - Ensure frequency recovers to pre-disturbance within 15 minutes - Manually run SCED or use offset as needed. LOG: - Log the following information: - Possible reasons, if known (Base Point deviation, large schedule change, unit trip, DC-Tie trip, etc.) - If unit trip: - Time of unit trip or DC-Tie, - Name of unit or DC-Tie, - Approximate net MW, - Approximate lowest TrueTime frequency (use 3 decimals), - Amount of ECRS released (if any), AND - Approximate ERCOT load. |
| Hydro Generation Operating in Synchronous Condenser Fast Response Mode | IF: - Hydro Resources operating in synchronous condenser fast-response mode who provide MW to the System in response to a frequency event without a ERCOT Contingency Reserve Service (ECRS) or Responsive Reserve Service (RRS) deployment; THEN: - QSE will request an electronic Dispatch Instruction confirmation - Choose Resource tab - Choose requesting QSE for Participant Name - Choose Resource name - Enter MW amount deployed in Current Operating Level - Choose Other For Resource for Instruction Type - State Hydro deployed in response to frequency in Other Information - Initiation Time, and - Completion Time When issuing a VDI or the confirmation, ensure the use of three-part communication: - Issue the Operating Instruction - Receive a correct repeat back - Give an acknowledgement - An electronic Dispatch Instruction confirmation will be needed for each Resource. IF: - QSE contacts ERCOT to determine if it is allowed to recall and reset; THEN: - ERCOT grants approval to come off-line once the frequency recovers to pre-disturbance level or 60 Hz, whichever is lower, OR - Request QSE to remain On-line - May not exceed 30 minutes per release for each frequency deviation or event - Shall not exceed two hours per a 12-hour period in aggregate unless an EEA is declared |
| ### Response to High Frequency |  |
| BAAL Sheet | Located on the realtime drive in the _Operations Official Spreadsheets folder. Open BAAL ERCOT Interconnection and select Control T simultaneously. |
| Monitor | IF: - Frequency goes above 60.05 Hz and exceeds 60.05 Hz > 5 minutes AND - Regulation Down service remains and is deploying; THEN: - Manually run SCED - Call QSEs with Resources that have positive Base Point deviations and issue an Operating Instruction to bring their Base Point deviations to zero. IF: - Frequency goes above 60.05 Hz, AND - Out of Down Regulation; THEN: - CHECK the GEN-LDL or Cap to decrease BP on the EMS to ensure there is adequate down room, - Manually run SCED. IF: - There is no generation left for SCED to lower; THEN: - Coordinate with the Shift Supervisor and Transmission Operator to select a Resource to RUC decommit, - Request RUC Operator to issue an Operating Instruction to RUC decommit Resource. |
| 10 MINUTES | REFERENCE DISPLAY: EMP Applications>Generation Unit Status>Related Displays>Expected Generation and Load Details>Top Ten button AND Market Operation>Real-Time Market>SCED Displays>DSI Displays>DSI Data Processes>DSI Generation Requirement Manual Adjustment IF: - 10 consecutive minutes of ACE above BAALHigh (60.09 Hz); THEN: - Call QSEs with Resources that have positive Base Point deviations and issue an Operating Instruction to bring their Base Point deviations to zero, - Verify SCEDs capacity to decrease Base Points GEN-LDL, - Enter manual offset, - Manually run SCED (do not run SCED more than once between SCED runs). |
| Notify | If it is recognized that Frequency is or expected to be outside +/- 0.1 Hz for a non-transient event and will not recover within 15 minutes, notify the Nuclear Power Plants QSEs. |
| 15 Minutes | IF: - 15 consecutive minutes of ACE above BAALHigh (60.09 Hz); THEN: - Call QSEs with Resources that have positive Base Point deviations and issue an Operating Instruction to bring their Base Point deviations to zero, - Verify SCEDs capacity to decrease Base Points GEN-LDL, - Re-adjust manual offset, - Manually run SCED, - Log the event and notify Operations Support Engineer to send an event notification to OperationsAnalysis@ercot.com. IF: - There is no generation left for SCED to lower; THEN: - Coordinate with the Shift Supervisor and Transmission Operator to select a Resource to RUC decommit, - Request RUC Operator to issue Operating Instruction to RUC decommit Resource. |
| 20 Minutes | IF: - 20 consecutive minutes of ACE above BAALHigh (60.09 Hz) and Frequency is above 60.10 Hz; THEN: - Call QSEs with Resources that have positive Base Point deviations and issue an Operating Instruction to bring their Base Point deviations to zero - Curtail appropriate amount of DC-Tie imports (issue an Emergency), - Coordinate with Shift Supervisor, Transmission Operator to select an additional Resource to RUC decommit, - Request RUC Operator to issue Operating Instruction to RUC decommit Resource. |
| 25 Minutes | IF: - 25 consecutive minutes of ACE above BAALHigh (60.09 Hz) and Frequency is above 60.10 Hz; THEN: - Call QSEs with Resources with positive Base Point deviations and issue an Operating Instruction to take their Resource off-line. - Coordinate with Shift Supervisor, Transmission Operator to select an additional Resource to RUC decommit, - Request RUC Operator to issue Operating Instruction to RUC decommit Resource. |
| Stable | IF: - A manual offset was used; THEN: - Ensure that it has been removed. |
| Log | Log all actions. |
| ### Response to Low Frequency |  |
| BAAL Sheet | Located on the realtime drive in the _Operations Official Spreadsheets folder. Open BAAL ERCOT Interconnection and select Control T simultaneously. |
| NOTE | Responsive Reserve Service - Primary Frequency Response (RRS-PFR) - Fast Frequency Response (RRS-FFR) - Units - Controllable Load Resource (CLR) - Non-Controllable Load Resource (NCLR) - Under Frequency Response (RRS-UFR) |
| NOTE | The minimum capacity required from Gen Resources providing RRS using Primary Frequency Response shall not be less than 1,150 MW. |
| NOTE | UFRs will deploy as follows: - Fast Frequency Response (FFR) – 59.85 Hz - Hydro RRS (ONRR), Hydro ECRS (ONECRS) - 59.80 Hz - Load Resource providing RRS, Load Resources providing ECRS with relay armed – 59.70 Hz |
| NOTE | Manually deploy Load Resources other than Controllable Load Resources providing ECRS or RRS before entering an Energy Emergency Alert (EEA), to maintain a minimum 500 MWs of Physical Responsive Capability (PRC) reserves on Generation Resources. Deployment order starts with Group 0 Resources, and then next higher order group. |
| Monitor/ Release | IF: - Frequency drops below 59.95 Hz, AND - Regulation Up service remains and is deploying; THEN: - Manually run SCED (do not run SCED more than once between SCED runs) - Call QSEs with Resources with negative Base Point deviations and issue an Operating Instruction to bring their Base Point deviations to zero. IF: - Frequency drops below 59.95 Hz, AND - Out of Up Regulation; THEN: - Check the GTBD[HDL] on the Splunk SCED GEN ONLINE Dashboard or Cap to increase BP or HDL-Gen on the EMS and enter appropriate manual offset (the offset will continue until removed). Do not commit a manual offset while SCED is running. - If using Splunk Dashboard, do not enter an offset > than GTBD[HDL] - If using EMS, do not enter an offset > than Cap to increase BP or HDL-Gen IF: - Frequency is below 59.95 Hz and out of Up Regulation, AND - There is not adequate up room; THEN: - Manually release SCED dispatchable ECRS using the ERCOT Nodal Summary display on the EMS - Check the box labeled “Activate Manual ECRS” to activate, - Enter the “Manual ECRS Desired MW”, - Select Enter, - Select Commit. - QSE’s have one minute to update ECRS schedule to free up the capacity, SCED will automatically run after one minute. - Remember to remove the manual ECRS amount when frequency has recovered. IF: - Frequency is below 59.95 Hz and out of Up Regulation, AND - There is not adequate up room; - SCED dispatchable ECRS has already been released. THEN: - Manually release RRS from PFR using the ERCOT Nodal Summary display on the EMS - Check the box labeled “Activate Manual Responsive Reserve” to activate, - Enter the “Desired RRS MW”, - Select Enter, - Select Commit. - QSE’s have one minute to update RRS schedule to free up the capacity, SCED will automatically run after one minute. Remember to remove the manual RRS amount when frequency has recovered. |
| 10 Minutes | REFERENCE DISPLAY: EMP Applications>Generation Unit Status>Related Displays>Expected Generation and Load Details>Top Ten button AND Market Operation>Real-Time Market>SCED Displays>DSI Displays>DSI Data Processes>DSI Generation Requirement Manual Adjustment IF: - 10 consecutive minutes of ACE is less than BAALLow (59.91 Hz); THEN: - Call QSEs with Resources with negative Base Point deviations and issue an Operating Instruction to bring their Base Point deviations to zero, - Confirm ECRS has been released, - Verify SCEDs capacity to increase Base Points, - Enter manual offset - If room is available - Manually run SCED IF: - There is no generation left for SCED to increase; THEN: - Coordinate with the Shift Supervisor and Resource Operator to deploy Non-Spin, - Manually release ECRS using the ERCOT Nodal Summary display on the EMS - Check the box labeled “Activate Manual ECRS” to activate, - Enter the “Manual ECRS Desired MW”, - Select Enter, - Select Commit. - QSE’s have one minute to update ECRS schedule to free up the capacity, SCED will automatically run after one minute. - Manually release ONECRS or Hydro resources operating in Synchronous Condenser Fast Response Mode using the ERCOT Nodal Summary display on the EMS - Check the box labeled “Activate Manual ONECRS” to activate, - QSE’s have one minute to update ECRS schedule to free up the capacity, and release all available ECRS capacity within 10 minutes. - Manually release Generation Responsive Reserve (RRS-PFR) using the ERCOT Nodal Summary display on the EMS - Check the box labeled “Activate Manual Responsive Reserve” to activate, - Enter the “Desired RRS MW”, - Select Enter, - Select Commit. - QSE’s have one minute to update schedule to free up the capacity, SCED will automatically run after one minute. - Remember to remove the manual ECRS and RRS amount when frequency has recovered. - Notify the Shift Supervisor of the need to possibly RUC commit additional Resources. |
| Note | ERCOT may declare an EEA Level 2 when the clock-minute average system frequency falls below 59.91 Hz for 15 consecutive minutes. |
| Notify | If it is recognized that the Frequency is or expected to be outside +/- 0.1 Hz for a non-transient event and will not recover within 15 minutes, notify the Nuclear Power Plants QSEs. |
| 15 Minutes | IF: - 15 consecutive minutes of ACE less than BAALLow (59.91 Hz ); THEN: - Curtail appropriate amount of DC-Tie export (issue an Emergency), - Coordinate with the Resource Operator to manually deploy group(s) of Load Resources providing ECRS or RRS, - Coordinate with the ERCOT Resource Desk Operator to manually deploy RRS-FFR (NCLR), if available. - Call QSEs with Resources that have negative Base Point deviations and issue an Operating Instruction to bring their Base Point deviations to zero, - Verify SCEDs capacity to increase Base Points (HDL-GEN), - Re-adjust manual offset, - If room is available - Manually run SCED, - Log the event and notify Operations Support Engineer to send notification of the event to OperationsAnalysis@ercot.com. |
| 20 Minutes | IF: - 20 consecutive minutes of ACE less than BAALLow (59.91 Hz); THEN: - Implement EEA Level 2 - EEA2 PRC <1750 - Call QSEs with Resources that have negative Base Point deviations and issue an Operating Instruction to bring their Base Point deviations to zero, - Verify SCEDs capacity to increase Base Points (HDL-GEN), - If room is available, re-adjust manual offset, - Manually run SCED, - Monitor ECRS and RRS Load Resource deployments. - Consider manually releasing RRS-FFR, if available using the ERCOT Nodal Summary display on the EMS - Check the box labeled “Activate Manual FFR” to activate, - Enter the “Desired FFR MW”, - Select Commit. - Remember to remove the manual FFR amount when frequency has recovered. - Make Hotline call to QSE’s RRS-FFR released MW to QSE is allocated based on the RRS-FFR responsibility from both units and CLR’s. |
| ERS Resources | Q#7 - Typical Hotline Script for EEA2 deploying ERS-10 / ERS-30 / both ERS-10 and ERS 30 / ERS-30 including Weather Sensitive ERS / ERS-10 and ERS-30 including Weather Sensitive |
| Load Resources | Q#8 - Typical Hotline Script for EEA2 deploying Load Resources |
| 25 Minutes | IF: - 25 consecutive minutes of ACE less than BAALLow (59.91 Hz ); THEN: - Implement EEA Level 3 - EEA3 Unable to Maintain 59.91 Hz or PRC <1000 MW - Verify SCEDs capacity to increase Base Points, - Re-adjusted manual offset, - Do Not enter an offset > than (HDL-GEN) - Manually run SCED as needed, - Monitor ECRS and RRS Load Resource deployments, - Monitor DC-tie curtailments, - Coordinate with the Transmission and Security Operator to shed an appropriate amount of firm load. - Make Hotline call to QSE’s ## Q#11 EEA3 With Firm Load Shed: |
| Stable | IF: - Firm load was shed; THEN: - Coordinate with the Transmission and Security Operator to restore firm load. - Make Hotline call to QSE’s ## Q#13 Restoring Firm Load: IF: - SCED dispatchable ECRS was manually released; THEN: - Uncheck the Activate Manual ECRS, - Uncheck the Activate Manual ONECRS IF: - RRS-PFR or RRS-FFR was manually released; THEN: - Uncheck the Activate Manual Responsive Reserve, - Uncheck the Activate Manual FFR Responsive Reserve, - Notify the ERCOT Resource Desk Operator to recall FFR NCLR, if deployed. IF: - Load Resources providing ECRS or RRS were manually deployed; THEN: - Recall Load Resources providing ECRS or RRS starting with the highest group. IF: - A manual offset was used; THEN: - Ensure that it has been removed. |
| Log | Log all actions. |
| ### Monitor Frequency for the Loss of EMS or Site Failover |  |
|  | The ability to view an adequate Frequency source may be limited during a site-failover, database load, or if AGC is temporarily unavailable. To view the System Frequency during these conditions you may monitor the following sources. - ERCOT Control Room VORNE digital wall frequency displays - PI Process Book → ERCOT → TrueTime Frequency (Taylor) and/or - PI ProcessBook → ERCOT → TrueTime Frequency (Bastrop) It may be necessary to reload the PI ProcessBook “ERCOT Main Summary” display to show the historical data. |
| ### Actions When Frequency Telemetry is Incorrect |  |
|  | REVIEW REFERENCE DISPLAY: EMP Applications>Generation Control>Generation Area Status>Current Frequency Deviation from Nominal IF: - Frequency is believed to be incorrect; THEN: - Check the current Frequency and switch to a different source, - Select Skip on the incorrect Frequency device, - Contact the Help Desk. |

## 3.3	System Failures

Procedure Purpose:  To ensure frequency is maintained in the event of a SCED, RLC, or LFC failure.  Also, to ensure proper notification is made for these failures along with notification for ICCP, ERCOT Website and Outage Scheduler outages.

| Protocol Reference | 6.3.3 | 6.5.9.1(2) | 6.5.9.2 | 6.5.9.3.3 |
| --- | --- | --- | --- | --- |
| Guide Reference | 2.2.4.3 (1) |  |  |  |
| NERC Standard | BAL-005-1 R2, R5 | TOP-001-5 R9 |  |  |

| Version: 1 | Revision: 33 | Effective Date: June 30, 2023 |
| --- | --- | --- |

| Step |  | Action |  |
| --- | --- | --- | --- |
| ### SCED Failure |  |  |  |
| NOTE |  | When RLC sees that the SCED solution has not updated within the last 425 seconds, emergency base points (EBP) will automatically activate. Any time EBPs are activated, SCED solutions are being blocked from being communicated to MPs. The RLC Control Parameters (SCED Failure Threshold) should be set to 125 seconds. This is due to a code that adds 300 seconds to the 125 seconds from SCED Failure Threshold Parameter in the display, so total number of seconds RLC waits for SCED solution is 425 before enabling the emergency base points. |  |
| FREQUENCY GUIDELINES |  | During System Failures, Emergency Base Point (EBP) or instructing a QSE to go on Constant Frequency Control (CFC) - Frequency within +/- 0.03 Hz of schedule – Normal with available regulation - Frequency within +/- 0.05 Hz of schedule – When returning to Normal Operations with available regulation - Frequency maintained within +/- 0.09 Hz of schedule – Balancing Authority ACE Limit (BAAL) |  |
| NOTE |  | If for some reason a manual EBP is required for a Resource, communicate the Resource name, MW output requested, start time and duration of the dispatch instruction to the QSE representing the Resource. |  |
| 1 |  | IF: - Any module of the SCED Workflow Controller fails; THEN: - Manually run the SCED process. |  |
| 2 |  | IF: - SCED still fails after manually running, AND - EBPs have automatically activated; THEN: - Contact the Help Desk, - Initiate the Watch Hotline call to QSEs, - Notify Resource Operator to post a message on the ERCOT Website, - Notify Transmission Operator to make Hotline call to TOs. Q#27 - Typical Hotline Script for Watch for SCED Failure |  |
| 3 |  | EMP Applications>Generation Area Status>Related Displays>ERCOT Nodal Summary MONITOR: - Regulation Service (Up/Dn) margins to ensure frequency can be adequately maintained. IF: - It is determined that remaining Regulation Service (Up/Dn) is no longer sufficient to maintain system frequency; THEN: - Enter the EBP increment/decrement as needed to control frequency to recall deployed Regulation. - Once the MW amount has been entered and committed, the EBP amount will return to zero |  |
| 4 |  | WHEN: - SCED is solving with a valid solution; THEN: - Remove the Emergency Base Point flag, - Initiate Hotline call to cancel the Watch, - Notify Resource Operator to cancel the ERCOT Website posting, - Notify Transmission Operator to cancel the Watch with TOs. Q#28 - Typical Hotline Script for Cancel Watch for SCED is Solving |  |
| Log |  | Log all actions. |  |
| ### SCED Data Input Failure |  |  |  |
| 1 |  | IF: - SCED receives data input failures and gives erroneous results; THEN: - Manually activate EBP, - Contact the Help Desk, - Initiate the Watch Hotline call - Notify Resource Operator to post the message on the ERCOT Website, - Notify the Transmission Operator to make Hotline call to TOs. Q#29 - Typical Hotline Script for Watch for SCED Data Input Failure |  |
| 2 |  | WHEN: - SCED is solving with a valid solution; THEN: - Remove the Emergency Base Point flag, - Initiate Hotline call to cancel the Watch, - Notify Resource Operator to cancel the ERCOT Website posting, - Notify Transmission Operator to cancel the Watch with TOs. Q#28 - Typical Hotline Script for Cancel Watch for SCED is Solving |  |
| ### RLC Failure |  |  |  |
| 1 |  | The Resource Limit Calculator (RLC) can fail independently of AGC. If RLC fails, SCED will not function (invalid results), even though it shows available. A RLC failure will be displayed to the Operator in the upper right corner of the RLC display as follows: - Process Status: RLC Up (Normal Operation) - Process Status: RLC Down (will be displayed in RED when failed) - RLC (PI Alarm) will be flashing RED. |  |
| NOTE |  | Regulation is functioning, RRS is not. EBP will have to be manually checked. |  |
| 2 |  | IF: - RLC has failed; THEN: - Verify the status of AGC - IF AGC is also failed, proceed to the EMS (LFC and RLC) Failure procedure - Contact the Help Desk, - Initiate a Watch Hotline call to QSEs - Notify Resource Operator to post the message on the ERCOT Website - Notify Transmission Desk Operator to make Hotline call to TOs. Q#30 - Typical Hotline Script for Watch for RLC Failure |  |
| 3 |  | EMP Applications>Generation Area Status>Related Displays>ERCOT Nodal Summary MONITOR: - Regulation Service (Up/Dn) margins to ensure frequency can be adequately maintained. IF: - It is determined that remaining Regulation Service (Up/Dn) is no longer sufficient to maintain system frequency; THEN: - Enter the EBP increment/decrement as needed to control frequency to recall deployed Regulation. - Once the MW amount has been entered and committed, the EBP amount will return to zero |  |
| 4 |  | WHEN: - RLC is restored; THEN: - Remove the Emergency Base Point flag, - Initiate Hotline call to cancel the Watch, - Notify Resource Operator to cancel the ERCOT Website posting, - Notify Transmission Operator to cancel the Watch with TOs. Q#31 - Typical Hotline Script to Cancel Watch for RLC is Restored |  |
| Log |  | Log all actions. |  |
| ### LFC (AGC) Failure |  |  |  |
| NOTE |  | AGC will suspend when frequency falls to 59.5 Hz or below. AGC will require a manual reset from the operator and will not reset automatically once frequency recovers above 59.5. Reference: Desktop Guide Real Time Desk 2.12 |  |
| NOTE |  | When LFC (AGC) is paused or suspended and RLC and SCED are functioning, UDBP are not going out to resources and Regulation, ECRS, RRS and EBP are not functioning. |  |
| 1 |  | IF: - LFC is not functioning as indicated by: - AGC is SUSPENDED or PAUSED OR - “Last AGC Cycle” time on Generation Area Status display is not updating; THEN: - Verify the status of RLC - If RLC is also failed, proceed to the next procedure “EMMS Failure” - If RLC is still functioning properly, - Contact Help Desk, - Continue with this procedure REFERENCE Displays: EMP Applications>Generation Area Status>Ancillary Service Monitoring Summary>Capacity Reserve QSE Detail>QSE CFC tab DETERMINE: - Which QSE has ample GEN-LASL from the QSE CFC tab when load is expected to be decreasing, to place on constant frequency control, - Which QSE has ample Spinning Reserve Capacity from the QSE CFC tab when load is expected to be increasing to place on constant frequency control. - Ample Available Ramp Rate (Up/Dn) from the QSE CFC tab THEN: - Issue an Operating Instruction to selected QSE to go on constant frequency, - Check box “On CFC” of selected QSE from QSE CFC tab. This action will toggle ERCOT AGC to “Monitor” mode. - As time permits, issue electronic Dispatch Instruction confirmation, - Choose “OPERATE AT CONSTANT FREQUENCY” as the Instruction Type from QSE Level When issuing a VDI or the confirmation, ensure the use of three-part communication: - Issue the Operating Instruction - Receive a correct repeat back - Give an acknowledgement Q#112 - Typical Script to Instruct a QSE on Constant Frequency for LFC Failure: All Operating Instructions shall be in a clear, concise, and definitive manner. Ensure the recipient of the Operating Instruction repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |  |
| 2 |  | THEN: - Initiate the Emergency Notice Hotline call to QSEs - Notify Resource Operator to post the message on the ERCOT Website, - Notify Transmission Operator to make Hotline call to TOs. Q#32 - Typical Hotline Script for Emergency Notice a QSE is on Constant Frequency for LFC/EMS Failure |  |
| 3 |  | MONITOR: - Frequency, HASL-GEN, GEN-LASL and Available Ramp Rate (Up/Dn) availability for QSE on constant frequency, AND/OR - The QSE on constant frequency notifies ERCOT of capacity issue; THEN: - Determine which QSE has the most available Capacity, - Issue a Verbal Dispatch Instruction (VDI) to QSE to assist the QSE on Constant Frequency, - Choose “Other For Resource” as the Instruction Type |  |
| 4 |  | IF: - There is no longer any available HASL-GEN, GEN-LASL and Available Ramp Rate (Up/Dn) to issue unit specific instructions; THEN: - Request RUC Operator to RUC commit/decommit a Resource |  |
| 5 |  | WHEN: - ERCOT AGC Control is functioning properly; THEN: - Issue an Operating Instruction to QSE to come off Constant Frequency, - Uncheck box “On CFC” of selected QSE from QSE CFC tab. This action will toggle ERCOT AGC to “ON” mode. , - Cancel VDI(s) for additional generation, if issued, - Initiate Hotline to cancel the Emergency Notice to QSEs, - Notify Resource Operator to cancel the ERCOT Website posting, - Notify Transmission Operator to cancel the Emergency Notice with TOs. Q#113 - Typical Script to Instruct QSE to End Constant Frequency for LFC Functioning: Q#33 - Typical Hotline Script to Cancel Emergency Notice for QSE on Constant Frequency for LFC/EMS Functioning: |  |
| Log |  | Log all actions. |  |
| ### EMMS (LFC and RLC/SCED) Failure |  |  |  |
| NOTE |  | AGC will suspend when frequency falls to 59.5 Hz or below. AGC will require a manual reset from the operator and will not reset automatically once frequency recovers above 59.5. Reference: Desktop Guide Real Time Desk 2.12 |  |
| NOTE |  | Regulation, RRS, UDBP, BP, EBP, and manual offset not functioning. |  |
| 1 |  | LFC (AGC): - AGC is SUSPENDED or PAUSED, - “Last ACE crossing zero” time on the Generation Area Status page is not updating, - AGC operation adversely impacts the reliability of the Interconnection, - SCED and EMS are not functioning, - Problem cannot be resolved quickly RLC: - Process Status: RLC Down will be displayed in RED in the upper right-hand corner of the RLC display - RLC (PI Alarm) will be flashing RED. REFERENCE Display: EMP Applications>Generation Area Status>Ancillary Service Monitoring Summary>Capacity Reserve QSE Detail>QSE CFC tab DETERMINE: - Which QSE has ample GEN-LASL from the QSE CFC tab when load is expected to be decreasing to place on constant frequency Control; - Which QSE has ample Spinning Reserve Capacity from the QSE CFC tab when load is expected to be increasing. - Ample Available Ramp Rate (Up/Dn) from the QSE CFC tab THEN: - Issue an Operating Instruction to selected QSE to go on constant frequency - Check box “On CFC” of selected QSE from QSE CFC tab. This action will toggle ERCOT AGC to “Monitor” mode. - As time permits, issue an electronic Dispatch confirmation - Choose “OPERATE AT CONSTANT FREQUENCY” as the Instruction Type from QSE Level When issuing a VDI or the confirmation, ensure the use of three-part communication: - Issue the Operating Instruction - Receive a correct repeat back - Give an acknowledgement Q#114 - Typical Script to Instruct a QSE on Constant Frequency for LFC/SCED Failure: All Operating Instructions shall be in a clear, concise, and definitive manner. Ensure the recipient of the Operating Instruction repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |  |
| 2 |  | THEN: - Initiate the Emergency Notice Hotline call to QSEs, - Notify Resource Operator to post the message on the ERCOT Website, - Notify Transmission Operator to make Hotline call to TOs Q#34 - Typical Hotline Script for Emergency Notice a QSE is on Constant Frequency for LFC/EMS and SCED failure: |  |
| 3 |  | MONITOR: - Frequency, HASL-GEN, GEN-LASL, Available Ramp Rate (Up/Dn) availability, and Spinning Reserve Capacity for QSE on constant frequency, AND/OR - The QSE on Constant Frequency notifies ERCOT that they are having control issues; THEN: - Determine which QSE has the most available Capacity, - Issue a Verbal Dispatch Instruction (VDI) to QSE to assist the QSE on Constant Frequency, - Choose “Other For Resource” as the Instruction Type |  |
| 4 |  | IF: - There is no longer any available HASL-GEN, GEN-LASL and Available Ramp Rate (Up/Dn) to issue unit specific instructions; THEN: - Request RUC Operator to RUC commit/decommit a Resource |  |
| 5 |  | WHEN: - AGC and RLC is restored; THEN: - Instruct QSE to come off constant frequency by ending VDI, - Uncheck box “On CFC” of selected QSE from QSE CFC tab. This action will toggle ERCOT AGC to “ON” mode., - Cancel VDI(s) for additional generation, if issued, - Initiate Hotline to cancel Emergency Notice to QSEs, - Notify Resource Operator to cancel the ERCOT Website posting, - Notify Transmission Operator to cancel Emergency Notice with TOs. Q#115 - Typical Script to Instruct a QSE to end Constant Frequency for LFC/SCED Functioning, : Q#35 - Typical Hotline Script to Cancel Emergency Notice with LFC/EMS Functioning, SCED valid: |  |
| Log |  | Log all actions. |  |
| ## ICCP, ERCOT Website, and Outage Scheduler Outages |  |  |  |
| 1 |  | For any planned or unplanned outage of ERCOT’s ICCP, ERCOT Website (affecting COP submissions) or the Outage Scheduler lasting longer than 30 minutes, notifications to QSEs are required. IF: - ERCOT’s ICCP, ERCOT Website (affecting COP submissions) or the Outage Scheduler has a planned or unplanned outage that is expected to last 30 minutes or more; THEN: - Make a Hotline call to the QSEs: Q#108 - Typical Hotline Script for ERCOT’s ICCP, ERCOT Website, or the Outage Scheduler Planned or Unplanned Outage |  |
| 2 |  | Once operational: Make a Hotline call to notify QSEs: Q#109 - Typical Hotline Script for ERCOT’s ICCP, ERCOT Website or Outage Scheduler back to Normal |  |
| LOG |  | Log all actions |  |
| ## STATE ESTIMATOR (SE)/Real-Time Contingency Analysis (RTCA) |  |  |  |
| 1 | IF: - Notified that the SE/RTCA has not solved; THEN: - Coordinate with the Transmission Desk Operator and the Operations Support Engineer for up to 15 minutes from last successful solution; IF: - The SE/RTCA remains unsolved; THEN: - Make notifications, - Continue to monitor the system as possible, - Coordinate with the Operations Support Engineer to ensure a Real-time Assessment (RTA) is performed within 30 minutes of the last SE/RTCA solution and within 30 minutes of each RTA conducted thereafter. |  |  |
| 2 | Within 30 minutes of the SE/RTCA tool outage: Confirm notification was completed by the Transmission Desk Operator to the two master QSEs that represent the Nuclear Plants that ERCOTs [State Estimator/RTCA] is not functioning and is expected to be functional within approximately [# minutes]. |  |  |
| 3 | If the State Estimator/RTCA has NOT solved within the last 30 minutes: Make a Hotline call to issue an Advisory to the QSEs: Q#48 - Typical Hotline Script for Advisory for State Estimator/RTCA Not Solved |  |  |
| 4 | Once the State Estimator/RTCA is operational: Make a Hotline call to cancel the Advisory to the TOs: Q#49 - Typical Hotline Script to Cancel Advisory for State Estimator/RTCA: |  |  |
| 5 | Confirm notification was completed by the Transmission Desk Operator to the two master QSEs that represent the Nuclear Plants that the [State Estimator/RTCA] is now functional. |  |  |
| LOG | Log all actions |  |  |

## 3.5	Monitor Capacity and Reserves and Respond to Shortages or Surplus

Procedure Purpose:  Monitoring sufficient operating reserves and capacity surplus.  Deploying/Recalling Non-Spin, manually Releasing/Recalling ECRS, and manually Releasing/Recalling RRS.

| Protocol Reference | 6.5.7.6.2.2 | 6.5.7.6.2.3 |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.8 |  |  |  |
| NERC Standard | IRO-001-4 R1 | TOP-001-5 R2 |  |  |

| Version: 1 | Revision: 25 | Effective Date: June 30, 2023 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | The Day-Ahead process, the Adjustment Period process, and the Real-Time process must be utilized before ordering Resources to specific output levels with Emergency Base Point instructions. |
| ## Insufficient Generation |  |
| RMR | Prior to declaring EEA, start RMR Units available in the time frame of the emergency. RMR Units should be loaded to full capability. |
| NOTE | The Projected Ramp Available in 30min represents the calculation HASL – (GTBD + GTBD offset) – (IRR Curtailment) – (30-minute Net Load Ramp) |
| Deploying Non-Spin | Triggers to deploy Non-Spin WHEN: - PRC < 3200 MW and not expected to recover within 30 minutes without deploying reserves, THEN: - Coordinate with the Resource Operator to deploy a group(s) or all available Non-Spin capacity. MONITOR: - The Non-Spin Deployment Trigger Display - Projected Ramp Available in 30min WHEN: - Projected Ramp Available in 30min < -300 THEN: - Coordinate with the Resource Operator to deploy a group(s) of available Non-Spin. When: - Projected Ramp Available in 30min < -600, OR - PRC is < 3200 MW; THEN: - Coordinate with the Resource Operator to deploy available groups of Non-Spin, as needed, if not already deployed. |
| NOTE | If a condition indicates that additional capacity may need to be brought On-Line to manage reliability, operators will evaluate the system condition and deploy Non-Spin groups as needed if no other better options are available to resolve the system condition. Under emergency, the emergency process will govern the deployment of Non-Spin. |
| Recalling Non-Spin | WHEN: - Projected Ramp Available in 30min > 1000, AND - PRC is > 3200 MW; THEN: - Coordinate with the Resource Operator to recall half of the groups of deployed Non-Spin. WHEN: - Projected Ramp Available in 30min > 1000, AND - PRC is > 3400 MW; THEN: - Coordinate with the Resource Operator to recall all deployed groups of Non-Spin. |
| NOTE | Trigger 1 : (Current PRC – 3200 MW) + Remaining QSGR capacity - (projected 10min Net Load ramp) < 300 MW Trigger 2: (10min ramp capacity) – (projected 10min Net Load ramp) < 0 MW |
| Releasing SCED Dispatchable ECRS | Triggers to release ECRS MONITOR: - The ECRS Deployment Trigger Display WHEN: - Current PRC - 3200 MW plus Remaining QSGR Capacity minus Projected Net Load Ramp < 300 MW, THEN: - Manually release SCED dispatchable ERCOT Contingency Reserve Service using the ERCOT Nodal Summary display on the EMS - Check the box labeled “Activate Manual ECRS” to activate, - Enter the “Manual ECRS Desired MW”, - Select Enter, - Select Commit. - QSE’s have one minute to update ECRS schedule to free up the capacity, SCED will automatically run after one minute. To release additional ECRS, SCED will need to be manually run one minute after the commitment. WHEN: - ECRS is manually released and not expected to be recalled within 30 minutes. THEN: - Coordinate with the Resource desk operator to deploy the desired Group(s) or all the available Non-Spin capacity, if not already deployed. - Recall manually released dispatchable ECRS as soon as conditions allow to restore reserves WHEN: - 10min Generation Ramp Capacity minus Projected Ramp in 10min < 0 THEN: - Manually release SCED dispatchable ECRS using the ERCOT Nodal Summary display on the EMS - Check the box labeled “Activate Manual ECRS” to activate, - Enter the “Manual ECRS Desired MW”, - Select Enter, - Select Commit. - QSE’s have one minute to update ECRS schedule to free up the capacity, SCED will automatically run after one minute. To release additional ECRS, SCED will need to be manually run one minute after the commitment. WHEN: - ECRS is manually released and not expected to be recalled within 30 minutes. THEN: - Coordinate with the Resource desk operator to deploy the desired Group(s) or all the available Non-Spin capacity, if not already deployed. - Recall manually released dispatchable ECRS as soon as conditions allow to restore reserves. |
| NOTE | If a condition indicates that additional capacity may need to be brought On-Line to manage reliability, operators will evaluate the system condition and release SCED dispatchable ECRS as needed if no other better options are available to resolve the system condition. Under emergency, the emergency process will govern the release of ECRS. |
| Recalling ECRS | WHEN: - Current PRC - 3200 MW plus Remaining QSGR Capacity minus Projected Net Load Ramp > 500 MW; and - In stable operation condition and expected to trend in that direction THEN: - Recall manually released ECRS WHEN: - 10min Generation Ramp Capacity minus Projected Ramp in 10min > 0 - In stable operation condition and we don’t expect an increase in the Net Load Ramp THEN: - Recall manually released ECRS |
| NOTE | RRS for capacity may be manually released (HASL released) when the system approaches scarcity conditions so that the capacity reserved behind HASL will be released to Security-Constrained Economic Dispatch (SCED). The existing measure of scarcity is Physical Responsive Capability (PRC) and spinning reserves. If PRC and spinning reserves drop below 3,000 MW, this process may be used. Scarcity conditions may occur during the Peak Load Season when ERCOT System Load is above 60,000 MW. For all other months, they could occur when ERCOT System Load is above 50,000 MW. |
| NOTE | Manually release Load Resources other than Controllable Load Resources providing ECRS and RRS before entering an Energy Emergency Alert (EEA), to maintain a minimum 500 MWs of Physical Responsive Capability (PRC) reserves on Generation Resources. |
| HASL Release – Manually Release RRS | Triggers to manually release RRS MONITOR: - “HASL – Load Ramp” value on the Generation Area Status display, this is HASL – (Gen + 5-minute load ramp) IF: - HASL – Load Ramp < = 200 MW; THEN: - Ensure all Non-Spin has been deployed first then ensure all SCED dispatchable ECRS has been released before manually releasing RRS. - Manually release up to 500 MW of RRS. IF: - After Resources have responded to the previous release, AND - HASL – Load Ramp < = 200 MW; THEN: - Manually release up to the available remaining RRS, AND - Maintain a minimum 500 MWs of Physical Responsive Capability (PRC) reserves on Generation Resources. (it is incremental). IF: - PRC < = 2000 MW, OR; - All available RRS has been released, AND - Maintain a minimum 500 MWs of Physical Responsive Capability (PRC) reserves on Generation Resources. THEN: - Notify Shift Supervisor and Resource operator to manually deploy group(s) of Load Resources other than Controllable Load Resources providing RRS as needed. WHEN: - Notified by the Resource desk operator that group(s) of Load Resources have been deployed by XML, THEN: - Notify QSEs via a Hotline call of the deployment of Load Resources. - Deploying Load Resources, the Resource Operator must complete the XML deployment of the Load Resources before the Hotline call is made. Q#131 - Typical Hotline Script for Deployment of Load Resources to Maintain a Minimum 500 MW of Generation RRS |
| HASL - RRS Recall | WHEN: - HASL – (Gen + 5-minute load ramp) > 1600 MW AND/OR - PRC > = 3300 MW, AND - Frequency is 59.970 HZ or above; THEN: - Manually recall group(s) of Load Resources - Manually recall the RRS, which can be done in up to 500 MW steps. |
| ## Surplus Generation |  |
| SCED Surplus | MONITOR: - The Generation Area Status Page IF: - (GEN-LDL) < 200 MW; THEN: - Consult with RUC Operator to ensure HRUC is seeing the situation and is decommitting Resources, - If needed, request the RUC Operator to issue VDI to RUC decommit a Resource to help alleviate the surplus |
| Log | Log all actions. |
| ## Valley Generation |  |
| Monitor | Market Operations>Reliability Unit Commitment>HRUC Displays>UC Displays>Output Display Menu>Generator Outputs>Generation Schedule OR Market Operations>Reliability Unit Commitment>HRUC Displays>UC Displays>Input Display Menu>Generation Self-Commitment Status |
| 1 | WHEN: - Two or more Generation plants (DUKE, NEDIN and/or SILASRAY) are scheduled to go Off-Line at the same time; THEN: - Discuss with Transmission and Security Operator AND Shift Supervisor - Ensure AEP TO is notified with the shut down time and with at least an hours’ notice, they need to pre-posture reactive devices. |
| Log | Log all actions. |

## 3.7	Responding to North to Houston Interface Issues

Procedure Purpose:  Deployment/Termination of ECRS and Non-Spin Reserve Service for Congestion Management as requested by the Transmission Operator.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.2.4(1) | 4.5.2(2)(b) |  |  |
| NERC Standard | EOP-011-2 R1, R1.1, R1.2, R1.2.4 | IRO-001-4 R1 | TOP-001-5 R1 |  |

| Version: 1 | Revision: 9 | Effective Date: June 30, 2023 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Issue Watch & Deploy ECRS and Non-Spin | WHEN: - Notified by the Transmission Operator that ECRS and Non-Spin needs to be deployed in the Houston area for the North-Houston Interface; THEN: - Using the Hotline, issue a Watch, - Resource Operator will deploy ECRS and Non-Spin Q#39 - Typical Hotline Script for Watch/Deploy ECRS and Non-Spin for N-H Interface |
| NOTE | To the extent that ERCOT deploys a Load Resource that has chosen a group deployment option, ERCOT shall either deploy the entire offer or, if only partial deployment is possible, skip the offer by the Load Resource with the group deployment option and proceed to deploy the next available Resource. To the extent possible start by deploying group 0 Load Resources i.e. that are not carrying RRSUFR and don’t have a relay armed; then deploy group 1a which is Load Resources that is only carrying ECRS and have a relay armed; then 1b, 1c, group 2, group 3 |
| Issue Emergency Notice & Deploy Load Resources | WHEN: - Notified by the Transmission Operator to deploy Load Resources in the Houston area for the North-Houston Interface; THEN: - Using the Hotline, issue the Emergency Notice Q#40 - Typical Hotline Script for Emergency/ Deploy Load Resources for N-H Interface |
| Recall Load Resources | WHEN: - Notified by the Transmission Operator to recall Load Resources in the Houston area for the North-Houston Interface; THEN: - Using the Hotline, cancel the Emergency Notice, Q#41 - Typical Hotline Script to Cancel Emergency Notice for N-H Interface / Recall Load Resources: |
| Recall ECRS and Non-Spin | WHEN: - Notified by the Transmission Operator to recall ECRS and Non-Spin in the Houston area for the North-Houston Interface; THEN: - Using the Hotline, cancel the Watch, Q#42 - Typical Hotline Script to Cancel Watch for N-H Interface / Recall ECRS and Non-Spin |
| Log | Log all actions. |

## 4.1	Managing SCED

Procedure Purpose: To ensure that a SCED solution has solved, and that the solution is reasonable.

| Protocol Reference | 3.8.3 | 3.9.1(10) | 3.10.7.5.1(5) | 8.1.1.2(16) |
| --- | --- | --- | --- | --- |
| Guide Reference | 7.3.3 |  |  |  |
| NERC Standard | TOP-003-5 R5, R5.2 | TOP-010-1(i) R1, R1.3, R2, R2.3 |  |  |

| Version: 1 | Revision: 23 | Effective Date: June 30, 2023 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Workflow Controller Messages |  |
| NOTE | The SCED Workflow Controller provides three color coded messages as indicated in the following: - GREEN – Informational (i) and Success (s) - BLUE – Warning (w) - RED – Error (e) and Fatal Error (f) |
| 1 | REVIEW REFERENCE DISPLAY: Market Operation>Real-Time Market>SCED Displays>Workflow>SCED Workflow Messages Monitor SCED Workflow Controller logs for “Warning” and “Error” messages. |
| 2 | IF: - The log indicates an “Error” or “Fatal Error”; THEN: - Contact the Help Desk and notify the Control Room staff, - Attempt to resolve the issue, refer to Desktop Guide Real Time Desk Section 2.5, - Refer to Section 3.3 “Managing SCED Failures” in this procedure. |
| ### SCED Solution Time Parameter |  |
| NOTE | Typically, SCED should produce a solution within 20 seconds. It is highly desirable to have at least 3 executions of SCED in any 15-minute period. |
| Automatic Trigger | Verify that SCED is automatically triggered: - Periodically every 5 minutes - About 60 seconds after ECRS is automatically released by LFC - Frequency is < 59.95 Hz for > two consecutive minutes IF: - SCED is not automatically executed (but has not failed); THEN: - Manually execute SCED, - Immediately notify the Shift Supervisor and Operations Support Engineer, - Continue to manually execute SCED approximately every 5 minutes until the condition is corrected. |
| Manual Trigger | SCED may be manually triggered when the following is identified: - Frequency deviates +/-0.05 Hz for more than 5 minutes - Generation Resource trips and Frequency is > 59.91 Hz - When approximately 50% of Regulation has been deployed - Approximately 60 seconds after Generation Resources providing ECRS or RRS have been released. - As frequently as needed after Load Resources providing ECRS or RRS have been deployed. |
| LOG | Log all actions. |
| ### Quick Start Generation Resource |  |
| QSGR | A Generation Resource that in its cold-temperature state can come On-Line within ten minutes of receiving ERCOT notice and has passed an ERCOT Quick Start Generation Resource test that establishes an amount of capacity that can be deployed within a ten-minute period. - These Resources can be viewed at ERCOT SharePoint > System Operations – Control Center > Quick Links > Approved Quick Start (QSGR) Resources |
| COP | The QSE for a QSGR that is available for deployment by SCED shall set the COP Resource Status ON, the COP LSL and HSL values to the expected sustainable LSL and HSL for the QSGR for the hour. If the QSGR is providing Non-Spin, then the A/S Resource Responsibility for Non-Spin shall be set to the Resource’s Non-Spin responsibility in the COP. If the Resource’s Non-Spin responsibility is greater than the difference between HSL and LSL, then the QSGR that is available for deployment by SCED shall set the COP LSL to zero. If the QSGR is providing ECRS, then the A/S Resource Responsibility for ECRS shall be set to the Resource’s ECRS responsibility in the COP. If the Resource’s ECRS responsibility is greater than the difference between HSL and LSL, then the QSGR that is available to be released by SCED shall set the COP LSL to zero. |
| Telemeter | The QSGR that is available to be released by SCED and awarded ECRS and Non-Spin shall telemeter a Resource Status of OFFQS and an LSL of zero prior to receiving a release instruction from SCED. This status is necessary for SCED to recognize that the Resource can be Dispatched. The status of the breaker shall be open, and the output of the Resource shall be zero in order for the State Estimator to correctly assess the state of the system. After being released for energy by SCED, the Resource shall telemeter an LSL equal to or less than the Resource’s actual output until the Resource has ramped to its physical LSL. After reaching its physical LSL, the QSGR shall telemeter an LSL that reflects its physical LSL. The QSGR that is providing ECRS shall telemeter Ancillary Service Resource Responsibility and Ancillary Service Schedule to reflect the Resource’s ECRS obligation. For the QSGR providing (online) Non-Spin shall telemeter Ancillary Service Resource Responsibility to reflect the Resource’s Non-Spin obligation and telemeter Ancillary Service Schedule of zero to make the capacity available for SCED. The QSGR that is providing Off-Line Non-Spin shall always telemeter OFFNS Resource Status and telemeter an Ancillary Service Resource Responsibility and Ancillary Service Schedule for Non-Spin to reflect the Resource’s Non-Spin obligation A QSGR with a telemeter breaker status of open and a telemeter Resource Status of OFFQS shall not provide Regulation or Responsive Reserve Service. |
| QSGR Decommitment | Please refer to Desktop Guide Common to Multiple Desks for the QSGR decommitment process. |
| QSGR Qualification Test | WHEN: - Conducting a QSGR qualification test for Operations Analysis; THEN: - Issue a VDI confirmation - Choose “OTHER_RES” as the Instruction Type from Resource level - Enter MW amount that the QSE is requesting to qualify its QSGR to provide. - Enter “QSGR Qualification Test” in “Other Information” - . When issuing a VDI or the confirmation ensure the use of three-part communication: - Issue the Operating Instruction - Receive a correct repeat back - Give an acknowledgement |
| ### Generation Resource Shut-down/Start-up Process |  |
| Shutdown/ Startup | Shut-down: - A QSE representing a Generation Resource that is not actively providing A/S (except for Off-line Non-Spin) may only use a Resource Status of SHUTDOWN through telemetry that the Resource is operating in a shutdown sequence requiring manual control and is not available for Dispatch. Start-up: - A QSE representing a Generation Resource that is not actively providing A/S may only use a Resource Status of STARTUP through telemetry that the Resource is operating in a start-up sequence requiring manual control and is not available for Dispatch. |
| NOTE | QSEs can manage basepoint deviations by adjusting their telemetered ramp rate. |
| NOTE | When a Resource is carrying “Off-Line” Non-spin and that Non-Spin is being recalled, the QSE would continue to show the Non-Spin responsibility on the Resource that is shutting down. |
| ### Combine Cycle Generation Resources |  |
| NOTE | WHEN: - Combine Cycle Generation Resources are changing configuration creating basepoint deviations THEN: - QSEs will need to manage their telemetered HSL for proper basepoints. |
| ### Telemetry Issues that could affect SCED and/or LMPs |  |
| Not Dispatchable to SCED | REVIEW REFERENCE DISPLAY: EMS Applications>Generation Control>Resource Limit Calculation>RLC Unit Input Data and RLC Unit Output Data WHEN: - A QSE has telemetered more A/S on a specific Resource that is greater than their HSL, OR - A Resource is generating more than their telemetered HSL; THEN: - SCED will set the HDL=LDL=MW making the Resource undispatchable, - Request the QSE to make corrections to their telemetry (Resource status, Resource limits, A/S responsibilities, etc.) |
| ### Real-Time Data Issues known by the QSE |  |
| NOTE | Manually replaced telemetry data is data entered by a QSE on their systems that is transmitted to ERCOT via ICCP in place of the normal points experiencing an issue. If Reliability issues can’t be resolved in a timely manner, ERCOT reserves the right to order the Resource off-line until the problem is resolved. |
| Notification of Telemetry Data Issue | IF: - Notified of a telemetry data issue (telemetry data will not be available or is unreliable for operational purposes; THEN: - The QSE should correct of the telemetry data as soon as practicable, or, - Manually replace the data, if available. |
| Cannot Resolve | IF: - The QSE cannot resolve the telemetry data issue within two Business Day, fix the issue in a timely manner; THEN: - The QSE shall provide an estimated time of resolution. |

## 5.3	Implement EEA Levels

Procedure Purpose:  To provide for maximum possible continuity of service while maintaining the integrity of the ERCOT System to reduce the chance of Cascading Outages.

| Protocol Reference | 6.5.7.6.2.2(16) | 6.5.9.3.4(6) | 6.5.9.4 | 6.5.9.4.2 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.4.3 |  |  |  |
| Guide Reference | 4.5.3 | 4.5.3.1 | 4.5.3.2 | 4.5.3.3 |
|  | 4.5.3.4 |  |  |  |
| NERC Standard | EOP-011-2 R2, R2.1, R2.2, R2.2.2, R2.2.3, R2.2.3.1, R2.2.3.4, R2.2.4, R2.2.7 | IRO-001-4 R1 | TOP-001-5 R2 |  |

| ### Version: 1 | Revision: 38 | Effective Date: June 30, 2023 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - Any time the clock-minute average system frequency falls < 59.91 Hz for 20 consecutive minutes, ERCOT CAN immediately implement EEA 3. - IF steady state system frequency falls < 59.5 Hz, ERCOT SHALL immediately implement EEA 3 for any duration. |
| NOTE | Confidentiality requirements regarding Transmission Operations and System Capacity information will be lifted, as needed to restore reliability. |
| NOTE | The minimum capacity required from Gen Resources providing RRS using Primary Frequency Response shall not be less than 1,150 MW. |
| NOTE | Manually deploy Load Resources other than Controllable Load Resources providing ECRS and RRS before entering an Energy Emergency Alert (EEA), to maintain a minimum 500 MWs of Physical Responsive Capability (PRC) reserves on Generation Resources. |
| NOTE | XML messages and Hotline calls are required for all deployments of Load Resources and ERS Resources |
| ERS-30 | ERS with a thirty-minute ramp period. |
| ERS-10 | ERS with a ten-minute ramp period. |
| TCEQ | The Texas Commission on Environmental Quality (TCEQ) will exercise enforcement discretion for exceedances of emission limits and operational limits for Resources that exceed air permit limits in order to maximize generation for the duration of the EEA event. A Market Notice will be sent to Market Participants. Make Hotline call. Q#5 Typical Hotline Script for TCEQ Notice of Enforcement Discretion |
| Media Appeal | When an ERCOT-wide appeal through the public news media for voluntary energy conservation is made. Make Hotline call and coordinate with Resource operator for posting message. Q#10 Typical Hotline Script for Media Appeal |
| ESR | Energy Storage Resources (ESR) will be required to suspend charging during an Energy Emergency Alert (EEA) except in limited circumstances, including Security-Constrained Economic Dispatch (SCED), Load Frequency Control (LFC) Dispatch, or a manual instruction. An exception to this provision is if an ESR is co-located with onsite generation that would be incapable of exporting additional power to the ERCOT System. |
| ### Implement EEA Level 1 |  |
| EEA 1 PRC<2300 | IF: - PRC < 2300 MW and is not projected to be recovered above 2300 MW within 30 minutes without the use of EEA Level 1; THEN: - Select the activate EEA flag in EMS, - Maintain steady state system frequency near 60 Hz and maintain PRC above 1750 MW, - Determine whether system conditions warrant the deployment of ERS if not already deployed. Refer to the ERS tab on the Real-Time Values Spreadsheet for amounts in each time period and number of times deployed: - Consider the peak hour, deploy all ERS if needed and available to prevent PRC from falling < 1750 MW, - When deploying the ERS, also deploy the weather-sensitive ERS if available for the current time period. - Using the Hotline, notify the QSEs to implement EEA 1. Q#6 - Typical Hotline Script for EEA1 |
| When ERS Time Periods Change | IF: - ERS Resources are deployed, and the Time Period is changing - If it is June – September and during time period TP3 or TP4 on a business day; THEN: - After Resource Operator has completed the XML deployment, make the QSE Hotline call Q#26 - Typical Hotline Script for EEA1 deploying ERS for New Time Period |
| RRS Release to HASL | REVIEW REFERENCE DISPLAYS: EMP Applications>Generation Area Status>Nodal Operations Status>Responsive Reserve Service Summary Data EMP Applications>Generation Area Status>Nodal Operations Status>ONECRS Display IF: - PRC < 2000 MW; THEN: - Activate Manual Responsive Reserve - Manually release any remaining RRS (maintain a minimum 500 MW RRS Generation) - Manually release any remaining SCED dispatchable ECRS - If necessary and available, release the Resources providing ECRS using ONECRS Resource Status |
| Log | Log all actions. |
| ### Implement EEA Level 2 |  |
| Note | ERCOT may declare an EEA Level 2 when the clock-minute average system frequency falls below 59.91 Hz for 15 consecutive minutes. |
| EEA 2 PRC<1750 | IF: - PRC < 1750 MW or unable to maintain system frequency at a minimum of 59.91 Hz and is not projected to be recovered above 1750 MW within 30 minutes without the use of EEA Level 2; THEN: - Verify with Shift Supervisor a public appeal has been issued - Maintain steady state system frequency at a minimum of 59.91 Hz and maintain PRC above 1,430 MW, - Determine when system conditions require the deployment of undeployed ERS, and/or deploy ECRS or RRS supplied from Load Resources that are not controllable (Do Not forget the WS ERS if available): - Deploy ERS if not already deployed - Deploy Load Resources Group 0/Group 0+1a+1b+1c/Group 0+1a+1b+1c+2/ Group 0+1a+1b+1c+2+3/All. - Using the Hotline, notify the QSEs to implement EEA 2 and any measures associated with EEA 1, if not already implemented. |
| ERS Resources | IF: - Deploying ERS, the Resource Operator must complete the XML deployment of the ERS before the Hotline call is made. - Deploy all ERS Resources as a single group. - If it is June – September and during time period TP3 or TP4 on a business day Q#7 - Typical Hotline Script for EEA2 |
| Load Resources | IF: - Deploying Load Resources, the Resource Operator must complete the XML deployment of the Load Resources before the Hotline call is made. - PRC < 1750 MW, deploy Group 0/Group 0+1a+1b+1c/Group 0+1a+1b+1c+2/Group 0+1a+1b+1c+2+3/All - PRC < 1430 MW, deploy all Groups simultaneously Q#8 - Typical Hotline Script for EEA2 deploying Load Resources |
| When ERS Time Periods Change | IF: - ERS Resources are deployed, and the Time Period is changing - If it is June – September and during time period TP3 or TP4 on a business day; THEN: - After Resource Operator has completed the XML deployment, make the QSE Hotline call Q#9 - Typical Hotline Script for EEA2 deploying ERS-10 / ERS-30 / both ERS-10 and ERS-30 / ERS-10, ERS-30 including Weather Sensitive Script |
| NOTE | - All Load Resources, 10 MIN ERS, and 30 MIN ERS must be deployed before firm load |
| Media Appeal | - Unless already in effect, verify with the Shift Supervisor that the communications group has issued an appeal through the public news media for voluntary energy conservation, - Notify QSEs, via Hotline, that a media appeal for conservation is in effect. Q#10 - Typical Hotline Script for Media Appeal |
| Log | Log all actions. |
| ### Implement EEA Level 3 |  |
| Note | ERCOT may declare an EEA Level 3 when the clock-minute average system frequency falls below 59.91 Hz for 20 consecutive minutes. |
| EEA3 PRC <1430 MW | ERCOT will declare an EEA Level 3 when PRC cannot be maintained above 1,430 MW. Using the Hotline, notify the QSEs to implement EEA 3 Without Firm Load Shed and any measures associated with EEA 1 and 2, if not already implemented. Q#103 - Typical Hotline Script for EEA3 PRC <1430 Without Firm Load Shed |
| EEA3 Unable to Maintain 59.91 Hz or PRC <1000 MW | IF: - PRC < 1000 MW and is not projected to be recovered above 1,000 MW within 30 minutes or unable to maintain system frequency at 59.91 Hz for 25 consecutive minutes; THEN: - Using the Hotline, notify the QSEs to implement EEA 3 Firm Load Shed and any measures associated with EEA 1 and 2, if not already implemented. Q#11 - Typical Hotline Script for EEA3 With Firm Load Shed |
| When ERS Time Periods Change | IF: - ERS Resources are deployed, and the Time Period is changing - If it is June – September and during time period TP3 or TP4 on a business day; THEN: - After Resource Operator has completed the XML deployment, make the QSE Hotline call Q#12 - Typical Hotline Script for EEA3 deploying ERS-10 / ERS-30 / both ERS-10 and ERS-30 / ERS-10, ERS-30 including Weather Sensitive |
| RRS Release to HASL | REVIEW REFERENCE DISPLAY: EMP Applications>Generation Area Status>Nodal Operations Status>Responsive Reserve Service Summary Data IF: - Unable to maintain PRC > 1000 MW; THEN: - May be necessary to de-activate Manual Responsive Reserve |
| Log | Log all actions. |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Frosch, Hartmann, Stone, and Barcalow | Prepares | November 10 , 2010 |
| Frosch and Hartmann | Procedure writers and editors | November 29, 2010 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2010 |
| Frosch, Foster, and Hartmann | Procedure writers and editors | January 3, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 26, 2011 |
| Frosch and Hartmann | Procedure writers and editors | March 23, 2011 |
| Frosch and Hartmann | Procedure writers and editors | April 20, 2011 |
| Frosch and Hartmann | Procedure writers and editors | June 6, 2011 |
| Frosch and Hartmann | Procedure writers and editors | July 18, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 1, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 30, 2011 |
| Frosch and Hartmann | Procedure writers and editors | September 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | October 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 16, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | April 25, 2012 |
| Frosch and Hartmann | Procedure writers and editors | May 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | May 30, 2012 |
| Barcalow, Frosch, and Hartmann | Procedure writers and editors | July 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | August 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | October 26, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 26, 2013 |
| Frosch and Hartmann | Procedure writers and editors | May 28, 2013 |
| Frosch and Hartmann | Procedure writers and editors | July 8, 2013 |
| Frosch and Hartmann | Procedure writers and editors | August 7, 2013 |
| Frosch and Hartmann | Procedure writers and editors | September 25, 2013 |
| Frosch and Hartmann | Procedure writers and editors | December 11, 2013 |
| Frosch and Hartmann | Procedure writers and editors | December 20, 2013 |
| Frosch, Gaddy, Hartmann, and Solis | Procedure writers and editors | April 1, 2014 |
| Frosch, Gaddy, and Hartmann | Procedure writers and editors | May 27, 2014 |
| Frosch and Hartmann | Procedure writers and editors | July 29, 2014 |
| Frosch and Hartmann | Procedure writers and editors | September 29, 2014 |
| Drummond, Frosch, and Hartmann | Procedure writers and editors | December 10, 2014 |
| Frosch and Thompson | Procedure writers and editors | December 19, 2014 |
| Frosch and Hartmann | Procedure writers and editors | February 25, 2015 |
| Frosch and Hartmann | Procedure writers and editors | March 25, 2015 |
| Frosch and Hartmann | Procedure writers and editors | April 29, 2015 |
| Frosch, Hartmann, and Gaddy | Procedure writers and editors | July 13, 2015 |
| Hartmann and Gaddy | Procedure writers and editors | December 22, 2015 |
| Hartmann, Gaddy, and Frosch | Procedure writers and editors | February 23, 2016 |
| Hartmann and Gaddy | Procedure writers and editors | April 22, 2016 |
| Hartmann, Gaddy, and Frosch | Procedure writers and editors | June 24, 2016 |
| Hartmann and Gaddy | Procedure writers and editors | July 15, 2016 |
| Hartmann, Gaddy, and Frosch | Procedure writers and editors | September 26, 2016 |
| Hartmann and Gaddy | Procedure writers and editors | October 31, 2016 |
| Hartmann, Gaddy, and Frosch | Procedure writers and editors | December 23, 2016 |
| Hartmann, Gaddy, and Frosch | Procedure writers and editors | March 24, 2017 |
| Hartmann and Gaddy | Procedure writers and editors | April 5, 2017 |
| Hartmann, Gaddy, and Ballew | Procedure writers and editors | May 26, 2017 |
| Hartmann, Gaddy, and Ballew | Procedure writers and editors | June 23, 2017 |
| Hartmann, Gaddy, and Ballew | Procedure writers and editors | July 24, 2017 |
| Hartmann, Gaddy, and Ballew | Procedure writers and editors | September 27, 2017 |
| Hartmann, Gaddy, and Ballew | Procedure writers and editors | October 27, 2017 |
| Hartmann, Gaddy, Ballew ,and Frosch | Procedure writers and editors | December 22, 2017 |
| Hartmann, Gaddy, Ballew ,and Frosch | Procedure writers and editors | February 22, 2018 |
| Hartmann, Gaddy, and Ballew | Procedure writers and editors | April 2, 2018 |
| Hartmann, Gaddy, Ballew ,and Frosch | Procedure writers and editors | April 27, 2018 |
| Hartmann, Gaddy, and Ballew | Procedure writers and editors | August 24, 2018 |
| Hartmann, Gaddy, and Ballew | Procedure writers and editors | September 27, 2018 |
| Hartmann, Gaddy, and Ballew | Procedure writers and editors | December 21, 2018 |
| Hartmann, Gaddy, and Ballew | Procedure writers and editors | January 25, 2019 |
| Hartmann, Gaddy, and Frosch | Procedure writers and editors | March 26, 2019 |
| Hartmann, Gaddy, and Pence | Procedure writers and editors | July 29, 2019 |
| Hartmann, Gaddy, and Cyphers | Procedure writers and editors | October 29, 2019 |
| Hartmann, Gaddy, and Cyphers | Procedure writers and editors | December 20, 2019 |
| Hartmann, Gaddy, and Cyphers | Procedure writers and editors | January 27, 2020 |
| Hartmann, Gaddy, and Cyphers | Procedure writers and editors | February 24, 2020 |
| Hartmann, Gaddy, and Cyphers | Procedure writers and editors | June 25, 2020 |
| Hartmann, Gaddy, Cyphers, and Sheets | Procedure writers and editors | December 23, 2020 |
| Hartmann, Gaddy, Cyphers, and Sheets | Procedure writers and editors | March 26, 2021 |
| Hartmann, Gaddy, Cyphers, and Sheets | Procedure writers and editors | April 29, 2021 |
| Hartmann, Gaddy, Cyphers, and Sheets | Procedure writers and editors | June 11, 2021 |
| Hartmann, Gaddy, Cyphers, and Sheets | Procedure writers and editors | July 8, 2021 |
| Hartmann, Gaddy, Cyphers, and Sheets | Procedure writers and editors | July 28, 2021 |
| Hartmann, Gaddy, Cyphers, and Sheets | Procedure writers and editors | August 27, 2021 |
| Hartmann, Gaddy, and Cyphers | Procedure writers and editors | November 29, 2021 |
| Hartmann, Gaddy, Cyphers, and Frosch | Procedure writers and editors | December 17, 2021 |
| Hartmann, Gaddy, and Cyphers | Procedure writers and editors | January 27, 2022 |
| Hartmann, Gaddy, Cyphers, and Frosch | Procedure writers and editors | February 24, 2022 |
| Hartmann, Gaddy, and Cyphers | Procedure writers and editors | May 20, 2022 |
| Hartmann, Gaddy, Cyphers, and Frosch | Procedure writers and editors | July 25, 2022 |
| Hartmann, Gaddy, and Cyphers | Procedure writers and editors | October 3, 2022 |
| Hartmann, Gaddy, and Cyphers | Procedure writers and editors | October 12, 2022 |
| Hartmann, Gaddy, Cyphers, and Frosch | Procedure writers and editors | December 22, 2022 |
| Hartmann, Gaddy, Cyphers, and Frosch | Procedure writers and editors | March 28, 2023 |
| Hartmann, Gaddy, Cyphers, and Luker | Procedure writers and editors | June 5, 2023 |
| Hartmann, Gaddy, Cyphers, and Luker | Procedure writers and editors | June 26, 2023 |

Manual Change History

| Procedure | Ver/Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All Sections | 1.0 / 0 | New procedures for all sections for Nodal implementation | November 28, 2010 |
| 2.4 3.1 3.2 3.4 3.5 3.6 4.2 5.3 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Updated Categories and Priorities Updated Response to High Frequency steps 15, 20 and 25 minutes and Response to Low Frequency step 15 Updated steps Failure Indication/Issues and QSE Capacity Issues Updated steps AGC/RLC Issues, System Wide Capacity Issue and AGC/RLC Issues Resolved Updated step 1 Updated step Capacity Surplus Updated step 2, 3, 4 and 5 Updated all steps of “Implement Level 2B” | December 1, 2010 |
| 4.1 4.2 5.2 | 1.0 / 1 1.0 / 2 1.0 / 1 | Updated step “MP unable to Override” Updated step 1 & 2 Updated step 1 in sections WATCH and Advisory | December 15, 2010 |
| 3.1 3.2 3.3 3.4 4.1 5.1 5.4 | 1.0 / 2 1.0 / 2 1.0 / 1 1.0 / 2 1.0 / 2 1.0 / 1 1.0 / 1 | Updated step “BAAL” Updated step “AGC Issues Resolved” Updated step “Hotline” Updated step “Failure Indications, AGC/RLC Issues, System Wide Capacity Issue, AGC/RLC Issues Resolved” Updated step 2 in “Workflow Controller Messages”, added new procedure “Exceeding West – North Stability Limit”, updated Note in “Generation Resource Shut-down/Start-up Process” Updated step 1 in “Watch” and step Hotline in “Scripts” Updated step 1 in “Move from EEA level 3 to EEA lever 2B” | January 5, 2011 |
| 2.4 2.5 2.6 2.7 3.1 3.2 3.3 3.4 3.5 4.1 4.2 5.1 5.2 5.3 5.4 5.5 6.1 6.2 6.3 | 1.0 / 0 1.0 / 2 1.0 / 0 1.0 / 0 1.0 / 3 1.0 / 3 1.0 / 2 1.0 / 2 1.0 / 1 1.0 / 3 1.0 / 3 1.0 / 2 1.0 / 2 1.0 / 2 1.0 / 2 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Added new procedure Changed procedure number Added new procedure Added new procedure Updated sections “Maintain System Frequency”, “Response to High Frequency”, “Response to Low Frequency” and “Actions when Frequency Telemetry in Incorrect. Combined sections 3.3, 3.4 & 4.2 into 3.2 Changed 3.5 “Potential DCS Event” to 3.3 & updated whole procedure Changed 3.6 “Monitor Capacity Reserves & Respond to Capacity Issues to 3.4 Changed 3.7 “Monitor and Control Time Error Correction to 3.5 & updated script Deleted Exceeding West-North Stability Limit Deleted Procedure Updated script Updated step 1 in “Advisory” and “Watch” Updated all steps Updated all steps Updated all steps Updated all steps Updated all steps Updated OCN | January 31, 2011 |
| 2.6 3.2 3.3 3.4 3.6 5.1 5.2 | 1.0 / 1 1.0 / 4 1.0 / 3 - / 3 1.0 / 0 1.0 / 3 1.0 / 3 | Updated step Site Failovers Updated step 3 in SCED Failure, step 4 in RLC Failure, Note in LFC (AGC) Failure and step 2 in EMS (LFC and RLC/SCED Failure Updated step 3 Updated step Capacity Shortage Added new procedure Updated Watch and Emergency Notice All step 1’s | March 25, 2011 |
| 2.6 3.1 3.2 3.3 3.6 5.1 5.4 5.5 | 1.0 / 2 1.0 / 4 1.0 / 5 1.0 / 4 1.0 / 1 - / 4 1.0 / 3 1.0 / 2 | Added steps and updated whole procedure Added new step to Maintain System Frequency and updated Response to High Frequency & Response to Low Frequency Updated steps 2, 3, 5 in SCED Failure; steps 2, 3, 4, 6 in RLC Failure; steps 1, 3 in LFC (AGC) Failure; steps 2, 5 in EMS (LFC and RLC/SCED) Failure Updated NERC Recovery Criteria, step 1 & 4 Updated 1st script Updated step 1 in Watch and Emergency Notice and step Post Updated 1st and 2nd script in Restore Firm Load, Updated 1st in Move From EEA Level 3 to EEA Level 2B Updated step 3 | April 22, 2011 |
| 3.3 5.1 5.3 5.4 6.1 6.2 6.3 6.4 | 1.0 / 5 1.0 / 5 1.0 / 3 1.0 / 4 1.0 / 2 1.0 / 0 1.0 / 2 1.0 / 2 | Updated step NERC Recovery Criteria Updated all step 1’s Updated step 1 in Implement EEA Level 1, step 1 in Implement EEA Level 2A, added note and updated step 2 in Implement EEA Level 2B, step 1 in Implement EEA Level 3 Updated all step 1’s Updated all steps Added new procedure Updated section number and all steps Updated section number and all steps | June 8, 2011 |
| 2.6 3.1 5.1 5.2 5.3 5.4 8.1 | 1.0 / 3 1.0 / 5 1.0 / 6 1.0 / 4 1.0 / 4 1.0 / 5 1.0 / 1 | Added step If EBPs are needed”, updated step IF EBPs are needed and W-N was Active before site failover started Added step Hydro, updated step Frequency Deviations Updated step Watch Updated all steps Updated 1st note, step 1 in EEA level 1 & 2A Updated step 1 in Move for EEA level 1 to 0 Added Market Participant Backup Control Center Transfer procedure | July 20, 2011 |
| 3.1 3.2 3.4 4.1 6.4 6.5 | 1.0 / 6 1.0 / 6 1.0 / 4 1.0 / 4 1.0 / 0 1.0 / 3 | Updated step Monitor, 15 minutes, 20 minutes, and 25 minutes in Response to High Frequency Updated step 2 in LFC Failure, step 4 & 5in EMS Failure Updated step Capacity Surplus Updated step 2 in Workflow Controller Messages Added new procedure “Extreme Hot Weather” Changed section number | August 3, 2011 |
| 2.7 3.1 5.1 5.2 5.3 5.4 6.4 7.1 | 1.0 / 1 1.0/ 7 1.0 / 7 1.0 / 5 1.0 / 5 1.0 / 6 1.0 / 1 1.0 / 1 | Updated step Hotline Call Updated NERC Standard reference table Added projected reserve capacity shortage and Extreme Hot Weather in Watch Updated step 1 in Advisory & Watch Updated 2nd Note, step 1 in Implement EEA 1, step Media Appeal & 1 in Implement EEA 2A, 1st Note & step 2 in Implement EEA 2B Added Note to Move From EEA 3 to EEA 2B and Move From EEA 2A to EEA 1 Updated temperature from 102 to 103 Updated 4th note and step 1 | September 1, 2011 |
| 3.2 5.3 5.4 | 1.0 / 7 1.0 / 6 1.0 / 7 | Updated SCED Failure step 2 and 3, RLC Failure step 3 and LFC (AGC) Failure step 3 Combined EEA 2A & B per NPRR 379 Combined EEA 2 A & B per NPRR 379 | October 1, 2011 |
| 3.2 | 1.0 / 8 | Updated script for LFC and EMS Failure | November 1, 2011 |
| 2.4 2.6 4.1 5.1 6.3 | 1.0 / 1 1.0 / 4 1.0 / 5 1.0 / 8 1.0 / 3 | Added step Review, Updated “Site Failover with W-N Active” Added Note to Large Resource Trips or Runbacks Updated Post in “Scripts” Updated “OCN” and “Advisory” All procedures in this manual have been reviewed. | December 15, 2011 |
| 1.2 3.1 4.1 8.1 | 1.0 / 1 1.0 / 7 1.0 / 6 - / 2 | Updated Scope Updated Response to High Frequency & Response to Low Frequency Updated Large Resource Trips or Runbacks, Quick Start Generation Resource Updated Market Participant Backup Control Center Transfer | January 19, 2012 |
| 2.1 3.1 5.1 5.3 7.1 8.1 | 1.0 / 1 1.0 / 8 1.0 / 7 1.0 / 9 1.0 / 7 1.0 / 2 1.0 / 3 | Updated paragraph 4 Updated BAAL Updated Desktop Guide reference & step QSE Override & QSE unable to Override Updated step 1 in Watch Updated Step 1 in Implement EEA Level 1 Updated Desktop Guide references Changed title names, updated steps 1 & 3 & step Power System Stabilizers (PSS) & Automatic Voltage Regulators (AVR) | March 1, 2012 |
| 2.1 3.1 3.2 3.3 3.5 4.1 5.1 6.2 6.3 6.4 8.1 | 1.0 / 2 1.0 / 9 1.0 / 9 1.0 / 6 1.0 / 2 1.0 / 8 1.0 / 10 1.0 / 4 1.0 / 2 1.0 / 4 1.0 / 4 | Changed TSO, DSP to TO Changed Shift Engineer to Operations Support Engineer, removed Automatic SCED Runs & Hydro Generation in Fast Response Mode, updated Note, Monitor/Deploy, 15 minutes, 20 minutes in Response to Low Frequency Updated step 2, 4 & 5, added SCED Data Input Failure, updated RLC Failure, LFC Failure, & EMMS Failure sections Updated NERC Recovery Criteria step & step 3 Updated Requirements and Notes Changed Shift Engineer to Operations Support Engineer, deleted Large Resource Trips or Runbacks section Updated OCN, Advisory, Watch, Emergency Notice sections Deleted Cold Weather, replaced with Extreme Cold Weather Section changed to Extreme Hot Weather, added OCN and Emergency Notice steps Section number changed Changed Shift Engineer to Operations Support Engineer | May 1, 2012 |
| 3.1 3.4 5.2 | 1.0 / 10 1.0 / 5 1.0 / 6 | Added back step Hydro Generation Operating in Synchronous Condenser Fast Response Mode Updated to reflect changes in the TAC approved Non-Spin document Updated to reflect changes in the TAC approved Non-Spin document | May 14, 2012 |
| 2.6 5.3 5.4 6.3 | 1.0 / 5 1.0 / 8 1.0 / 8 1.0 / 3 | Updated Site Failover step Updated EILS to ERS per NPRR 451 Updated EILS to ERS per NPRR 451 Updated EILS to ERS per NPRR 451 | June 1, 2012 |
| 1.3 2.6 5.1 5.3 5.4 6.2 6.3 7.1 | 1.0 / 1 1.0 / 6 1.0 / 11 1.0 / 9 1.0 / 9 1.0 / 5 1.0 / 4 1.0 / 3 | Removed ERCOT Shift Supervisor paragraph Updated all steps Updated all step 1’s Updated 2nd note, added TCEQ, & XML for ERS Clarified LR and ERS recalls Updated script for Emergency Notice Updated script for Emergency Notice Updated 4th note | July 16, 2012 |
| 2.6 3.1 4.1 5.3 | 1.0 / 7 1.0 / 11 1.0 / 9 1.0 / 10 | Added note to step Database Load Updated Frequency Deviations and Monitor Frequency for the Loss of EMS or Site Failover Incorporated NPRR348 Added 30 MIN ERS and updated steps 1, 2 & 3 on Implement EEA Level 1 | August 29, 2012 |
| 2.2 2.5 3.5 4.1 5.3 | 1.0 / 1 1.0 / 3 1.0 / 3 1.0 / 10 1.0 / 11 | Added Hotline Call Communication Updated step 3 Updated per NOGRR100 Added Note to Shut-down/Start-up Process and new Combine Cycle Generation Resources section Updated ERS scripts All procedures in this manual have been reviewed. | November 1, 2012 |
| 2.5 3.1 3.2 3.3 3.4 3.5 3.6 3.7 5.4 | 1.0 / 4 1.0 / 12 1.0 / 0 1.0 / 10 1.0 / 7 1.0 / 6 1.0 / 4 1.0 / 2 1.0 / 10 | Updated step 3 Updated BAAL New procedure, Monitor Large Ramp Events Updated section # & SCED failure step 2 Updated section # Updated section # Updated section # Updated section # Updated Cancel Watch All procedures in this manual have been reviewed. | March 1, 2013 |
| 2.6 2.7 3.1 3.2 3.3 3.4 3.7 4.1 5.1 5.2 5.3 5.4 5.5 6.1 6.2 6.3 6.4 | 1.0 / 8 1.0 / 2 1.0 / 13 1.0 / 1 1.0 / 11 1.0 / 8 1.0 / 3 1.0 / 11 1.0 / 12 1.0 / 8 1.0 / 12 1.0 / 11 1.0 / 3 1.0 / 3 1.0 / 6 1.0 / 5 1.0 /5 | Updated scripts Updated scripts Updated Monitor Frequency for the Loss of EMS or Site Failover & Actions when Frequency Telemetry is Incorrect Updated scripts Updated scripts Updated script Updated scripts Added QSGR Decommitment step to QSGR Added Generic and Specific scripts Updated Note and scripts Updated TCEQ section and scripts Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts Correct spelling and updated script | June 1, 2013 |
| 2.6 3.1 3.2 3.8 5.1 5.3 5.4 | 1.0 / 9 1.0 / 14 1.0 / 2 1.0 / 0 1.0 / 13 1.0 / 13 1.0 / 12 | Changed title name & updated step EMS Changes & added MMS Changes Updated steps Base Point Deviation & 10 Minutes Updated 1st note Moved procedures from Resource desk Updated step 1 in Watch & Emergency Notice Updated step Pilot Project WS ERS Updated step Reserves | July 15, 2013 |
| 2.6 3.2 3.8 4.1 | 1.0 / 10 1.0 / 3 1.0 / 1 1.0 / 12 | Updated MMS Changes Updated 1st Note Updated Unit & Load RRS Shortage & Not Dispatchable to SCED Updated Shutdown/Startup | August 9, 2013 |
| 3.8 | 1.0 / 2 | Updated Unit RRS Shortage, Load RRS Shortage, REG Shortage, & added Real-Time Non-Spin Shortage | September 27, 2013 |
| 2.4 3.1 3.2 3.3 3.4 3.5 3.7 4.1 5.1 5.2 5.3 5.4 5.5 6.1 6.2 6.3 6.4 7.1 8.1 | 1.0 / 2 1.0 / 15 1.0 / 4 1.0 / 12 1.0 / 9 1.0 / 7 1.0 / 4 1.0 / 13 1.0 / 14 1.0 / 9 1.0 / 14 1.0 / 13 1.0 / 4 1.0 / 4 1.0 / 7 1.0 / 6 1.0 / 6 1.0 / 4 1.0 / 5 | Updated step Log Updated step Frequency Deviations & step Log Updated step Log Updated step Log Updated step Log Added step RMR & updated step Log Updated step Log Updated step Log Updated step Log Updated step Log Updated step Log Updated step Log Updated step Log Updated step Log Updated step Log Updated step Log Updated note and step Log Updated step Log Added & updated step Log All procedures in this manual have been reviewed | December 13, 2013 |
| 2.6 3.3 5.1 | 1.0 / 11 1.0 / 13 1.0 / 15 | Updated for NPRR542 Updated for NPRR542 Updated for NPRR542, deleted West to North GTL and updated procedure for North to Houston to a new GTL | January 1, 2014 |
| 2.6 3.1 3.3 3.5 3.6 4.1 5.3 5.4 6.4 8.1 | 1.0 / 12 1.0 / 16 1.0 / 14 1.0 / 8 1.0 / 5 1.0 / 14 1.0 / 15 1.0 / 14 1.0 / 7 1.0 / 6 | Updated Site Failover Complete Updated VDI information, step Monitor/Deploy & step 10 Minutes in Response to Low Frequency Updated VDI information Updated VDI information Updated step Terminating Time Error Correction Updated VDI information Updated ERS, Media appeal, TCEQ and VDI information Updated steps Reserves and 1 in Restore firm load and step 2 in Move From EEA Level 2 to EEA Level 1 Updated Note Updated Requests to Decommit Self-committed Resource in Operating Period | April 4, 2014 |
| 2.2 3.1 3.3 4.1 5.1 5.2 6.2 6.3 | 1.0 / 2 1.0 / 17 1.0 / 15 1.0 / 15 1.0 / 16 1.0 / 10 1.0 / 8 1.0 / 7 | Added VDIs to Master QSEs Updated step BAAL Updated SCED Failure & SCED Data Input Failure steps Updated QSGR in Quick Start Generation Resource Added Note, updated Market Notices Advisory & Watch Updated Watch steps Updated Emergency Notice step Updated Emergency Notice step | June 1, 2014 |
| 3.5 5.3 | 1.0 /9 1.0 / 16 | Updated Deploying Non-Spin, added HASL Release & Recall Added Media Appeal | August 1, 2014 |
| 4.1 5.1 5.3 | 1.0 / 16 1.0 / 17 1.0 / 17 | Updated Reference section step 2 Updated Generic Script Added HASL Release step | October 1, 2014 |
| 2.3 2.4 2.6 3.3 3.5 5.1 5.3 | 1.0 / 1 1.0 / 3 1.0 / 13 1.0 / 16 1.0 / 10 1.0 / 18 1.0 / 18 | Updated all steps Updated step Send E-mail Deleted Site Failover with W-N Active & updated step If EBPs are Needed Updated 1st note & updated scripts Added new procedure, “Valley Generation” Updated GMD scripts Updated scripts to consolidate All procedures in this manual have been reviewed | December 15, 2014 |
| 6.2 | 1.0 / 9 | Updated Note and scripts | December 22, 2014 |
| 2.2 3.1 3.2 3.5 3.9 6.2 | 1.0 / 3 1.0 / 18 1.0 / 5 1.0 / 11 1.0 / 0 1.0 / 10 | Added Dispatch and VDI definitions Updated Objective and BAAL Updated procedure Updated step 1 and added Log on Valley Generation Added new procedure for NOGRR136 Updated scripts | March 1, 2015 |
| 3.1 3.3 3.5 3.10 4.1 5.1 | 1.0 / 19 1.0 / 17 1.0 / 12 1.0 / 0 1.0 / 17 1.0 / 19 | Clarification to step Frequency Deviation & Hydro Operating in Synch. Condenser Mode Updated Dispatch Instruction scripts Clarification to step HASL Release Manually Deploy RRS New GMD procedure Updated Dispatch Instruction scripts Deleted script for GMD | March 30, 2015 |
| 2.6 2.7 3.2 3.3 3.4 3.63.7 3.10 5.1 5.2 5.3 5.4 5.5 6.1 6.2 6.3 6.4 | 1.0 / 14 1.0 / 3 1.0 / 6 1.0 / 18 1.0 / 10 1.0 / 6 1.0 / 5 1.0 / 1 1.0 / 20 1.0 / 11 1.0 / 19 1.0 / 15 1.0 / 5 1.0 / 5 1.0 / 11 1.0 / 8 1.0 / 8 | Moved scripts to new script procedure Moved scripts to new script procedure Updated 1st note and moved scripts to new script procedure Updated step 2 on SCED Data Input Failure & moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Updated 4th bullet on Emergency Notice & moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure | May 1, 2015 |
| All Sections 2.6 3.5 3.9 3.10 5.1 5.2 6.3 | 1.0 / 1 1.0 / 15 1.0 / 13 1.0 / 1 1.0 / 2 1.0 / 21 1.0 / 12 1.0 / 9 | Added a “Q” for numbered QSE scripts Renamed section to Site Failovers and Database Loads Updated link for Monitor in the Valley Generation Updated 1st Note Updated Procedure Purpose and removed script Updated Specific Scripts, New GTC Updated Q#1, Q#2, Q#3, & Q#4 Script titles Removed Watch script | July 15, 2015 |
| 2.6 3.2 3.3 3.4 3.6 3.7 3.9 3.10 5.1 5.2 5.3 5.4 5.5 6.1 6.2 6.3 6.4 | 1.0 / 16 1.0 / 7 1.0 / 19 1.0 / 11 1.0 / 7 1.0 / 6 1.0 /2 1.0 / 3 1.0 / 21 1.0 / 13 1.0 / 20 1.0 / 16 1.0 / 6 1.0 / 6 1.0 / 12 1.0 / 10 1.0 / 9 | Updated step MMS Changes Typical Script Q#19 Updated step Site Failover Q#20 Updated step Site Failover Complete Q#21 Updated Step If EBP’s are needed Q#22 Updated step Site Failover Complete If EBP’s were needed Q#23 Updated step 2 Q#26 Updated SCED Failure step 2 Q#27 & step 4 Q#28 Updated SCED Data Input Failure step 1 Q#29 Updated RLC Failure step 2 Q#30 & step 4 Q#31 Updated LFC (AGC) Failure step 1 Typical Script step 2 Q#32, step 4 Typical script & Q#33 Updated EMMS (LFC and RLC/SCED) Failure step 1 Typical Script, step 2 Q#34, step 5 Typical Script & Q#35 Updated step 3 Q#36 Updated step Initiating Time Error Correction Q#37 Updated step Terminating Time Error Correction Q#38 Updated step Issue Watch and Deploy Non-Spin Q#39 Updated step Issue Emergency Notice & Deploy Load Resources Q#40 Updated step Recall Load Resources Q#41 Updated step Recall Non-Spin Q#42 Updated step Start CFC Test & End CFC Test Typical Scripts Updated step 1 Q#43 Updated step K Level Increases/Decreases Q#44 Updated step Cancel Q#45 Updated Title Operating Condition Script Updated step Hotline Q#46 Updated step Hotline Cancellation Q#47 Updated Title Specific Scripts for Transmission Operator [State Estimator/RTCA/VSAT] Updated step State Estimator/RTCA Not Solved In 30 MIN Q#48 & Q#49 Updated step VSAT Not Solved In 30 MIN Q#50 & Q#51 Updated step Qualifying Facility Directed to Operate Below LSL Q#52 & Q#53 Updated step New GTC Q#54 Updated step Transmission Watch Q#55 & Q#56 Updated Advisory step Issue Advisory Q#1 Updated Advisory step Cancel Advisory Q#2 Updated Watch step Issue Watch Q#3 Updated Watch step Cancel Watch Q#4 First Note, Updated Implement EEA Level 1 step EEA 1 PRC <2300 Q#5 & Q#6 Updated Implement EEA Level 2 step ERS Resources Q#7 Updated Implement EEA Level 2 step Load Resources Q#8 Updated Implement EEA Level 2 step When ERS Business Hours Change Q#9 Updated Implement EEA Level 3 step When ERS Business Hours Change Q#12, and Implement NPRR708 for EEA, Updated Restore Firm Load step 1 Q#13 Updated Move From EEA Level 3 to EEA Level 2 step 1 Q#14 Updated Move From EEA Level 2 to EEA Level 1 step 1 Q#15 Updated Move From EEA Level 1 to EEA Level 0 step 1 Q#16 Updated Cancel Watch step 1 Q#17 Updated step Return to Normal QSE Notification Q#57 Updated step Emergency Notice Q#61 Updated step Emergency Notice Q#65 Updated step Emergency Notice Q#69 Updated step OCN/Advisory/Watch Q#70 All procedures in this manual have been reviewed | December 31, 2015 |
| 1.3 2.1 3.3 5.1 | 1.0 / 2 1.0 / 3 1.0 / 20 1.0 / 22 | Removed Interchange Coordinator Updated System Operator Responsibility and Authority Updated SCED Failure Note Corrected spelling Qualifying Facility Directed to Operate below LSL Q#52 | March 1, 2016 |
| 2.4 3.1 3.2 4.1 | 1.0 / 4 1.0 / 20 1.0 / 8 1.0 / 18 | Added 2nd Send E-Mail Updated Frequency bias and BAAL step Updated Down Ramp Event step 2 Updated QSGR Qualification Test | April 29, 2016 |
| 2.1 2.2 3.1 3.3 3.5 3.9 4.1 5.1 5.5 | 1.0 / 4 1.0 / 4 1.0 / 21 1.0 / 21 1.0 / 14 1.0 / 3 1.0 / 19 1.0 / 23 1.0 / 7 | Updated for COM-002-4 Updated for COM-002-4 Updated for BAL-001-2 and COM-002-4 Updated for COM-002-4 Updated Deploying Non-Spin step Updated for COM-002-4 Updated for COM-002-4 Updated for COM-002-4 Updated for COM-002-4 | June 30, 2016 |
| 5.3 | 1.0 / 21 | Changed Business Hour to Time Period | July 15, 2016 |
| 2.2 3.3 | 1.0 / 5 1.0 / 22 | Added Hotline Call Communication Note Added SCED Failure Frequency Guidelines Updated LFC Failure Step 2 Q#32 Script Title Updated LFC Failure Step 4 Q#33 Script Title Updated EMMS Failure step 2 Q#34 Script Title Updated EMMS Failure step 5 Q#35 Script Title | September 30, 2016 |
| 3.5 5.1 | 1.0 / 15 1.0 / 24 | Updated Valley Generation step 1 Added Specific Scripts for Transmission Operator step Transmission Emergency script Q#71 | November 2, 2016 |
| 4.1 | 1.0 / 20 | Added Real-Time Data Issues known by the QSE All procedures in this manual have been reviewed | December 30, 2016 |
| 1.3 2.1 2.5 2.6 2.7 3.2 3.10 5.1 5.3 5.5 6.1 6.2 6.3 8.1 | 1.0 / 3 1.0 / 5 1.0 / 5 1.0 / 17 1.0 / 4 1.0 / 9 1.0 / 4 1.0 / 25 1.0 / 22 1.0 / 8 1.0 / 7 1.0 / 13 1.0 / 11 1.0 / 7 | Updated Roles/Responsibilities section Updated for IRO-001-4 Updated categories to show RAS Updated procedure purpose Updated procedure purpose Deleted ELRAS and held location open Updated procedure purpose Updated title and all 1st steps Removed step WS ERS Added Implement EEA Level 3 step EEA3 PRC <1000 MW Updated first note Updated procedure purpose Updated procedure purpose Updated procedure purpose Updated procedure purpose | March 31, 2017 |
| 3.1 | 1.0 / 22 | Updated Frequency bias | April 4, 2017 |
| 3.3 5.1 | 1.0 / 23 1.0 / 26 | Added section on ICCP Outages Updated Transmission Watch | April 6, 2017 |
| 3.1 3.5 | 1.0 / 23 1.0 / 16 | Updated Response to Low Frequency step Monitor/Deploy Updated Insufficient Generation step Deploying Non-Spin | June 1, 2017 |
| 3.1 5.3 | 1.0 / 24 1.0 / 23 | Updated Response to Low Frequency step 25 Minutes Updated 1st note, step EEA Level 2 and EEA Level 3 | June 30, 2017 |
| 2.4 3.1 5.3 | 1.0 / 5 1.0 / 25 1.0 / 24 | Updated steps Added note Response to Low Frequency Updated step 20 Minutes and added scripts Added note Implement EEA Level 2 and Level 3 | July 28, 2017 |
| 3.1 3.3 | 1.0 / 26 1.0 / 24 | Updated Response to Low Frequency step 10 Minutes Updated LFC (AGC) Failure steps 1 & 3 Updated EMMS (LFC and RLC/SCED) Failure steps 1,3, &4 | September 29, 2017 |
| 3.9 | 1.0 / 4 | Updated note | October 31, 2017 |
| 2.4 3.4 7.1 | 1.0 / 6 1.0 / 12 1.0 / 5 | All procedures in this manual have been reviewed Updated steps Updated procedure for BAL-002-2 Updated Primary Control Center 4th note | December 28, 2017 |
| 3.3 3.5 3.9 | 1.0 / 25 1.0 / 17 1.0 / 5 | Updated ICCP Ouages to include MIS and outage scheduler Added Note Updated Start CFC Test & End CFC Test | February 28, 2018 |
| 3.1 | 1.0 / 27 | Updated Maintain System Frequency step Objective | April 5, 2018 |
| 2.2 2.7 3.3 3.9 | 1.0 / 6 1.0 / 5 1.0 / 26 1.0 / 6 | Updated procedure purpose Updated steps Updated steps LFC (AGC) Failure and EMMS (LFC and RLC/SCED) Updated steps | May 1, 2018 |
| 3.1 3.3 3.9 5.3 | 1.0 / 28 - / 27 1.0 / 7 1.0 / 25 | Updated Response to High Frequency & Response to Low Frequency steps Monitor Updated SCED Failure step3 Updated SCED Data Input Failure step 2 Updated RLC Failure step NOTE and step 3 Updated LFC (AGC) Failure NOTE, step 1 & 5 Added step 4. Moved step 4 to step 5 Updated EMMS (LFC and RLC/SCED) Failure step 1, 3, & 5 Updated Note Added Implement EEA Level 3 step | August 31, 2018 |
| 3.1 5.1 | 1.0 / 29 1.0 / 27 | Updated Monitor Frequency for the Loss of EMS or Site Failover Updated for NPRR 825 | October 1, 2018 |
| 3.3 5.3 | 1.0 / 28 1.0 / 26 | Added STATE ESTIMATOR (SE)/Real-Time Contingency Analysis (RTCA) Deleted duplicate Log step All procedures in this manual have been reviewed | December 28, 2018 |
| 2.4 | 1.0 / 7 | Updated steps | January 31, 2019 |
| 3.1 | 1.0 / 30 | Updated Maintain System Frequency step Objective | April 1, 2019 |
| 3.1 4.1 | 1.0 / 31 1.0 / 21 | Updated Response to High Frequency step Monitor & Response to Low Frequency steps Updated SCED Solution Time Parameter step Automatic Trigger | August 1, 2019 |
| 3.5 5.3 | 1.0 / 18 1.0 / 27 | Updated Manually Deploy RRS and Recall steps Added Implement EEA Level 1 step | November 1, 2019 |
| 5.3 5.4 | 1.0 / 28 1.0 / 17 | Updated MSSC Updated MSSC All procedures in this manual have been reviewed | January 1, 2020 |
| 3.1 3.3 3.5 5.4 7.1 | 1.0 / 32 1.0 / 29 1.0 / 19 1.0 / 18 1.0 / 6 | Clarified RUC commits/decommits Clarified RUC commits/decommits Clarified RUC commits/decommits Clarified RUC commits/decommits Updated Primary Control Center steps 1 & 3 | January 31, 2020 |
| 3.1 3.3 7.1 | 1.0 / 33 1.0 / 30 1.0 / 7 | Updated Response to Low Frequency Added Note to LFC (AGC) Failure & EMMS (LFC and RLC/SCED) Failure Updated Title and removed Alternate Control Center | February 28, 2020 |
| 2.1 5.1 5.4 | 1.0 / 6 1.0 / 28 1.0/19 | Added Advance Action Notice per NPRR930 Added Advance Action Notice section per NPRR930 Updated Cancel Watch | July 1, 2020 |
| 2.6 2.7 3.3 3.9 5.1 5.2 6.1 6.2 6.3 6.4 8.1 | 1.0 / 18 1.0 / 6 1.0 / 31 1.0 / 8 1.0 / 29 1.0 / 14 1.0 / 8 1.0 / 14 1.0 / 12 1.0 / 10 1.0 / 8 | Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 & added Note Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 All procedures in this manual have been reviewed | December 31, 2020 |
| 2.3 3.1 3.9 | 1.0 / 2 1.0 / 34 1.0 / 9 | Organization change Organization change Organization change | April 1, 2021 |
| 2.6 5.1 | 1.0 / 19 1.0 / 30 | Changed Notice Builder to Grid Conditions Communications (GCC) Notices Added information on AAN information | May 6, 2021 |
| 2.3 2.4 5.3 5.4 | 1.0 / 3 1.0 / 8 1.0 / 29 1.0 / 20 | Updated email Updated email Added Note Added Note | June 16, 2021 |
| 3.5 5.1 5.2 5.4 | 1.0 / 20 1.0 / 31 1.0 / 15 1.0 / 21 | Updated for OBDRR031 Updated for OBDRR031 Updated for OBDRR031 Updated for OBDRR031 | July 12, 2021 |
| 3.5 5.2 | 1.0 / 21 1.0 / 16 | Updated for OBDRR031 Updated Cancel Watch | July 31, 2021 |
| 5.3 | 1.0 / 30 | Updated 1st Note | September 1, 2021 |
| 5.2 5.3 | 1.0 / 17 1.0 / 31 | Updated for NPRR1106 Updated for NPRR1106 | December 1, 2021 |
| 2.2 3.1 5.1 5.2 5.4 6.1 6.2 6.3 6.4 | 1.0 / 7 1.0 / 35 1.0 / 32 1.0 / 18 1.0 / 22 1.0 / 9 1.0 / 15 1.0 / 13 1.0 / 11 | Updated step 1 Updated instruct to coordinate Updated all steps Updated for clarification Updated Move From EEA Level 2 to EEA Level 1 Updated all steps Updated all steps Updated all steps Updated all steps All procedures in this manual have been reviewed | December 31, 2021 |
| 6.4 | 1.0 / 12 | Updated Note | February 1, 2022 |
| 2.8 | 1.0 / 0 | New procedure section | March 1, 2022 |
| 3.1 3.5 3.7 5.3 | 1.0 / 36 1.0 / 22 1.0 / 7 1.0 / 32 | Updated for NPRR939 & NOGRR191 Updated for NPRR939, NPRR1093 & NOGRR191 Updated for NPRR939 Updated for NPRR939 & NOGRR191 | May 26, 2022 |
| 5.2 | 1.0 / 19 | Updated Steps | July 29, 2022 |
| 5.3 | 1.0 / 33 | Added ESR | October 7, 2022 |
| 3.1 5.2 5.3 | 1.0 / 38 1.0 / 20 1.0 / 34 | Updated Response to Low Frequency steps Updated Advisory Updated RRS Release to HASL | October 14, 2022 |
| 3.5 5.2 5.3 5.4 | 1.0 / 23 1.0 / 21 1.0 / 35 1.0 / 23 | Updated Deploying Non-Spin Updated Media Appeal and TCEQ Added Large Load Curtailment Program step and Watch Updated Media Appeal, TCEQ and EEA 1 Added Cancel Advisory and Log All procedures in this manual have been reviewed | December 30, 2022 |
| 3.1 5.3 6.4 | 1.0 / 39 1.0 / 36 1.0 / 13 | Added Note Response to Low Frequency Added Note Updated procedure title and note | March 31, 2023 |
| 3.1 3.3 3.5 3.7 3.8 4.1 5.3 5.4 | 1.0 / 40 1.0 / 32 1.0 / 24 1.0 / 8 1.0 / 3 1.0 / 22 1.0 / 37 1.0 / 24 | Updated for NPRR863 Updated for NPRR863 Updated for NPRR863 Updated for NPRR863 Updated for NPRR863 Updated for NPRR863 Updated for NPRR863 Updated for NPRR863 | June 9, 2023 |

| 3.1 3.3 3.5 3.7 4.1 5.3 | 1.0 / 41 1.0 / 33 1.0 / 25 1.0 / 9 1.0 / 23 1.0 / 38 | Updated Deploy to Release Updated Deployments to Instructions Updated Deploy to Release Updated Note Updated Deploy to Release Updated Deploy to Release | June 30, 2023 |
| --- | --- | --- | --- |