- Power Operations Bulletin # 1105

ERCOT has posted/revised the Resource Desk manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

- http://www.ercot.com/mktrules/guides/procedures/index.html

## 3.3	Notifications for Diminishing Reserves, Deploying Non-Spin and ERS

Procedure Purpose:  Monitor the Physical Responsive Capability (PRC) for issuing advance notice of diminishing Responsive Reserve.  This also includes the deployment of Non-Spin when PRC drops below 3200 MW and deployment of Emergency Response Service (ERS) when PRC drops below 3000 MW.

| Protocol Reference | 3.17.3(2) | 6.5.7.6.2.2(13) | 6.5.7.6.2.3 | 6.5.9.4.1 |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.5.3.1(1)(d) | 4.5.3.1(1)(e) |  |  |
| NERC Standard | EOP-011-2 R2, R2.1, R2.2, R2.2.3, R2.2.3.1 | IRO-001-4 R1 | TOP-001-5 R2 |  |

| Version: 1 | Revision: 25 | Effective Date: November 1, 2023 |
| --- | --- | --- |

| Step |  | Action |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Media Appeal |  | When an ERCOT-wide appeal through the public news media for voluntary energy conservation is made, make posting: ## Typical ERCOT Website posting for media appeal: ERCOT has issued an appeal through the public news media for voluntary energy conservation for [Day, Date, HE XX:XX through XX:XX]. |  |  |  |
| PRC < 3200 MW |  | IF: - Notified by the ERCOT Real Time operator of the need to deploy Non-Spin due to PRC < 3200 MW. THEN: - Coordinate with Real Time operator and Shift Supervisor, - Coordinate with the Transmission Operator to verify the Non-Spin does not create congestion, - Deploy the desired Group(s) or all the available Non-Spin capacity. (Refer to Desktop Guide Resource Desk Section 2.1.1) - Post message on the ERCOT Website for Non-Spin deployment. Typical ERCOT Website Posting for Non-Spin deployment: “At [xx:xx] approximately [xx] MW of Non-Spin has been deployed, anticipated duration is [xx].” |  |  |  |
| NOTE |  | The Projected Ramp Available in 30min represents the calculation HASL – (GTBD + GTBD offset) – (IRR Curtailment) – (30-minute Net Load Ramp) |  |  |  |
| Projected Ramp Available in 30min |  | IF: - Notified by the ERCOT Real Time operator of the need to deploy Group(s) / or All Non-Spin due to the Projected Ramp Available in 30min < -300; THEN: - Coordinate with Real Time operator and Shift Supervisor, - Coordinate with the Transmission Operator to verify the Non-Spin does not create congestion, - Deploy half of the available groups for Non-Spin, if not already deployed, (Refer to Desktop Guide Resource Desk Section 2.1.1) - Post message on the ERCOT Website for Non-Spin deployment. IF: - Notified by the ERCOT Real Time operator of the need to deploy Group(s) / or All Non-Spin due to the Projected Ramp Available in 30min < -500; THEN: - Coordinate with Real Time operator and Shift Supervisor, - Coordinate with the Transmission Operator to verify the Non-Spin does not create congestion, - Deploy the available groups for Non-Spin, as needed, if not already deployed, (Refer to Desktop Guide Resource Desk Section 2.1.1) - Post message on the ERCOT Website for Non-Spin deployment. |  |  |  |
| NOTE |  | If Non-Spin is deployed from one operating day to the next operating day, new deployments will need to be sent for the new day. |  |  |  |
| Request Resource Stay Online |  | IF: - Notified by a QSE that their Off-line Non-Spin obligation has ended, AND - The Resources is still needed; THEN: - Request the RUC operator to issue an electronic Dispatch Instruction to RUC commit. |  |  |  |
| Additional Deployment |  | IF: - Additional Non-Spin becomes available going into next hour; THEN: - Determine if the additional Non-Spin is needed, - Deploy if needed (Refer to Desktop Guide Resource Desk Section 2.1.1) |  |  |  |
| LOG |  | Log all actions |  |  |  |
| NOTE |  | All Non-Spin must be deployed before requesting Large Load Curtailment participants to curtail consumption and deploying ERS. |  |  |  |
| Request Large Load Curtailment Program |  | WHEN: - Notified by the ERCOT Shift Supervisor that the Large Load Voluntary Curtailment Program Participants were requested to curtail consumption; THEN: - Post message that Large Load Voluntary Curtailment Program Participants were requested to curtail consumption on the ERCOT Website. Typical ERCOT Website Posting for Large Load Curtailment Program Participants: ERCOT has requested the ERCOT Large Load Voluntary Curtailment Program Participants to curtail consumption. ERCOT will send another notification when curtailment is no longer requested. |  |  |  |
| Large Load Curtailment Program Ended |  | WHEN: - Notified by the ERCOT Shift Supervisor that the Large Load Voluntary Curtailment Program Participants requested to curtail consumption ended; THEN: - Post message that Large Load Voluntary Curtailment Program Participants requested to curtail consumption ended on the ERCOT Website. Typical ERCOT Website Posting for Large Load Curtailment Program Participants Ended: ERCOT has ended the request for ERCOT Large Load Voluntary Curtailment Program Participants to curtail consumption. |  |  |  |
| ### Watch |  |  |  |  |  |
| NOTE |  | XML messages and Hotline calls are required for all deployments of Load Resources and ERS Resources |  |  |  |
| ERS-30 |  | ERS with a thirty-minute ramp period. |  |  |  |
| ERS-10 |  | ERS with a ten-minute ramp period. |  |  |  |
| WS-ERS |  | Each Standard Contract Term(SCT) Request for Proposal (RFP) will state what time periods in that SCT weather sensitive can provide offers for. |  |  |  |
| Issue Watch, ERS Deployments & DVR |  | WHEN: - PRC falls < 3000 MW and is not projected to recover above 3000 MW within 30 minutes, AND all Non-Spin has been deployed; THEN: - Coordinate with the Real-Time Operator, Transmission Operator and Shift Supervisor, - Post message for Watch on the ERCOT Website, AND - Determine whether system conditions warrant the deployment of ERS-30 / ERS-10 / both ERS-30 and ERS-10 / Weather Sensitive,/ Distribution Voltage Reduction. Refer to the ERS tab on the Real-Time Values Spreadsheet for amounts in each time period and number of times deployed: - Consider the peak hour, deploy all ERS-30 / ERS-10 / both ERS-30 and ERS-10 / Weather Sensitive / Distribution Voltage Reduction where available to prevent PRC from falling < 3000 MW, - When deploying the ERS, always deploy the weather-sensitive ERS if available for the current time period. - Post message for deploying ERS-30/10/WS on the ERCOT Website. - Coordinate with the Transmission Operator that ERCOT is requesting Transmission Operators to implement distribution voltage reduction measures if available. - Post message for requesting Distribution Voltage Reduction on the ERCOT Website Typical ERCOT Website Posting an Watch for PRC: “ERCOT is issuing an Advisory for Physical Responsive Capability less than 3000 MW.” Typical ERCOT Website Posting for Non-Spin deployment: “At [xx:xx] approximately [xx] MW of Non-Spin has been deployed, anticipated duration is [xx].” Typical ERCOT Website Posting for deploying ERS-30/10/WS: Reserves are below 3,000 MW. Emergency Response Service 30/10/Weather Sensitive is being deployed. Typical ERCOT Website Posting for requesting distribution voltage reduction: Reserves are below 3,000 MW. ERCOT is requesting Transmission Operators to implement distribution voltage reduction measures if available. |  |  |  |
| NOTE |  | All Non-Spin must be deployed before requesting Large Load Curtailment participants to curtail consumption and deploying ERS. |  |  |  |
| ERS Time Period Changes |  | IF: - ERS Resources are deployed, and the Time Period is changing and if ERS is still needed; THEN: - Deploy next Time Period - Take into consideration the time requirement for the ERS-10 and ERS-30 |  |  |  |
| Cancel Watch, Recall ERS & DVR |  | WHEN: - PRC > 3000 MW or greater; THEN: - Coordinate with Real-Time Operator and Shift Supervisor, AND - Send XML message to recall ERS, including Weather Sensitive - ERS must be recalled first before hotline call is made (see Desktop Guide Resource Desk Section 2.3.3) - Coordinate with Transmission desk to ensure Transmission Operators have been requested to return Distribution Voltage Reduction to normal operation. - Coordinate with Real-Time Operator to notify QSE’s using the Hotline, - Cancel message(s) on ERCOT Website. |  |  |  |
| Off-Line Non-Spin Termination |  | IF: - Notified by the ERCOT Real Time Operator that Non-Spin is no longer needed; THEN: - Recall the Non-Spin, by sending a Zero MW XML (Refer to Desktop Guide Resource Desk Section 2.1.4). - Post message on the ERCOT Website to recall the Non-Spin Typical ERCOT Website Posting for Non-Spin Recall: “At [xx:xx], All Non-Spin has been recalled.” |  |  |  |
| Log |  | Log all actions. |  |  |  |
| Additional Deployment |  | IF: - Additional Non-Spin becomes available going into next hour; THEN: - Determine if the additional Non-Spin is needed, - Deploy if needed (Refer to Desktop Guide Resource Desk Section 2.1.1) |  |  |  |
| Request Resource Stay Online |  | IF: - Notified by a QSE that their Off-line Non-Spin obligation has ended, AND - PRC < 3000 MW; THEN: - Request that the Resource stay On-line, - Request RUC operator to issue an electronic Dispatch Instruction to RUC commit |  |  |  |
| NOTE |  | If Non-Spin is deployed from one operating day to the next operating day, new deployments will need to be sent for the new day. |  |  |  |
| Cancel Watch |  | WHEN: - PRC > 3000 MW; THEN: - Coordinate with the Real-Time Operator and Shift Supervisor - Cancel message for Watch on the ERCOT Website |  |  |  |
| Log |  | Log all actions. |  |  |  |

## 7.2	Implement EEA Levels

Procedure Purpose:  To provide for maximum possible continuity of service while maintaining the integrity of the ERCOT system to reduce the chance of cascading outages.

| Protocol Reference | 6.5.7.6.2.2(1)(b) & (13) | 6.5.7.6.2.3(1) | 6.5.9.4 | 6.5.9.4.1 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.4.2 |  |  |  |
| Guide Reference | 4.5.3 | 4.5.3.1 | 4.5.3.2 | 4.5.3.3 |
|  | 4.5.3.4 |  |  |  |
| NERC Standard | EOP-011-2 R2, R2.1, R2.2, R2.2.3, R2.2.3.1, R2.2.7 | IRO-001-4 R1 | TOP-001-5 R2 |  |

| Version: 1 | Revision: 31 | Effective Date: November 1, 2023 |
| --- | --- | --- |

| Step |  | Action |  |  |
| --- | --- | --- | --- | --- |
| NOTE |  | - ERCOT MAY immediately implement EEA Level 2 when clock-minute average system frequency falls below 59.91 Hz for 15 consecutive minutes. - ERCOT MAY immediately implement EEA Level 3 any time the clock-minute average system frequency falls below 59.91 Hz for 20 consecutive minutes OR when steady-state frequency falls below 59.8 Hz for any duration of time. - ERCOT SHALL immediately implement EEA Level 3 any time the steady-state frequency is below 59.5 Hz for any duration. |  |  |
| Note |  | ERCOT will declare an EEA Level 1 when PRC falls below 2,500 MW and is not projected to be recovered above 2,500 MW within 30 minutes without the use of the following actions that are prescribed for EEA Level 1 |  |  |
| NOTE |  | Confidentiality requirements regarding Transmission Operations and System Capacity information will be lifted, as needed to restore reliability. |  |  |
| NOTE |  | Manually deploy Load Resources other than Controllable Load Resources providing ECRS or RRS before an Energy Emergency Alert (EEA), to maintain a minimum 500 MWs of Physical Responsive Capability (PRC) reserves on Generation Resources. |  |  |
| NOTE |  | XML messages and Hotline calls are required for all deployments of Load Resources and ERS Resources |  |  |
| ERS-30 |  | ERS with a thirty-minute ramp period. |  |  |
| ERS-10 |  | ERS with a ten-minute ramp period. |  |  |
| WS-ERS |  | Each Standard Contract Term(SCT) Request for Proposal (RFP) will state what time periods in that SCT weather sensitive can provide offers for. |  |  |
| TCEQ |  | The Texas Commission on Environmental Quality (TCEQ) will exercise enforcement discretion for exceedances of emission limits and operational limits for Resources that exceed air permit limits in order to maximize generation for the duration of the EEA event. A Market Notice will be sent to Market Participants and a Hotline call made |  |  |
| Media Appeal |  | When an ERCOT-wide appeal through the public news media for voluntary energy conservation is made, make posting: ## Typical ERCOT Website posting for media appeal: ERCOT has issued an appeal through the public news media for voluntary energy conservation for [Day, Date, HE XX:XX through XX:XX]. |  |  |
| ESR |  | Instruct ESRs to suspend charging. For ESRs, ERCOT shall issue the suspension instruction via a SCED Base Point instruction, or, if otherwise necessary, via a manual Dispatch Instruction. An ESR shall suspend charging unless it is providing Primary Frequency Response, has received a charging instruction via SCED Base Point, or is carrying Reg-Down and has received a charging instruction from LFC. However, an ESR co-located behind a POI with onsite generation that is incapable of exporting additional power to the ERCOT System may continue to charge as long as maximum output to the ERCOT System is maintained. |  |  |
| ### Implement EEA Level 1 |  |  |  |  |
| 1 |  | IF: - PRC < 2500 MW; THEN: - Deploy all available Non-Spin (if not previously deployed) (see Desktop Guide Resource Desk Section 2.1.1). - Determine whether system conditions require the deployment of ERS-30 (if not already deployed) (see Desktop Guide Resource Desk Section 2.3.2). - Make EEA 1 posting to the ERCOT Website - Use preformatted notice “EEA Level 1” |  |  |
| 3 |  | Verify all measures have been implemented. |  |  |
| Log |  | Log all actions. |  |  |
| ### Implement EEA Level 2 |  |  |  |  |
| Note |  | - ERCOT may immediately implement EEA Level 2 when the clock-minute average system frequency falls below 59.91 Hz for 15 consecutive minutes. - ERCOT will declare an EEA Level 2 when PRC falls below 2,000 MW and is not projected to be recovered above 2,000 MW within 30 minutes without the use of the following actions that are prescribed for EEA Level 2: - ERCOT may immediately implement EEA Level 3 any time the clock-minute average system frequency falls below 59.91 Hz for 20 consecutive minutes or when steady-state frequency falls below 59.8 Hz for any duration of time. ERCOT shall immediately implement EEA Level 3 any time the steady-state frequency is below 59.5 Hz for any duration. |  |  |
| 1 |  | IF: - PRC < 2000 MW or unable to maintain system frequency at 59.91 Hz and is not projected to be recovered above 2000 MW within 30 minutes without the use of EEA Level 2; THEN: - Determine when system conditions require the deployment of ERS-30 / ERS-10 (if not already deployed)/ Load Resources - (Do Not forget the WS ERS if available): - Deploy ERS-30 if not already done in EEA1 - Deploy ERS-10 - Deploy Load Resources Group 0/Group 0+1a+1b+1c/Group 0+1a+1b+1c+2/Group 0+1a+1b+1c+2+3/All. - Notify the Real-Time Operator when XML message has been completed. ERS / Load Resources/ must be deployed first before hotline call is made, - Desktop Guide Resource Desk (Section 2.2.1 for Load Resources; Section 2.3.2 for ERS). - Make EEA 2 posting to the ERCOT Website - Use preformatted notice “EEA Level 2” |  |  |
| ERS Time Period Changes |  | IF: - ERS Resources are deployed, and the Time Period is changing and if ERS is still needed; THEN: - Deploy next Time Period - Take into consideration the time requirement for the ERS-10 and ERS-30 - Notify the Real-Time Operator when XML message has been completed. ERS must be deployed before hotline call is made. |  |  |
| 2 |  | IF: Went straight to EEA Level 2; THEN: - Ensure tasks in EEA Level 1 are complete. |  |  |
| 3 |  | Verify all measures have been implemented. |  |  |
| Log |  | Log all actions. |  |  |
| ### Implement EEA Level 3 |  |  |  |  |
| Note |  | ERCOT may declare an EEA Level 3 when the clock-minute average system frequency falls below 59.91 Hz for 20 consecutive minutes or when steady-state frequency falls below 59.8 Hz. ERCOT will declare an EEA Level 3 when PRC cannot be maintained above 1,500 MW or when the clock-minute average system frequency falls below 59.91 Hz for 25 consecutive minutes. Upon declaration of an EEA Level 3, ERCOT shall take any of the following measures as necessary to recover frequency or PRC to the minimum required levels: |  |  |
| EEA3 Unable to Maintain 59.91 Hz or PRC <1500 MW |  | IF: - PRC <1,500 MW and is not projected to be recovered above 1,500 MW within 30 minutes or unable to maintain system frequency at 59.91 Hz for 25 consecutive minutes; THEN: - Make EEA 3 posting to the ERCOT Website - Use preformatted notice “EEA Level 3” |  |  |
| 1 |  | Verify all measures have been implemented. |  |  |
| Log |  | Log all actions. |  |  |

## 7.3	Restore EEA Levels

Procedure Purpose:  To restore the ERCOT grid to normal state as system conditions warrant while recovering from an EEA event.

| Protocol Reference | 6.5.9.4.3 |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.5.3.5 |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 23 | Effective Date: November 1, 2023 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | XML messages and Hotline calls are required for all recalls of Load Resources and ERS Resources |
| RESERVES | 1500 MW of PRC must be restored within 90 minutes. |
| ### Restore Firm Load |  |
| 1 | IF: - Sufficient Regulation Service exist to control to 60 Hz, AND - PRC – Regulation Up Responsibility ≥ 1500 MW for the last 15 minutes; THEN: - Transmission Operator will restore firm load. |
| ### Move from EEA Level 3 to EEA Level 2 |  |
| 1 | IF: - Sufficient Regulation Service exist to control to 60 Hz, AND - PRC is ≥ 2000 MW, AND - All firm loads have been instructed to be restored; THEN: - When instructed by the Real-Time Operator to recall Load Resources - Send XML message to recall Load Resources, (see Desktop Guide Resource Desk Section 2.2.4) - Make EEA 3 to EEA 2 posting to the ERCOT Website - Use preformatted notice |
| ### Move from EEA Level 2 to EEA Level 1 |  |
| 1 | IF: - The system can maintain PRC ≥ 2500 MW, AND - All Load Resources have been instructed to be restored; - THEN: - Make EEA 2 to EEA 1 posting to the ERCOT Website - Use preformatted notice |
| ### Move from EEA Level 1 to EEA 0 |  |
| 1 | IF: - The system can maintain PRC ≥ 2300 MW, AND - All RUC committed units secured in EEA 1 can be released, AND - Emergency energy from the DC Ties is no longer needed; THEN: - Terminate EEA 1 by posting to the ERCOT Website - Use preformatted notice “Return to Normal” |
| ### Cancel Watch |  |
| 1 | WHEN: - Projected Ramp Available in 30min > 1000, AND - PRC is > 3000 MW; THEN: - Cancel Watch - Cancel message for Watch on the ERCOT Website |
| Log | Log all actions. |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Frosch, Hartmann, Stone, and Barcalow | Preparers | November 10, 2010 |
| Frosch and Hartmann | Procedure writers and editors | November 29, 2010 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2010 |
| Frosch and Hartmann | Procedure writers and editors | January 26, 2011 |
| Frosch and Hartmann | Procedure writers and editors | March 23, 2011 |
| Frosch and Hartmann | Procedure writers and editors | April 20, 2011 |
| Frosch and Hartmann | Procedure writers and editors | May 10, 2011 |
| Frosch and Hartmann | Procedure writers and editors | June 6, 2011 |
| Frosch and Hartmann | Procedure writers and editors | July 18, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 30, 2011 |
| Frosch and Hartmann | Procedure writers and editors | September 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | October 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 16, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | April 25, 2012 |
| Frosch and Hartmann | Procedure writers and editors | May 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | May 30, 2012 |
| Barcalow, Frosch, and Hartmann | Procedure writers and editors | July 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | August 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | October 26, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 26, 2013 |
| Frosch and Hartmann | Procedure writers and editors | May 28, 2013 |
| Frosch and Hartmann | Procedure writers and editors | July 8, 2013 |
| Cheng, Frosch, and Hartmann | Procedure writers and editors | August 7, 2013 |
| Frosch and Hartmann | Procedure writers and editors | September 25, 2013 |
| Frosch and Hartmann | Procedure writers and editors | December 11, 2013 |
| Frosch, Gaddy, and Hartmann | Procedure writers and editors | April 1, 2014 |
| Frosch, Gaddy, and Hartmann | Procedure writers and editors | May 27, 2014 |
| Frosch and Hartmann | Procedure writers and editors | July 29, 2014 |
| Frosch and Hartmann | Procedure writers and editors | September 29, 2014 |
| Frosch and Hartmann | Procedure writers and editors | December 10, 2014 |
| Frosch and Thompson | Procedure writers and editors | December 19, 2014 |
| Frosch and Hartmann | Procedure writers and editors | February 25, 2015 |
| Frosch and Hartmann | Procedure writers and editors | April 29, 2015 |
| Frosch and Hartmann | Procedure writers and editors | July 13, 2015 |
| Hartmann and Gaddy | Procedure writers and editors | September 4, 2015 |
| Hartmann and Gaddy | Procedure writers and editors | September 25, 2015 |
| Frosch, Gaddy, and Hartmann | Procedure writers and editors | October 27, 2015 |
| Hartmann and Gaddy | Procedure writers and editors | December 22, 2015 |
| Hartmann, Gaddy, and Frosch | Procedure writers and editors | January 22, 2016 |
| Hartmann and Gaddy | Procedure writers and editors | February 23, 2016 |
| Hartmann and Gaddy | Procedure writers and editors | April 22, 2016 |
| Hartmann, Gaddy, and Frosch | Procedure writers and editors | June 24, 2016 |
| Hartmann and Gaddy | Procedure writers and editors | December 23, 2016 |
| Hartmann, Gaddy, and Frosch | Procedure writers and editors | March 27, 2017 |
| Hartmann, Gaddy, and Ballew | Procedure writers and editors | May 26, 2017 |
| Hartmann, Gaddy, and Ballew | Procedure writers and editors | June 23, 2017 |
| Hartmann, Gaddy, and Ballew | Procedure writers and editors | July 24, 2017 |
| Hartmann, Gaddy, and Ballew | Procedure writers and editors | October 27, 2017 |
| Hartmann, Gaddy, and Ballew | Procedure writers and editors | December 22, 2017 |
| Hartmann, Gaddy, Ballew, and Frosch | Procedure writers and editors | February 22, 2018 |
| Hartmann, Gaddy, Ballew, and Frosch | Procedure writers and editors | April 27, 2018 |
| Hartmann, Gaddy, and Ballew | Procedure writers and editors | August 24, 2018 |
| Hartmann, Gaddy, and Ballew | Procedure writers and editors | December 21, 2018 |
| Hartmann, Gaddy, and Cyphers | Procedure writers and editors | October 29, 2019 |
| Hartmann, Gaddy, and Cyphers | Procedure writers and editors | December 20, 2019 |
| Hartmann, Gaddy, and Cyphers | Procedure writers and editors | January 27, 2020 |
| Hartmann, Gaddy, and Cyphers | Procedure writers and editors | February 24, 2020 |
| Hartmann, Gaddy, and Cyphers | Procedure writers and editors | June 25, 2020 |
| Hartmann, Gaddy, Cyphers, and Sheets | Procedure writers and editors | December 23, 2020 |
| Hartmann, Gaddy, Cyphers, and Sheets | Procedure writers and editors | April 29, 2021 |
| Hartmann, Gaddy, Cyphers, and Sheets | Procedure writers and editors | June 11, 2021 |
| Hartmann, Gaddy, Cyphers, and Sheets | Procedure writers and editors | July 8, 2021 |
| Hartmann, Gaddy, Cyphers, and Sheets | Procedure writers and editors | July 28, 2021 |
| Hartmann, Gaddy, Cyphers, and Sheets | Procedure writers and editors | August 27, 2021 |
| Hartmann, Gaddy, and Cyphers | Procedure writers and editors | November 29, 2021 |
| Hartmann, Gaddy, Cyphers and Frosch | Procedure writers and editors | December 17, 2021 |
| Hartmann, Gaddy, Cyphers and Frosch | Procedure writers and editors | February 24, 2022 |
| Hartmann, Gaddy, and Cyphers | Procedure writers and editors | May 20, 2022 |
| Hartmann, Gaddy, and Cyphers | Procedure writers and editors | June 27, 2022 |
| Hartmann, Gaddy, Cyphers, and Frosch | Procedure writers and editors | July 25, 2022 |
| Hartmann, Gaddy, and Cyphers | Procedure writers and editors | October 3, 2022 |
| Hartmann, Gaddy, and Cyphers | Procedure writers and editors | October 26, 2022 |
| Hartmann, Gaddy, Cyphers, and Frosch | Procedure writers and editors | December 22, 2022 |
| Hartmann, Gaddy, Cyphers, and Luker | Procedure writers and editors | April 25, 2023 |
| Hartmann, Gaddy, Cyphers, and Luker | Procedure writers and editors | June 5, 2023 |
| Hartmann, Gaddy, Cyphers, and Luker | Procedure writers and editors | June 26, 2023 |
| Hartmann, Gaddy, Cyphers, and Luker | Procedure writers and editors | August 29, 2023 |
| Hartmann, Cyphers, and Luker | Procedure writers and editors | October 26, 2023 |

Manual Change History

| Procedure | Ver/Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All Sections | 1.0 / 0 | New procedures for all sections for Nodal implementation | November 28, 2010 |
| 3.1 3.4 3.5 3.7 4.1 5.1 5.1 5.2 6.1 7.2 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Deleted WGR section, in section “Monitor QSE Ancillary Services Obligation”, updated step Infeasible A/S Capacity from RUC & A/S Difference in COP Updated Note Updated step 3 Updated whole procedure Updated step 2 In section “Procurement of Ancillary Services due to DAM Failure”, “ERCOT Increases the Amount of Ancillary Services”, “Replacement of Ancillary Service Due to Infeasibility/Failure to Provide”, “Replacement of Ancillary Services in Real Time”, Updated step 1 Updated whole procedure In section “Timeline Deviations”, Updated 2nd Note In section “Returning from Planned Outage Early”, Updated Deny In section “Implement EEA Level 1”, Updated step 1 | December 1, 2010 |
| 3.1 3.7 3.8 5.1 | 1.0 / 2 1.0 / 2 1.0 / 0 1.0 / 2 | Deleted “Monitor Base Point Deviations” and updated “A/S Difference in COP” Deleted step Note, Deployment, & Termination New Procedure Updated “Procurement of Ancillary Services due to DAM Failure”, “ERCOT Increases the Amount of Ancillary Services” and “Replacement of Ancillary Service Due to Infeasibility/Failure to Provide“ step 3 and 4 | December 15, 2010 |
| 3.1 3.2 3.4 3.3 3.5 3.7 4.1 5.1 5.2 7.1 7.2 7.3 8.2 | 1.0 / 3 1.0 / 1 1.0 / 2 1.0 / 1 1.0/ 2 1.0 / 3 1.0 / 2 1.0 / 3 1.0 / 2 - / 1 - / 2 1.0 / 1 1.0 / 1 | Updated step Telemetered Status, step 1 in Manual Override Checks and removed workaround step “Real Time A/S shortage” in Monitor QSE Ancillary Services Obligation Updated all steps Updated steps “Deployment” and “Termination” Updated step 1 on “Cancelation” Updated all steps and added note Updated all steps Updated and deleted Notes and step 1 Updated “Procurement of Ancillary Services due to DAM Failure”, “ERCOT Increases the Amount of Ancillary Services”, “Replacement of Ancillary Service Due to Infeasibility/Failure to Provide“ step 3 and added note on Replacement of Ancillary Services in Real Time Updated Second Note on “Timeline Deviations” Updated Hotline on “Scripts” Updated Step 1 on ” Implement EEA Level 1” and “Implement EEA Level 2A” Updated Steps 1 on “Move from EEA Level 3 to EEA Level 2B” and “Cancel Watch” Deleted Site Failover Notification procedure & changed 8.3 to 8.2 | January 31, 2011 |
| 3.3 3.4 3.7 5.1 7.1 | 1.0 / 2 1.0 / 3 1.0 / 4 1.0 / 4 1.0 / 2 | Updated step 1 in “Watch” & step 1 in “Cancelation” Updated “Deployment” and “Termination” Updated “Issue Watch & Deploy Non-Spin” and “Recall Non-Spin” Updated step 2 in “Replacement of Ancillary Service Due to Infeasibility/Failure to Provide” Updated “Watch” and “Emergency Notice” | March 25, 2011 |
| 3.5 7.1 7.3 | 1.0 / 3 1.0 / 3 1.0 / 2 | Updated NERC Recovery Criteria Updated step 1 in Watch and Emergency Notice and step Post Updated 1st and 2nd script in Restore Firm Load, Updated 1st in Move From EEA Level 3 to EEA Level 2B | April 22, 2011 |
| 3.8 3.9 5.1 8.1 | 1.0 / 0 1.0 / 1 1.0 / 5 1.0 / 1 | Added new procedure Changed section number from 3.8 to 3.9 Updated steps 3-5 in Replacement of A/S due to Infeasibility/Failure to Provide, deleted Replacement of A/S in Real-Time Change section name, updated step 2 & 3 | May 11, 2011 |
| 3.3 3.4 3.6 3.7 3.8 7.1 | 1.0 / 3 1.0 / 4 1.0 / 1 1.0 / 5 1.0 / 1 1.0 / 4 | Updated step 1 in Advisory and Watch Updated step Deployment Updated step 1 Updated step Deploy Non-Spin & Post & Deploy Load Resources & Post Updated step Post Updated all steps | June 8, 2011 |
| 3.3 3.4 3.5 3.8 4.1 5.2 7.1 7.2 7.3 9.1 | 1.0 / 4 1.0 / 5 1.0 / 4 1.0 / 2 1.0 / 3 1.0 / 3 1.0 / 5 1.0 / 3 1.0 / 3 1.0 / 1 | Updated step 1 in Advisory and Watch Updated step on Deployment Updated step on PRC Below 2300 Added step Termination, updated steps on Post and Cancel Posting Updated step 2 in Approve/Reject Decommitment QSE Requests in Operating Period Updated step 1 and deleted 2nd note in Timeline Deviations Updated step Watch Updated all steps Updated all steps Added Market Participant Backup Control Center Transfer procedure | July 20, 2011 |
| 3.3 3.4 5.1 7.1 7.2 7.3 8.2 | 1.0 / 5 1.0 / 6 1.0 / 6 1.0 / 6 1.0 / 4 1.0 / 4 1.0 / 2 | Updated step 1 in Cancelation Updated Note, added steps Additional Deployment & Commit, updated steps Note & Deployment Updated 1st Note Added projected reserve capacity shortage and Extreme Hot Weather in Watch Updated 2nd Note, step 1 & 2 in EEA Level 1, step 1 in EEA Level 2A, added note in EEA Level 2B Updated step 1 in Cancel Watch Updated 4th Note and step 1 | September 1, 2011 |
| 7.2 7.3 8.1 | 1.0 / 5 1.0 / 5 1.0 / 2 | Combined EEA 2A & B per NPRR 379 Combined EEA 2A & B per NPRR 379 Updated step 2 | October 1, 2011 |
| 3.1 3.4 3.6 3.8 3.9 4.1 5.1 8.1 | 1.0 / 4 1.0 / 7 1.0 / 2 1.0 / 3 1.0 / 2 1.0 / 4 1.0 / 7 1.0 / 3 | Changed desktop guide reference in Monitor QSE Ancillary Services Obligation Updated step Commit Updated procedure title and all steps Updated steps 1 & Termination, added step 2 Deleted procedure due to protocol change Added 2nd Note Updated steps 1 – 3 in Procurement of A/S due to DAM Failure, steps 1 -2 in ERCOT Increased the Amount of A/S, steps 1 & 4 in Replacement of A/S Due to Infeasibility/Failure to Provide Added Note 2 & 3 | November 1, 2011 |
| 3.3 3.4 3.7 3.8 7.1 | 1.0 / 6 1.0 / 8 1.0 / 6 1.0 / 4 1.0 / 7 | Add Note in Watch Added second Note Added second Note Added Note Updated Post in “Scripts” All procedures in this manual have been reviewed. | December 15, 2011 |
| 1.2 3.1 3.4 4.1 5.1 | 1.0 / 1 1.0 / 5 1.0 / 9 1.0 / 5 1.0 / 8 | Updated Scope Updated Monitor QSE A/S Obligation procedure Updated 1st Note Updated steps 1 & 2 Updated step 2, 3 & 4 | January 19, 2012 |
| 2.1 3.1 3.3 3.4 3.5 3.7 3.8 4.1 5.1 7.1 7.2 7.3 8.2 9.1 | 1.0 / 1 1.0 / 6 1.0 / 7 1.0 / 10 1.0 / 5 1.0 / 7 1.0 / 5 1.0 / 6 1.0 / 9 1.0 / 8 1.0 / 6 1.0 / 6 1.0 / 3 1.0 / 2 | Updated paragraph 4 Updated Desktop Guide references Updated Desktop Guide references Updated Desktop Guide references Updated Desktop Guide references Updated Desktop Guide references Updated Desktop Guide references Updated 1st Note & step 1 Updated Desktop Guide references, step 3s & 4 Updated step 1 of Watch Updated Desktop Guide references Updated Desktop Guide references Updated Desktop Guide references Updated QSE Override, QSE unable to Override, Backup/Alternate Control Center Transfer, QSE Issues & step Power System Stabilizers (PSS) & Automatic Voltage Regulators (AVR) | March 1, 2012 |
| 2.1 3.1 3.5 3.6 3.7 4.1 5.1 7.1 9.1 | 1.0 / 2 1.0 / 7 1.0 / 6 1.0 / 3 1.0 / 6 1.0 / 7 1.0 / 10 1.0 / 9 1.0 / 3 | Changed TSP/DP to TO Updated step Not Dispatchable to SCED Deleted Potential DCS Event, changed section number for System Failures Changed section number Changed section number & added step 3 Updated step 1 Updated information needed in e-mail Updated all step 1’s Changed Shift Engineer to Ops Support Engineer | May 1, 2012 |
| 3.3 3.4 | 1.0 / 8 1.0 / 11 | Updated to reflect changes in the TAC approved Non-Spin document Updated to reflect changes in the TAC approved Non-Spin document | May 14, 2012 |
| 7.2 7.3 | 1.0 / 7 1.0 / 7 | Updated EILS to ERS per NPRR 451 Updated EILS to ERS per NPRR 451 | June 1, 2012 |
| 1.3 4.1 6.1 7.1 7.2 7.3 8.2 | 1.0 / 1 1.0 / 8 1.0 / 2 1.0 / 10 1.0 / 8 1.0 / 8 1.0 / 4 | Removed ERCOT Shift Supervisor paragraph Added Desktop Guide to VDI reference Added Desktop Guide to VDI reference and updated Maintenance Level 2 and 3 outages Updated all step 1’s Added Desktop Guide to VDI reference, updated step 1 Implement EEA Level 2 and added ERS Updated step 1 Move from EEA Level 3 to EEA Level 2 Updated 4th note | July 16, 2012 |
| 3.1 7.2 | 1.0 / 8 1.0 / 9 | Updated step ONTEST Updated step 1 of Implement EEA Level 1 | August 29, 2012 |
| 2.2 7.2 8.1 | 1.0 / 1 1.0 / 10 1.0 / 4 | Added Hotline Call Communication Updated Implement EEA Level 1 step 2, Implement EEA Level 2 step 1 and ERS Business Hour Changes Updated 1st Note, step 1, 2 & 3. Added step 4 and Log All procedures in this manual have been reviewed. | November 1, 2012 |
| 3.3 3.4 3.6 3.7 4.1 5.1 7.3 | 1.0 / 9 1.0 /12 1.0 / 9 1.0 / 7 1.0 / 8 1.0 / 11 1.0 / 9 | Non-Spin deployment messages are now automated Non-Spin deployment messages are now automated Non-Spin deployment messages are now automated Non-Spin deployment messages are now automated Updated steps 1 & 2 Updated steps Note, Procurement Timeline & 1. Added new procedure, Daily Reconfiguration SASM Updated step 1 of Cancel Watch | March 1, 2013 |
| 3.3 3.5 5.1 5.2 7.1 7.2 7.3 8.1 9.1 | 1.0 / 10 1.0 / 4 1.0 / 12 1.0 / 4 1.0 / 11 1.0 / 11 1.0 / 10 1.0 / 5 1.0 / 4 | Removed notice builder reference Removed notice builder reference Updated steps 1 & 5 in ERCOT Increased the amount of A/S & steps in Daily Reconfiguration SASM Updated step 1 Updated Scripts Removed notice builder reference & Updated Scripts Removed notice builder reference Updated Script Updated Script | June 1, 2013 |
| 3.1 7.1 | 1.0 / 9 1.0 / 12 | Deleted 1st Note, added step Log, moved Not Dispatchable to SCED, Control Block Up/Down, & Real-Time RRS A/S Shortages to Real-Time procedure, deleted Manual Override Checks Updated step 1 in Watch & Emergency Notice | July 15, 2013 |
| 5.1 5.2 | 1.0 / 13 1.0 / 5 | Updated 1st Note for R4 changes, Daily SASM Timeline Updated 1st Note for R4 changes | August 9, 2013 |
| 5.1 6.1 | 1.0 / 14 1.0 / 3 | Updated 1st Note, Daily SASM Timeline Updated to reflect SCR770 changes | September 27, 2013 |
| 3.1 3.2 3.3 3.5 3.6 3.7 4.1 5.1 6.1 6.2 7.1 7.2 7.4 8.2 9.1 | 1.0 / 10 1.0 / 2 1.0 / 11 1.0 / 5 1.0 / 10 1.0 / 8 1.0 / 10 1.0 / 15 1.0 / 4 1.0 / 1 1.0 / 13 1.0 / 12 1.0 / 1 1.0 / 5 1.0 / 5 | Added Monitor QSE A/S Obligation Title Updated Evaluate Request Updated step Log Updated step Log Updated step Log Updated step Log Updated step 3 Updated step Log Updated Accept Maintenance Outage, Coordinate Maintenance Outage, Coordinate Maintenance Level 2 and 3 and Log Updated step Log Updated step Log Updated last step and added Log Updated step Log Updated step Log Updated and added step Log All procedures in this manual have been reviewed. | December 13, 2013 |
| 3.4 3.5 3.74.1 6.1 7.1 7.2 7.3 8.1 | 1.0 / 13 1.0 / 7 1.0 / 9 1.0 / 11 1.0 / 5 1.0 / 14 1.0 / 13 1.0 / 11 1.0 / 6 | Updated VDI information Updated for NPRR542 Updated VDI information Updated VDI information Updated VDI information Updated to incorporate NPRR542 Updated ERS, Media appeal, TCEQ, VDI language, and moved steps to RUC desk Updated Reserves and step 1 Updated step 1 & 3, added step 5 | April 4, 2014 |
| 2.2 3.1 3.3 3.4 4.1 5.1 5.2 7.1 | 1.0 / 2 1.0 / 11 1.0 / 12 1.0 / 14 1.0 / 12 1.0 / 16 1.0 / 6 1.0 / 15 | Added VDIs to Master QSEs Updated Monitor QSE AS Obligations steps Updated steps in Watch Updated title, step Deployment & Termination Updated step 1 & 2 Updated section titles & steps Updated Timeline Deviations Added Note, updated Advisory & Watch | June 1, 2014 |
| 3.1 3.4 3.6 3.7 4.1 5.1 6.1 7.2 7.3 | 1.0 / 12 1.0 / 15 1.0 / 11 1.0 / 10 1.0 / 13 1.0 / 17 1.0 / 6 1.0 / 14 1.0 / 12 | Updated Desktop references Updated Desktop references Updated Desktop references Updated Desktop references Updated Desktop reference Updated steps 1, 4-6 in Replacement of A/S due to infeasibility or failure to provide, & Desktop references Updated Forced Derate Updated Desktop references Updated Desktop references | August 1, 2014 |
| 7.1 | 1.0 / 16 | Updated Scripts | October 1, 2014 |
| 3.4 3.6 4.1 6.2 | 1.0 / 16 1.0 / 12 1.0 / 14 1.0 / 2 | Deleted Note & added Log Changed title & added Rio Grande Valley Re-worded procedure Added step 2 All procedures in this manual have been reviewed | December 15, 2014 |
| 5.1 | 1.0 / 18 | Added new procedure “Increasing A/S for Extreme Cold Weather and changed title for “Increasing A/S for other reasons and updated timeline | December 22, 2014 |
| 2.2 3.3 3.4 3.5 3.6 3.7 5.1 5.2 6.1 | 1.0 / 3 1.0 / 13 1.0 / 8 1.0 / 13 1.0 / 11 1.0 / 0 1.0 / 19 1.0 / 7 1.0 / 7 | Added Dispatch and VDI definitions Combined section 3.3 & 3.4 into one procedure Updated section number Updated section number Updated section number and Corrected VDI vs. Dispatch Instruction New, moved procedure from Shift Supervisor desk Added SASM Failure and reformatted Deleted procedure Corrected VDI vs. Dispatch Instruction | March 1, 2015 |
| 3.2 3.3 3.5 3.6 5.1 7.1 8.1 9.1 | 1.0 / 3 1.0 / 14 1.0 / 14 1.0 / 12 1.0 / 20 1.0 / 17 1.0 / 7 1.0 / 6 | Updated step Evaluate Request Combined step in Watch Updated GTL to GTC Updated step 2 Moved scripts to script procedure Moved scripts to script procedure Combined Note steps & moved scripts to script procedure Moved script to script procedure | May 1, 2015 |
| 5.1 | 1.0 / 21 | Added a “Q” for QSE scripts Updated per NPRR 682 | July 15, 2015 |
| 5.1 | 1.0 / 22 | Updated per NPRR 701 | September 9, 2015 |
| 5.1 | 1.0 / 23 | Updated Reconfiguration Supplemental Ancillary Service Market (RSASM) | October 1, 2015 |
| 3.5 | 1.0 / 15 | Updated to include calls for deployment and recalls of Load Resources. | October 30, 2015 |
| 3.3 3.4 3.7 5.1 7.1 7.2 7.3 8.1 9.1 | 1.0 / 15 1.0 / 9 1.0 / 1 1.0 / 24 1.0 / 18 1.0 / 15 1.0 / 13 1.0 / 8 1.0 / 7 | Updated Advisory step Issue Advisory Typical MIS Posting Updated Watch step Issue Watch & Deploy Off-Line Non-Spin Typical MIS Posting Updated Watch step Recall Non-Spin Typical MIS Posting Updated step 1 Typical MIS Posting Updated Unannounced Resource Testing step Testing Rules and Scripts Typical Script Updated Increasing Ancillary Services for Extreme Cold Weather step 1 & 2 Typical Scripts Updated Increasing Ancillary Services for other reasons step 1 & 2 Typical Scripts Updated Daily RSASM step 1 & 2 Typical MIS Postings Updated Operating Condition Script step Hotline Q#46 Updated Operating Condition Script step Hotline Cancellation Q#47 First Note, Updated Implement EEA Level 2 step 1, and Implement NPRR708 for EEA Updated Move from EEA Level 2 to EEA Level 1 step 1 Updated step 2 Q#75 Updated Courtesy Hotline Calls for ERCOT Application Issues step 1 Q#76 All procedures in this manual have been reviewed | December 31, 2015 |
| 2.1 3.6 5.1 7.2 8.1 | 1.0 / 3 1.0 / 13 1.0 / 25 1.0 / 6 1.0 / 9 | Updated System Operator Responsibilities and Authority Updated NERC Standard Reference Updated step WS-ERS Updated Replacement of Ancillary Service Due to Infeasibility or Failure to Provide step 1 with Hotline call Changed Business Hours to Time Periods Updated Alert Levels | February 1, 2016 February 10, 2016 |
| 1.3 5.1 | 1.0 / 2 1.0/ 26 | Removed Interchange Coordinator Updated Failure to Provide script title Q#72 | March 1, 2016 |
| 5.1 | 1.0 / 27 | Added Increasing Ancillary Services for Extreme Cold Weather step 1 MIS Posting Typical Script Added Increasing Ancillary Services for other reasons step 1 MIS Posting Typical Script | April 29, 2016 |
| 2.1 2.2 3.7 6.1 7.1 | 1.0 / 4 1.0 / 4 1.0 / 2 1.0 / 8 1.0 / 19 | Updated for COM-002-4 Updated for COM-002-4 Updated for COM-002-4 Updated for COM-002-4 Updated for COM-002-4 | June 30, 2016 |
| 9.1 | 1.0 / 8 | Added Real-Time Data Issues known by the QSE Deleted Telemetry Issues that could affect SCED and/or LMPs All procedures in this manual have been reviewed | December 30, 2016 |
| 1.3 2.1 7.1 7.2 | 1.0 / 3 1.0 / 5 1.0 / 20 1.0 / 17 | Deleted Roles/Responsibilities section Updated section Updated title and all 1st steps Added Implement EEA Level 3 step PRC < 1375 MW | March 31, 2017 |
| 5.1 7.2 | 1.0 / 28 1.0 / 18 | Updated Increasing Ancillary Services for Extreme Cold Weather step 1 Updated Implement EEA Level 3 step PRC <1375 | June 1, 2017 |
| 7.2 | 1.0 / 19 | Updated 1st Note and Implement EEA Level 3 steps | June 30, 2017 |
| 3.7 7.2 | 1.0 / 3 1.0 / 20 | Updated note Added note Implement EEA Level 2 and Level 3 | July 28, 2017 |
| 5.1 | 1.0 / 29 | Updated Replacement of Ancillary Service Due to Infeasibility or Failure to Provide steps | October 31, 2017 |
| 8.2 | 1.0 / 6 | All procedures in this manual have been reviewed Updated Primary Control Center 4th note | December 28, 2017 |
| 3.4 3.7 3.8 | 1.0/ 10 1.0 / 0 1.0 / 3 | Updated Procedure Purpose, added SCED/RLC/LFC (AGC) Failures heading and ICCP, MIS, and Outage Scheduler outages section Added new procedure Deploying Non-Spin for Critical Inertia Level for 3.7 Updated Unannounced Resource Testing procedure 3.7 to 3.8 | February 28, 2018 |
| 2.2 | 1.0 / 5 | Updated procedure purpose | May 1, 2018 |
| 3.8 | 1.0 / 4 | Added Notify and Log step Moved Unannounced Testing scripts to Scripts | August 31, 2018 |
| 7.3 | 1.0 / 14 | Added Log All procedures in this manual have been reviewed | December 28, 2018 |
| 7.3 8.1 | 1.0 / 15 1.0 / 10 | Updated Move from EEA Level 1 to EEA 0 step 1 Added steps | November 1, 2019 |
| 7.2 7.3 | 1.0 / 21 1.0 / 16 | Updated MSSC Updated MSSC All procedures in this manual have been reviewed | January 1, 2020 |
| 3.3 3.6 3.7 7.3 8.2 | 1.0 / 16 1.0 / 14 1.0 / 1 1.0 / 17 1.0 / 7 | Clarified RUC-commits/decommits Clarified RUC-commits/decommits Clarified RUC-commits/decommits Clarified RUC-commits/decommits Updated Primary Control Center steps 1 & 3 | January 31, 2020 |
| 8.2 | 1.0 / 8 | Updated Title and removed Alternate Control Center | February 28, 2020 |
| 2.1 6.1 7.1 | 1.0 / 6 1.0 / 9 1.0 / 21 | Added Advance Action Notice per NPRR930 Added Advance Action Notice section per NPRR930 Added Advance Action Notice section per NPRR930 | July 1, 2020 |
| 1.1 3.3 3.4 3.7 3.8 5.1 6.1 7.1 7.2 7.3 9.1 | 1.0 / 1 1.0 / 17 1.0 / 11 1.0 / 2 1.0 / 5 1.0 / 30 1.0 / 10 1.0 / 22 1.0 / 22 1.0 / 18 1.0 / 9 | Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 All procedures in this manual have been reviewed | December 31, 2020 |
| 1.1 3.4 | 1.0 / 2 1.0 / 12 | Changed Notice Builder to Grid Conditions Communication (GCC) Notices Changed Notice Builder to Grid Conditions Communications (GCC) Notices | May 6, 2021 |
| 7.2 7.3 | 1.0 / 23 1.0 / 19 | Added Note Added Note | June 16 2021 |
| 3.3 3.8 3.9 7.1 7.3 | 1.0 / 18 1.0 / 0 1.0 / 5 1.0 / 23 1.0 / 20 | Updated for OBDRR031 Added new 3.8 for OBDRR031 Moved Unannounced Resource Testing from 3.8 to 3.9 Updated for OBDRR031 Updated for OBDRR031 | July 12, 2021 |
| 3.8 7.3 | 1.0 / 1 1.0 / 21 | Updated section title and section Updated Cancel Watch | July 31, 2021 |
| 7.2 | 1.0 / 24 | Updated 1st Note | September 1, 2021 |
| 3.3 3.8 6.1 7.2 | 1.0 / 19 1.0 / 1 1.0 / 11 1.0 / 25 | Updated for NPRR1106 Moved to section 3.3 Updated Advance Action Notice (AAN) Updated for NPRR1106 | December 1, 2021 |
| 2.2 3.3 7.1 7.3 8.1 | - / 6 1.0 / 20 - / 24 1.0 / 22 - / 11 | Updated step 1 Updated Watch Updated all steps Updated Move from EEA Level 2 to EEA Level 1 Updated step 2 All procedures in this manual have been reviewed | December 31, 2021 |
| 2.3 | 1.0 / 0 | New procedure section | March 1, 2022 |
| 3.3 3.5 3.7 3.8 7.2 | 1.0 / 21 1.0 / 16 1.0 / 3 1.0 / 0 1.0 / 26 | Updated for NPRR1093 Updated for NPRR1093 Updated for NPRR1093 New section for NPRR939 & NOGRR191 Updated for NPRR939, NPRR1093 & NOGRR191 | May 26, 2022 |
| 3.3 3.7 | 1.0 / 22 1.0 / 4 | Updated PRC < 3200 & Projected Ramp Available in 30min Updated Deploy Off-Line Non-Spin | July 1, 2022 |
| 3.3 | 1.0 / 23 | Updated PRC < 3200 MW and Advisory | July 29, 2022 |
| 3.1 3.9 3.10 7.2 | 1.0 / 13 1.0 / 0 1.0 / 5 1.0 / 27 | Updated reference displays Added new Deploying FFR Created 3.10 and moved old 3.9 to 3.10 Added ESR | October 7, 2022 |
| 3.9 | 1.0 / 1 | Updated steps | November 2, 2022 |
| 3.3 3.11 7.2 | 1.0 / 24 1.0 / 0 1.0 / 28 | Added Media Appeal step Added Large Load Curtailment Program step and updated steps Added Unannounced ESR Testing Updated TCEQ and added Media Appeal step All procedures in this manual have been reviewed | December 30, 2022 |
| 6.1 | 1.0 / 12 | Added email address to posting | April 28, 2023 |
| 1.1 3.8 5.1 7.2 | 1.0 / 3 1.0 / 1 1.0 / 31 1.0 / 29 | Updated for NPRR865 Updated for NPRR865 Updated for NPRR865 Updated for NPRR865 | June 9, 2023 |
| 7.2 | 1.0 / 30 | Updated For NPRR865 | June 30, 2023 |
| 6.1 6.2 | 1.0 / 13 1.0 / 3 | Updated Forced Outages and Forced Derates Updated step 1 | September 1, 2023 |
| 3.3 7.2 7.3 | 1.0 / 25 1.0 / 31 1.0 / 23 | Updated for NPRR1176 Updated for NPRR1176 Updated for NPRR1176 | November 1, 2023 |