- Power Operations Bulletin # 1114

ERCOT has posted/revised the Real Time manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

- http://www.ercot.com/mktrules/guides/procedures/index.html

## 3.4	Reportable Balancing Contingency Event

Procedure Purpose:  To meet the Contingency Event Recovery Period after a Balancing Contingency  Event.

| Protocol Reference | 6.5.7.6.2.2 (2) |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 2.2.4 (2) |  |  |  |
| NERC Standard | BAL-002-3 R1, R1.1, R1.3, R3 | TOP-001-5 R11 |  |  |

| Version: 1 | Revision: 13 | Effective Date: December 01, 2023 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Reportable Balancing Contingency Event | Any Balancing Contingency Event occurring within a one-minute interval of an initial sudden decline in ACE based on EMS scan rate data that results in a loss of 800 MW. |
| Contingency Event Recovery Period | A period that begins at the time that the resource output begins to decline within the first one-minute interval of a Reportable Balancing Contingency Event and extends for fifteen minutes thereafter. |
| Contingency Reserve Restoration Period | A period not exceeding 90 minutes following the end of the Contingency Event Recovery Period. |
| NOTE | The steps below will need to happen quickly, let phones ring, or if available, another desk will take the calls. |
| 1 | IF: - ERCOT experiences a low frequency disturbance; THEN: - Immediately check to ensure that SCED sees the units correct telemetry (HSL of zero or Resource Status of “off”), Contact the QSE(s) if telemetry needs to be changed, - If SCED does not automatically execute within 60 seconds of the event, manually execute a SCED run, - Enter a manual off-set as necessary. |
| 2 | IF: - Frequency dropped below 59.7 Hz; THEN: - Load Resources have deployed on UFR. |
| NOTE | If Load Resources are deployed, it may become necessary to periodically execute SCED manually and/or use the manual offset to control frequency. |
| BAAL or near the 10-minute recovery time | IF: - Unable to control frequency within defined limits; THEN: - Refer to Frequency Control Operating Procedure section 3.1 Response to Low Frequency procedure. |
| 3 | WHEN: - System frequency has been restored; THEN: - Make Hotline call to QSEs to recall Load Resources. Q#36 - Typical Hotline Script to Recall Load Resources After a Frequency Event |
| PRC Below 2500 | IF: - PRC < 2500 MW; THEN: - Implement EEA (see section 5.3). |
| Log | Log all actions. |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Frosch, Hartmann, Stone, and Barcalow | Prepares | November 10 , 2010 |
| Frosch and Hartmann | Procedure writers and editors | November 29, 2010 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2010 |
| Frosch, Foster, and Hartmann | Procedure writers and editors | January 3, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 26, 2011 |
| Frosch and Hartmann | Procedure writers and editors | March 23, 2011 |
| Frosch and Hartmann | Procedure writers and editors | April 20, 2011 |
| Frosch and Hartmann | Procedure writers and editors | June 6, 2011 |
| Frosch and Hartmann | Procedure writers and editors | July 18, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 1, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 30, 2011 |
| Frosch and Hartmann | Procedure writers and editors | September 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | October 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 16, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | April 25, 2012 |
| Frosch and Hartmann | Procedure writers and editors | May 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | May 30, 2012 |
| Barcalow, Frosch, and Hartmann | Procedure writers and editors | July 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | August 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | October 26, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 26, 2013 |
| Frosch and Hartmann | Procedure writers and editors | May 28, 2013 |
| Frosch and Hartmann | Procedure writers and editors | July 8, 2013 |
| Frosch and Hartmann | Procedure writers and editors | August 7, 2013 |
| Frosch and Hartmann | Procedure writers and editors | September 25, 2013 |
| Frosch and Hartmann | Procedure writers and editors | December 11, 2013 |
| Frosch and Hartmann | Procedure writers and editors | December 20, 2013 |
| Frosch, Gaddy, Hartmann, and Solis | Procedure writers and editors | April 1, 2014 |
| Frosch, Gaddy, and Hartmann | Procedure writers and editors | May 27, 2014 |
| Frosch and Hartmann | Procedure writers and editors | July 29, 2014 |
| Frosch and Hartmann | Procedure writers and editors | September 29, 2014 |
| Drummond, Frosch, and Hartmann | Procedure writers and editors | December 10, 2014 |
| Frosch and Thompson | Procedure writers and editors | December 19, 2014 |
| Frosch and Hartmann | Procedure writers and editors | February 25, 2015 |
| Frosch and Hartmann | Procedure writers and editors | March 25, 2015 |
| Frosch and Hartmann | Procedure writers and editors | April 29, 2015 |
| Frosch, Hartmann, and Gaddy | Procedure writers and editors | July 13, 2015 |
| Hartmann and Gaddy | Procedure writers and editors | December 22, 2015 |
| Hartmann, Gaddy, and Frosch | Procedure writers and editors | February 23, 2016 |
| Hartmann and Gaddy | Procedure writers and editors | April 22, 2016 |
| Hartmann, Gaddy, and Frosch | Procedure writers and editors | June 24, 2016 |
| Hartmann and Gaddy | Procedure writers and editors | July 15, 2016 |
| Hartmann, Gaddy, and Frosch | Procedure writers and editors | September 26, 2016 |
| Hartmann and Gaddy | Procedure writers and editors | October 31, 2016 |
| Hartmann, Gaddy, and Frosch | Procedure writers and editors | December 23, 2016 |
| Hartmann, Gaddy, and Frosch | Procedure writers and editors | March 24, 2017 |
| Hartmann and Gaddy | Procedure writers and editors | April 5, 2017 |
| Hartmann, Gaddy, and Ballew | Procedure writers and editors | May 26, 2017 |
| Hartmann, Gaddy, and Ballew | Procedure writers and editors | June 23, 2017 |
| Hartmann, Gaddy, and Ballew | Procedure writers and editors | July 24, 2017 |
| Hartmann, Gaddy, and Ballew | Procedure writers and editors | September 27, 2017 |
| Hartmann, Gaddy, and Ballew | Procedure writers and editors | October 27, 2017 |
| Hartmann, Gaddy, Ballew ,and Frosch | Procedure writers and editors | December 22, 2017 |
| Hartmann, Gaddy, Ballew ,and Frosch | Procedure writers and editors | February 22, 2018 |
| Hartmann, Gaddy, and Ballew | Procedure writers and editors | April 2, 2018 |
| Hartmann, Gaddy, Ballew ,and Frosch | Procedure writers and editors | April 27, 2018 |
| Hartmann, Gaddy, and Ballew | Procedure writers and editors | August 24, 2018 |
| Hartmann, Gaddy, and Ballew | Procedure writers and editors | September 27, 2018 |
| Hartmann, Gaddy, and Ballew | Procedure writers and editors | December 21, 2018 |
| Hartmann, Gaddy, and Ballew | Procedure writers and editors | January 25, 2019 |
| Hartmann, Gaddy, and Frosch | Procedure writers and editors | March 26, 2019 |
| Hartmann, Gaddy, and Pence | Procedure writers and editors | July 29, 2019 |
| Hartmann, Gaddy, and Cyphers | Procedure writers and editors | October 29, 2019 |
| Hartmann, Gaddy, and Cyphers | Procedure writers and editors | December 20, 2019 |
| Hartmann, Gaddy, and Cyphers | Procedure writers and editors | January 27, 2020 |
| Hartmann, Gaddy, and Cyphers | Procedure writers and editors | February 24, 2020 |
| Hartmann, Gaddy, and Cyphers | Procedure writers and editors | June 25, 2020 |
| Hartmann, Gaddy, Cyphers, and Sheets | Procedure writers and editors | December 23, 2020 |
| Hartmann, Gaddy, Cyphers, and Sheets | Procedure writers and editors | March 26, 2021 |
| Hartmann, Gaddy, Cyphers, and Sheets | Procedure writers and editors | April 29, 2021 |
| Hartmann, Gaddy, Cyphers, and Sheets | Procedure writers and editors | June 11, 2021 |
| Hartmann, Gaddy, Cyphers, and Sheets | Procedure writers and editors | July 8, 2021 |
| Hartmann, Gaddy, Cyphers, and Sheets | Procedure writers and editors | July 28, 2021 |
| Hartmann, Gaddy, Cyphers, and Sheets | Procedure writers and editors | August 27, 2021 |
| Hartmann, Gaddy, and Cyphers | Procedure writers and editors | November 29, 2021 |
| Hartmann, Gaddy, Cyphers, and Frosch | Procedure writers and editors | December 17, 2021 |
| Hartmann, Gaddy, and Cyphers | Procedure writers and editors | January 27, 2022 |
| Hartmann, Gaddy, Cyphers, and Frosch | Procedure writers and editors | February 24, 2022 |
| Hartmann, Gaddy, and Cyphers | Procedure writers and editors | May 20, 2022 |
| Hartmann, Gaddy, Cyphers, and Frosch | Procedure writers and editors | July 25, 2022 |
| Hartmann, Gaddy, and Cyphers | Procedure writers and editors | October 3, 2022 |
| Hartmann, Gaddy, and Cyphers | Procedure writers and editors | October 12, 2022 |
| Hartmann, Gaddy, Cyphers, and Frosch | Procedure writers and editors | December 22, 2022 |
| Hartmann, Gaddy, Cyphers, and Frosch | Procedure writers and editors | March 28, 2023 |
| Hartmann, Gaddy, Cyphers, and Luker | Procedure writers and editors | June 5, 2023 |
| Hartmann, Gaddy, Cyphers, and Luker | Procedure writers and editors | June 26, 2023 |
| Hartmann, Cyphers, and Luker | Procedure writers and editors | September 28, 2023 |
| Hartmann, Cyphers, and Luker | Procedure writers and editors | October 27, 2023 |
| Hartmann, Cyphers, and Luker | Procedure writers and editors | November 2, 2023 |
| Hartmann, Cyphers, and Luker | Procedure writers and editors | November 28, 2023 |

Manual Change History

| Procedure | Ver/Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All Sections | 1.0 / 0 | New procedures for all sections for Nodal implementation | November 28, 2010 |
| 2.4 3.1 3.2 3.4 3.5 3.6 4.2 5.3 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Updated Categories and Priorities Updated Response to High Frequency steps 15, 20 and 25 minutes and Response to Low Frequency step 15 Updated steps Failure Indication/Issues and QSE Capacity Issues Updated steps AGC/RLC Issues, System Wide Capacity Issue and AGC/RLC Issues Resolved Updated step 1 Updated step Capacity Surplus Updated step 2, 3, 4 and 5 Updated all steps of “Implement Level 2B” | December 1, 2010 |
| 4.1 4.2 5.2 | 1.0 / 1 1.0 / 2 1.0 / 1 | Updated step “MP unable to Override” Updated step 1 & 2 Updated step 1 in sections WATCH and Advisory | December 15, 2010 |
| 3.1 3.2 3.3 3.4 4.1 5.1 5.4 | 1.0 / 2 1.0 / 2 1.0 / 1 1.0 / 2 1.0 / 2 1.0 / 1 1.0 / 1 | Updated step “BAAL” Updated step “AGC Issues Resolved” Updated step “Hotline” Updated step “Failure Indications, AGC/RLC Issues, System Wide Capacity Issue, AGC/RLC Issues Resolved” Updated step 2 in “Workflow Controller Messages”, added new procedure “Exceeding West – North Stability Limit”, updated Note in “Generation Resource Shut-down/Start-up Process” Updated step 1 in “Watch” and step Hotline in “Scripts” Updated step 1 in “Move from EEA level 3 to EEA lever 2B” | January 5, 2011 |
| 2.4 2.5 2.6 2.7 3.1 3.2 3.3 3.4 3.5 4.1 4.2 5.1 5.2 5.3 5.4 5.5 6.1 6.2 6.3 | 1.0 / 0 1.0 / 2 1.0 / 0 1.0 / 0 1.0 / 3 1.0 / 3 1.0 / 2 1.0 / 2 1.0 / 1 1.0 / 3 1.0 / 3 1.0 / 2 1.0 / 2 1.0 / 2 1.0 / 2 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Added new procedure Changed procedure number Added new procedure Added new procedure Updated sections “Maintain System Frequency”, “Response to High Frequency”, “Response to Low Frequency” and “Actions when Frequency Telemetry in Incorrect. Combined sections 3.3, 3.4 & 4.2 into 3.2 Changed 3.5 “Potential DCS Event” to 3.3 & updated whole procedure Changed 3.6 “Monitor Capacity Reserves & Respond to Capacity Issues to 3.4 Changed 3.7 “Monitor and Control Time Error Correction to 3.5 & updated script Deleted Exceeding West-North Stability Limit Deleted Procedure Updated script Updated step 1 in “Advisory” and “Watch” Updated all steps Updated all steps Updated all steps Updated all steps Updated all steps Updated OCN | January 31, 2011 |
| 2.6 3.2 3.3 3.4 3.6 5.1 5.2 | 1.0 / 1 1.0 / 4 1.0 / 3 - / 3 1.0 / 0 1.0 / 3 1.0 / 3 | Updated step Site Failovers Updated step 3 in SCED Failure, step 4 in RLC Failure, Note in LFC (AGC) Failure and step 2 in EMS (LFC and RLC/SCED Failure Updated step 3 Updated step Capacity Shortage Added new procedure Updated Watch and Emergency Notice All step 1’s | March 25, 2011 |
| 2.6 3.1 3.2 3.3 3.6 5.1 5.4 5.5 | 1.0 / 2 1.0 / 4 1.0 / 5 1.0 / 4 1.0 / 1 - / 4 1.0 / 3 1.0 / 2 | Added steps and updated whole procedure Added new step to Maintain System Frequency and updated Response to High Frequency & Response to Low Frequency Updated steps 2, 3, 5 in SCED Failure; steps 2, 3, 4, 6 in RLC Failure; steps 1, 3 in LFC (AGC) Failure; steps 2, 5 in EMS (LFC and RLC/SCED) Failure Updated NERC Recovery Criteria, step 1 & 4 Updated 1st script Updated step 1 in Watch and Emergency Notice and step Post Updated 1st and 2nd script in Restore Firm Load, Updated 1st in Move From EEA Level 3 to EEA Level 2B Updated step 3 | April 22, 2011 |
| 3.3 5.1 5.3 5.4 6.1 6.2 6.3 6.4 | 1.0 / 5 1.0 / 5 1.0 / 3 1.0 / 4 1.0 / 2 1.0 / 0 1.0 / 2 1.0 / 2 | Updated step NERC Recovery Criteria Updated all step 1’s Updated step 1 in Implement EEA Level 1, step 1 in Implement EEA Level 2A, added note and updated step 2 in Implement EEA Level 2B, step 1 in Implement EEA Level 3 Updated all step 1’s Updated all steps Added new procedure Updated section number and all steps Updated section number and all steps | June 8, 2011 |
| 2.6 3.1 5.1 5.2 5.3 5.4 8.1 | 1.0 / 3 1.0 / 5 1.0 / 6 1.0 / 4 1.0 / 4 1.0 / 5 1.0 / 1 | Added step If EBPs are needed”, updated step IF EBPs are needed and W-N was Active before site failover started Added step Hydro, updated step Frequency Deviations Updated step Watch Updated all steps Updated 1st note, step 1 in EEA level 1 & 2A Updated step 1 in Move for EEA level 1 to 0 Added Market Participant Backup Control Center Transfer procedure | July 20, 2011 |
| 3.1 3.2 3.4 4.1 6.4 6.5 | 1.0 / 6 1.0 / 6 1.0 / 4 1.0 / 4 1.0 / 0 1.0 / 3 | Updated step Monitor, 15 minutes, 20 minutes, and 25 minutes in Response to High Frequency Updated step 2 in LFC Failure, step 4 & 5in EMS Failure Updated step Capacity Surplus Updated step 2 in Workflow Controller Messages Added new procedure “Extreme Hot Weather” Changed section number | August 3, 2011 |
| 2.7 3.1 5.1 5.2 5.3 5.4 6.4 7.1 | 1.0 / 1 1.0/ 7 1.0 / 7 1.0 / 5 1.0 / 5 1.0 / 6 1.0 / 1 1.0 / 1 | Updated step Hotline Call Updated NERC Standard reference table Added projected reserve capacity shortage and Extreme Hot Weather in Watch Updated step 1 in Advisory & Watch Updated 2nd Note, step 1 in Implement EEA 1, step Media Appeal & 1 in Implement EEA 2A, 1st Note & step 2 in Implement EEA 2B Added Note to Move From EEA 3 to EEA 2B and Move From EEA 2A to EEA 1 Updated temperature from 102 to 103 Updated 4th note and step 1 | September 1, 2011 |
| 3.2 5.3 5.4 | 1.0 / 7 1.0 / 6 1.0 / 7 | Updated SCED Failure step 2 and 3, RLC Failure step 3 and LFC (AGC) Failure step 3 Combined EEA 2A & B per NPRR 379 Combined EEA 2 A & B per NPRR 379 | October 1, 2011 |
| 3.2 | 1.0 / 8 | Updated script for LFC and EMS Failure | November 1, 2011 |
| 2.4 2.6 4.1 5.1 6.3 | 1.0 / 1 1.0 / 4 1.0 / 5 1.0 / 8 1.0 / 3 | Added step Review, Updated “Site Failover with W-N Active” Added Note to Large Resource Trips or Runbacks Updated Post in “Scripts” Updated “OCN” and “Advisory” All procedures in this manual have been reviewed. | December 15, 2011 |
| 1.2 3.1 4.1 8.1 | 1.0 / 1 1.0 / 7 1.0 / 6 - / 2 | Updated Scope Updated Response to High Frequency & Response to Low Frequency Updated Large Resource Trips or Runbacks, Quick Start Generation Resource Updated Market Participant Backup Control Center Transfer | January 19, 2012 |
| 2.1 3.1 5.1 5.3 7.1 8.1 | 1.0 / 1 1.0 / 8 1.0 / 7 1.0 / 9 1.0 / 7 1.0 / 2 1.0 / 3 | Updated paragraph 4 Updated BAAL Updated Desktop Guide reference & step QSE Override & QSE unable to Override Updated step 1 in Watch Updated Step 1 in Implement EEA Level 1 Updated Desktop Guide references Changed title names, updated steps 1 & 3 & step Power System Stabilizers (PSS) & Automatic Voltage Regulators (AVR) | March 1, 2012 |
| 2.1 3.1 3.2 3.3 3.5 4.1 5.1 6.2 6.3 6.4 8.1 | 1.0 / 2 1.0 / 9 1.0 / 9 1.0 / 6 1.0 / 2 1.0 / 8 1.0 / 10 1.0 / 4 1.0 / 2 1.0 / 4 1.0 / 4 | Changed TSO, DSP to TO Changed Shift Engineer to Operations Support Engineer, removed Automatic SCED Runs & Hydro Generation in Fast Response Mode, updated Note, Monitor/Deploy, 15 minutes, 20 minutes in Response to Low Frequency Updated step 2, 4 & 5, added SCED Data Input Failure, updated RLC Failure, LFC Failure, & EMMS Failure sections Updated NERC Recovery Criteria step & step 3 Updated Requirements and Notes Changed Shift Engineer to Operations Support Engineer, deleted Large Resource Trips or Runbacks section Updated OCN, Advisory, Watch, Emergency Notice sections Deleted Cold Weather, replaced with Extreme Cold Weather Section changed to Extreme Hot Weather, added OCN and Emergency Notice steps Section number changed Changed Shift Engineer to Operations Support Engineer | May 1, 2012 |
| 3.1 3.4 5.2 | 1.0 / 10 1.0 / 5 1.0 / 6 | Added back step Hydro Generation Operating in Synchronous Condenser Fast Response Mode Updated to reflect changes in the TAC approved Non-Spin document Updated to reflect changes in the TAC approved Non-Spin document | May 14, 2012 |
| 2.6 5.3 5.4 6.3 | 1.0 / 5 1.0 / 8 1.0 / 8 1.0 / 3 | Updated Site Failover step Updated EILS to ERS per NPRR 451 Updated EILS to ERS per NPRR 451 Updated EILS to ERS per NPRR 451 | June 1, 2012 |
| 1.3 2.6 5.1 5.3 5.4 6.2 6.3 7.1 | 1.0 / 1 1.0 / 6 1.0 / 11 1.0 / 9 1.0 / 9 1.0 / 5 1.0 / 4 1.0 / 3 | Removed ERCOT Shift Supervisor paragraph Updated all steps Updated all step 1’s Updated 2nd note, added TCEQ, & XML for ERS Clarified LR and ERS recalls Updated script for Emergency Notice Updated script for Emergency Notice Updated 4th note | July 16, 2012 |
| 2.6 3.1 4.1 5.3 | 1.0 / 7 1.0 / 11 1.0 / 9 1.0 / 10 | Added note to step Database Load Updated Frequency Deviations and Monitor Frequency for the Loss of EMS or Site Failover Incorporated NPRR348 Added 30 MIN ERS and updated steps 1, 2 & 3 on Implement EEA Level 1 | August 29, 2012 |
| 2.2 2.5 3.5 4.1 5.3 | 1.0 / 1 1.0 / 3 1.0 / 3 1.0 / 10 1.0 / 11 | Added Hotline Call Communication Updated step 3 Updated per NOGRR100 Added Note to Shut-down/Start-up Process and new Combine Cycle Generation Resources section Updated ERS scripts All procedures in this manual have been reviewed. | November 1, 2012 |
| 2.5 3.1 3.2 3.3 3.4 3.5 3.6 3.7 5.4 | 1.0 / 4 1.0 / 12 1.0 / 0 1.0 / 10 1.0 / 7 1.0 / 6 1.0 / 4 1.0 / 2 1.0 / 10 | Updated step 3 Updated BAAL New procedure, Monitor Large Ramp Events Updated section # & SCED failure step 2 Updated section # Updated section # Updated section # Updated section # Updated Cancel Watch All procedures in this manual have been reviewed. | March 1, 2013 |
| 2.6 2.7 3.1 3.2 3.3 3.4 3.7 4.1 5.1 5.2 5.3 5.4 5.5 6.1 6.2 6.3 6.4 | 1.0 / 8 1.0 / 2 1.0 / 13 1.0 / 1 1.0 / 11 1.0 / 8 1.0 / 3 1.0 / 11 1.0 / 12 1.0 / 8 1.0 / 12 1.0 / 11 1.0 / 3 1.0 / 3 1.0 / 6 1.0 / 5 1.0 /5 | Updated scripts Updated scripts Updated Monitor Frequency for the Loss of EMS or Site Failover & Actions when Frequency Telemetry is Incorrect Updated scripts Updated scripts Updated script Updated scripts Added QSGR Decommitment step to QSGR Added Generic and Specific scripts Updated Note and scripts Updated TCEQ section and scripts Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts Correct spelling and updated script | June 1, 2013 |
| 2.6 3.1 3.2 3.8 5.1 5.3 5.4 | 1.0 / 9 1.0 / 14 1.0 / 2 1.0 / 0 1.0 / 13 1.0 / 13 1.0 / 12 | Changed title name & updated step EMS Changes & added MMS Changes Updated steps Base Point Deviation & 10 Minutes Updated 1st note Moved procedures from Resource desk Updated step 1 in Watch & Emergency Notice Updated step Pilot Project WS ERS Updated step Reserves | July 15, 2013 |
| 2.6 3.2 3.8 4.1 | 1.0 / 10 1.0 / 3 1.0 / 1 1.0 / 12 | Updated MMS Changes Updated 1st Note Updated Unit & Load RRS Shortage & Not Dispatchable to SCED Updated Shutdown/Startup | August 9, 2013 |
| 3.8 | 1.0 / 2 | Updated Unit RRS Shortage, Load RRS Shortage, REG Shortage, & added Real-Time Non-Spin Shortage | September 27, 2013 |
| 2.4 3.1 3.2 3.3 3.4 3.5 3.7 4.1 5.1 5.2 5.3 5.4 5.5 6.1 6.2 6.3 6.4 7.1 8.1 | 1.0 / 2 1.0 / 15 1.0 / 4 1.0 / 12 1.0 / 9 1.0 / 7 1.0 / 4 1.0 / 13 1.0 / 14 1.0 / 9 1.0 / 14 1.0 / 13 1.0 / 4 1.0 / 4 1.0 / 7 1.0 / 6 1.0 / 6 1.0 / 4 1.0 / 5 | Updated step Log Updated step Frequency Deviations & step Log Updated step Log Updated step Log Updated step Log Added step RMR & updated step Log Updated step Log Updated step Log Updated step Log Updated step Log Updated step Log Updated step Log Updated step Log Updated step Log Updated step Log Updated step Log Updated note and step Log Updated step Log Added & updated step Log All procedures in this manual have been reviewed | December 13, 2013 |
| 2.6 3.3 5.1 | 1.0 / 11 1.0 / 13 1.0 / 15 | Updated for NPRR542 Updated for NPRR542 Updated for NPRR542, deleted West to North GTL and updated procedure for North to Houston to a new GTL | January 1, 2014 |
| 2.6 3.1 3.3 3.5 3.6 4.1 5.3 5.4 6.4 8.1 | 1.0 / 12 1.0 / 16 1.0 / 14 1.0 / 8 1.0 / 5 1.0 / 14 1.0 / 15 1.0 / 14 1.0 / 7 1.0 / 6 | Updated Site Failover Complete Updated VDI information, step Monitor/Deploy & step 10 Minutes in Response to Low Frequency Updated VDI information Updated VDI information Updated step Terminating Time Error Correction Updated VDI information Updated ERS, Media appeal, TCEQ and VDI information Updated steps Reserves and 1 in Restore firm load and step 2 in Move From EEA Level 2 to EEA Level 1 Updated Note Updated Requests to Decommit Self-committed Resource in Operating Period | April 4, 2014 |
| 2.2 3.1 3.3 4.1 5.1 5.2 6.2 6.3 | 1.0 / 2 1.0 / 17 1.0 / 15 1.0 / 15 1.0 / 16 1.0 / 10 1.0 / 8 1.0 / 7 | Added VDIs to Master QSEs Updated step BAAL Updated SCED Failure & SCED Data Input Failure steps Updated QSGR in Quick Start Generation Resource Added Note, updated Market Notices Advisory & Watch Updated Watch steps Updated Emergency Notice step Updated Emergency Notice step | June 1, 2014 |
| 3.5 5.3 | 1.0 /9 1.0 / 16 | Updated Deploying Non-Spin, added HASL Release & Recall Added Media Appeal | August 1, 2014 |
| 4.1 5.1 5.3 | 1.0 / 16 1.0 / 17 1.0 / 17 | Updated Reference section step 2 Updated Generic Script Added HASL Release step | October 1, 2014 |
| 2.3 2.4 2.6 3.3 3.5 5.1 5.3 | 1.0 / 1 1.0 / 3 1.0 / 13 1.0 / 16 1.0 / 10 1.0 / 18 1.0 / 18 | Updated all steps Updated step Send E-mail Deleted Site Failover with W-N Active & updated step If EBPs are Needed Updated 1st note & updated scripts Added new procedure, “Valley Generation” Updated GMD scripts Updated scripts to consolidate All procedures in this manual have been reviewed | December 15, 2014 |
| 6.2 | 1.0 / 9 | Updated Note and scripts | December 22, 2014 |
| 2.2 3.1 3.2 3.5 3.9 6.2 | 1.0 / 3 1.0 / 18 1.0 / 5 1.0 / 11 1.0 / 0 1.0 / 10 | Added Dispatch and VDI definitions Updated Objective and BAAL Updated procedure Updated step 1 and added Log on Valley Generation Added new procedure for NOGRR136 Updated scripts | March 1, 2015 |
| 3.1 3.3 3.5 3.10 4.1 5.1 | 1.0 / 19 1.0 / 17 1.0 / 12 1.0 / 0 1.0 / 17 1.0 / 19 | Clarification to step Frequency Deviation & Hydro Operating in Synch. Condenser Mode Updated Dispatch Instruction scripts Clarification to step HASL Release Manually Deploy RRS New GMD procedure Updated Dispatch Instruction scripts Deleted script for GMD | March 30, 2015 |
| 2.6 2.7 3.2 3.3 3.4 3.63.7 3.10 5.1 5.2 5.3 5.4 5.5 6.1 6.2 6.3 6.4 | 1.0 / 14 1.0 / 3 1.0 / 6 1.0 / 18 1.0 / 10 1.0 / 6 1.0 / 5 1.0 / 1 1.0 / 20 1.0 / 11 1.0 / 19 1.0 / 15 1.0 / 5 1.0 / 5 1.0 / 11 1.0 / 8 1.0 / 8 | Moved scripts to new script procedure Moved scripts to new script procedure Updated 1st note and moved scripts to new script procedure Updated step 2 on SCED Data Input Failure & moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Updated 4th bullet on Emergency Notice & moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure Moved scripts to new script procedure | May 1, 2015 |
| All Sections 2.6 3.5 3.9 3.10 5.1 5.2 6.3 | 1.0 / 1 1.0 / 15 1.0 / 13 1.0 / 1 1.0 / 2 1.0 / 21 1.0 / 12 1.0 / 9 | Added a “Q” for numbered QSE scripts Renamed section to Site Failovers and Database Loads Updated link for Monitor in the Valley Generation Updated 1st Note Updated Procedure Purpose and removed script Updated Specific Scripts, New GTC Updated Q#1, Q#2, Q#3, & Q#4 Script titles Removed Watch script | July 15, 2015 |
| 2.6 3.2 3.3 3.4 3.6 3.7 3.9 3.10 5.1 5.2 5.3 5.4 5.5 6.1 6.2 6.3 6.4 | 1.0 / 16 1.0 / 7 1.0 / 19 1.0 / 11 1.0 / 7 1.0 / 6 1.0 /2 1.0 / 3 1.0 / 21 1.0 / 13 1.0 / 20 1.0 / 16 1.0 / 6 1.0 / 6 1.0 / 12 1.0 / 10 1.0 / 9 | Updated step MMS Changes Typical Script Q#19 Updated step Site Failover Q#20 Updated step Site Failover Complete Q#21 Updated Step If EBP’s are needed Q#22 Updated step Site Failover Complete If EBP’s were needed Q#23 Updated step 2 Q#26 Updated SCED Failure step 2 Q#27 & step 4 Q#28 Updated SCED Data Input Failure step 1 Q#29 Updated RLC Failure step 2 Q#30 & step 4 Q#31 Updated LFC (AGC) Failure step 1 Typical Script step 2 Q#32, step 4 Typical script & Q#33 Updated EMMS (LFC and RLC/SCED) Failure step 1 Typical Script, step 2 Q#34, step 5 Typical Script & Q#35 Updated step 3 Q#36 Updated step Initiating Time Error Correction Q#37 Updated step Terminating Time Error Correction Q#38 Updated step Issue Watch and Deploy Non-Spin Q#39 Updated step Issue Emergency Notice & Deploy Load Resources Q#40 Updated step Recall Load Resources Q#41 Updated step Recall Non-Spin Q#42 Updated step Start CFC Test & End CFC Test Typical Scripts Updated step 1 Q#43 Updated step K Level Increases/Decreases Q#44 Updated step Cancel Q#45 Updated Title Operating Condition Script Updated step Hotline Q#46 Updated step Hotline Cancellation Q#47 Updated Title Specific Scripts for Transmission Operator [State Estimator/RTCA/VSAT] Updated step State Estimator/RTCA Not Solved In 30 MIN Q#48 & Q#49 Updated step VSAT Not Solved In 30 MIN Q#50 & Q#51 Updated step Qualifying Facility Directed to Operate Below LSL Q#52 & Q#53 Updated step New GTC Q#54 Updated step Transmission Watch Q#55 & Q#56 Updated Advisory step Issue Advisory Q#1 Updated Advisory step Cancel Advisory Q#2 Updated Watch step Issue Watch Q#3 Updated Watch step Cancel Watch Q#4 First Note, Updated Implement EEA Level 1 step EEA 1 PRC <2300 Q#5 & Q#6 Updated Implement EEA Level 2 step ERS Resources Q#7 Updated Implement EEA Level 2 step Load Resources Q#8 Updated Implement EEA Level 2 step When ERS Business Hours Change Q#9 Updated Implement EEA Level 3 step When ERS Business Hours Change Q#12, and Implement NPRR708 for EEA, Updated Restore Firm Load step 1 Q#13 Updated Move From EEA Level 3 to EEA Level 2 step 1 Q#14 Updated Move From EEA Level 2 to EEA Level 1 step 1 Q#15 Updated Move From EEA Level 1 to EEA Level 0 step 1 Q#16 Updated Cancel Watch step 1 Q#17 Updated step Return to Normal QSE Notification Q#57 Updated step Emergency Notice Q#61 Updated step Emergency Notice Q#65 Updated step Emergency Notice Q#69 Updated step OCN/Advisory/Watch Q#70 All procedures in this manual have been reviewed | December 31, 2015 |
| 1.3 2.1 3.3 5.1 | 1.0 / 2 1.0 / 3 1.0 / 20 1.0 / 22 | Removed Interchange Coordinator Updated System Operator Responsibility and Authority Updated SCED Failure Note Corrected spelling Qualifying Facility Directed to Operate below LSL Q#52 | March 1, 2016 |
| 2.4 3.1 3.2 4.1 | 1.0 / 4 1.0 / 20 1.0 / 8 1.0 / 18 | Added 2nd Send E-Mail Updated Frequency bias and BAAL step Updated Down Ramp Event step 2 Updated QSGR Qualification Test | April 29, 2016 |
| 2.1 2.2 3.1 3.3 3.5 3.9 4.1 5.1 5.5 | 1.0 / 4 1.0 / 4 1.0 / 21 1.0 / 21 1.0 / 14 1.0 / 3 1.0 / 19 1.0 / 23 1.0 / 7 | Updated for COM-002-4 Updated for COM-002-4 Updated for BAL-001-2 and COM-002-4 Updated for COM-002-4 Updated Deploying Non-Spin step Updated for COM-002-4 Updated for COM-002-4 Updated for COM-002-4 Updated for COM-002-4 | June 30, 2016 |
| 5.3 | 1.0 / 21 | Changed Business Hour to Time Period | July 15, 2016 |
| 2.2 3.3 | 1.0 / 5 1.0 / 22 | Added Hotline Call Communication Note Added SCED Failure Frequency Guidelines Updated LFC Failure Step 2 Q#32 Script Title Updated LFC Failure Step 4 Q#33 Script Title Updated EMMS Failure step 2 Q#34 Script Title Updated EMMS Failure step 5 Q#35 Script Title | September 30, 2016 |
| 3.5 5.1 | 1.0 / 15 1.0 / 24 | Updated Valley Generation step 1 Added Specific Scripts for Transmission Operator step Transmission Emergency script Q#71 | November 2, 2016 |
| 4.1 | 1.0 / 20 | Added Real-Time Data Issues known by the QSE All procedures in this manual have been reviewed | December 30, 2016 |
| 1.3 2.1 2.5 2.6 2.7 3.2 3.10 5.1 5.3 5.5 6.1 6.2 6.3 8.1 | 1.0 / 3 1.0 / 5 1.0 / 5 1.0 / 17 1.0 / 4 1.0 / 9 1.0 / 4 1.0 / 25 1.0 / 22 1.0 / 8 1.0 / 7 1.0 / 13 1.0 / 11 1.0 / 7 | Updated Roles/Responsibilities section Updated for IRO-001-4 Updated categories to show RAS Updated procedure purpose Updated procedure purpose Deleted ELRAS and held location open Updated procedure purpose Updated title and all 1st steps Removed step WS ERS Added Implement EEA Level 3 step EEA3 PRC <1000 MW Updated first note Updated procedure purpose Updated procedure purpose Updated procedure purpose Updated procedure purpose | March 31, 2017 |
| 3.1 | 1.0 / 22 | Updated Frequency bias | April 4, 2017 |
| 3.3 5.1 | 1.0 / 23 1.0 / 26 | Added section on ICCP Outages Updated Transmission Watch | April 6, 2017 |
| 3.1 3.5 | 1.0 / 23 1.0 / 16 | Updated Response to Low Frequency step Monitor/Deploy Updated Insufficient Generation step Deploying Non-Spin | June 1, 2017 |
| 3.1 5.3 | 1.0 / 24 1.0 / 23 | Updated Response to Low Frequency step 25 Minutes Updated 1st note, step EEA Level 2 and EEA Level 3 | June 30, 2017 |
| 2.4 3.1 5.3 | 1.0 / 5 1.0 / 25 1.0 / 24 | Updated steps Added note Response to Low Frequency Updated step 20 Minutes and added scripts Added note Implement EEA Level 2 and Level 3 | July 28, 2017 |
| 3.1 3.3 | 1.0 / 26 1.0 / 24 | Updated Response to Low Frequency step 10 Minutes Updated LFC (AGC) Failure steps 1 & 3 Updated EMMS (LFC and RLC/SCED) Failure steps 1,3, &4 | September 29, 2017 |
| 3.9 | 1.0 / 4 | Updated note | October 31, 2017 |
| 2.4 3.4 7.1 | 1.0 / 6 1.0 / 12 1.0 / 5 | All procedures in this manual have been reviewed Updated steps Updated procedure for BAL-002-2 Updated Primary Control Center 4th note | December 28, 2017 |
| 3.3 3.5 3.9 | 1.0 / 25 1.0 / 17 1.0 / 5 | Updated ICCP Ouages to include MIS and outage scheduler Added Note Updated Start CFC Test & End CFC Test | February 28, 2018 |
| 3.1 | 1.0 / 27 | Updated Maintain System Frequency step Objective | April 5, 2018 |
| 2.2 2.7 3.3 3.9 | 1.0 / 6 1.0 / 5 1.0 / 26 1.0 / 6 | Updated procedure purpose Updated steps Updated steps LFC (AGC) Failure and EMMS (LFC and RLC/SCED) Updated steps | May 1, 2018 |
| 3.1 3.3 3.9 5.3 | 1.0 / 28 - / 27 1.0 / 7 1.0 / 25 | Updated Response to High Frequency & Response to Low Frequency steps Monitor Updated SCED Failure step3 Updated SCED Data Input Failure step 2 Updated RLC Failure step NOTE and step 3 Updated LFC (AGC) Failure NOTE, step 1 & 5 Added step 4. Moved step 4 to step 5 Updated EMMS (LFC and RLC/SCED) Failure step 1, 3, & 5 Updated Note Added Implement EEA Level 3 step | August 31, 2018 |
| 3.1 5.1 | 1.0 / 29 1.0 / 27 | Updated Monitor Frequency for the Loss of EMS or Site Failover Updated for NPRR 825 | October 1, 2018 |
| 3.3 5.3 | 1.0 / 28 1.0 / 26 | Added STATE ESTIMATOR (SE)/Real-Time Contingency Analysis (RTCA) Deleted duplicate Log step All procedures in this manual have been reviewed | December 28, 2018 |
| 2.4 | 1.0 / 7 | Updated steps | January 31, 2019 |
| 3.1 | 1.0 / 30 | Updated Maintain System Frequency step Objective | April 1, 2019 |
| 3.1 4.1 | 1.0 / 31 1.0 / 21 | Updated Response to High Frequency step Monitor & Response to Low Frequency steps Updated SCED Solution Time Parameter step Automatic Trigger | August 1, 2019 |
| 3.5 5.3 | 1.0 / 18 1.0 / 27 | Updated Manually Deploy RRS and Recall steps Added Implement EEA Level 1 step | November 1, 2019 |
| 5.3 5.4 | 1.0 / 28 1.0 / 17 | Updated MSSC Updated MSSC All procedures in this manual have been reviewed | January 1, 2020 |
| 3.1 3.3 3.5 5.4 7.1 | 1.0 / 32 1.0 / 29 1.0 / 19 1.0 / 18 1.0 / 6 | Clarified RUC commits/decommits Clarified RUC commits/decommits Clarified RUC commits/decommits Clarified RUC commits/decommits Updated Primary Control Center steps 1 & 3 | January 31, 2020 |
| 3.1 3.3 7.1 | 1.0 / 33 1.0 / 30 1.0 / 7 | Updated Response to Low Frequency Added Note to LFC (AGC) Failure & EMMS (LFC and RLC/SCED) Failure Updated Title and removed Alternate Control Center | February 28, 2020 |
| 2.1 5.1 5.4 | 1.0 / 6 1.0 / 28 1.0/19 | Added Advance Action Notice per NPRR930 Added Advance Action Notice section per NPRR930 Updated Cancel Watch | July 1, 2020 |
| 2.6 2.7 3.3 3.9 5.1 5.2 6.1 6.2 6.3 6.4 8.1 | 1.0 / 18 1.0 / 6 1.0 / 31 1.0 / 8 1.0 / 29 1.0 / 14 1.0 / 8 1.0 / 14 1.0 / 12 1.0 / 10 1.0 / 8 | Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 & added Note Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 All procedures in this manual have been reviewed | December 31, 2020 |
| 2.3 3.1 3.9 | 1.0 / 2 1.0 / 34 1.0 / 9 | Organization change Organization change Organization change | April 1, 2021 |
| 2.6 5.1 | 1.0 / 19 1.0 / 30 | Changed Notice Builder to Grid Conditions Communications (GCC) Notices Added information on AAN information | May 6, 2021 |
| 2.3 2.4 5.3 5.4 | 1.0 / 3 1.0 / 8 1.0 / 29 1.0 / 20 | Updated email Updated email Added Note Added Note | June 16, 2021 |
| 3.5 5.1 5.2 5.4 | 1.0 / 20 1.0 / 31 1.0 / 15 1.0 / 21 | Updated for OBDRR031 Updated for OBDRR031 Updated for OBDRR031 Updated for OBDRR031 | July 12, 2021 |
| 3.5 5.2 | 1.0 / 21 1.0 / 16 | Updated for OBDRR031 Updated Cancel Watch | July 31, 2021 |
| 5.3 | 1.0 / 30 | Updated 1st Note | September 1, 2021 |
| 5.2 5.3 | 1.0 / 17 1.0 / 31 | Updated for NPRR1106 Updated for NPRR1106 | December 1, 2021 |
| 2.2 3.1 5.1 5.2 5.4 6.1 6.2 6.3 6.4 | 1.0 / 7 1.0 / 35 1.0 / 32 1.0 / 18 1.0 / 22 1.0 / 9 1.0 / 15 1.0 / 13 1.0 / 11 | Updated step 1 Updated instruct to coordinate Updated all steps Updated for clarification Updated Move From EEA Level 2 to EEA Level 1 Updated all steps Updated all steps Updated all steps Updated all steps All procedures in this manual have been reviewed | December 31, 2021 |
| 6.4 | 1.0 / 12 | Updated Note | February 1, 2022 |
| 2.8 | 1.0 / 0 | New procedure section | March 1, 2022 |
| 3.1 3.5 3.7 5.3 | 1.0 / 36 1.0 / 22 1.0 / 7 1.0 / 32 | Updated for NPRR939 & NOGRR191 Updated for NPRR939, NPRR1093 & NOGRR191 Updated for NPRR939 Updated for NPRR939 & NOGRR191 | May 26, 2022 |
| 5.2 | 1.0 / 19 | Updated Steps | July 29, 2022 |
| 5.3 | 1.0 / 33 | Added ESR | October 7, 2022 |
| 3.1 5.2 5.3 | 1.0 / 38 1.0 / 20 1.0 / 34 | Updated Response to Low Frequency steps Updated Advisory Updated RRS Release to HASL | October 14, 2022 |
| 3.5 5.2 5.3 5.4 | 1.0 / 23 1.0 / 21 1.0 / 35 1.0 / 23 | Updated Deploying Non-Spin Updated Media Appeal and TCEQ Added Large Load Curtailment Program step and Watch Updated Media Appeal, TCEQ and EEA 1 Added Cancel Advisory and Log All procedures in this manual have been reviewed | December 30, 2022 |
| 3.1 5.3 6.4 | 1.0 / 39 1.0 / 36 1.0 / 13 | Added Note Response to Low Frequency Added Note Updated procedure title and note | March 31, 2023 |
| 3.1 3.3 3.5 3.7 3.8 4.1 5.3 5.4 | 1.0 / 40 1.0 / 32 1.0 / 24 1.0 / 8 1.0 / 3 1.0 / 22 1.0 / 37 1.0 / 24 | Updated for NPRR863 Updated for NPRR863 Updated for NPRR863 Updated for NPRR863 Updated for NPRR863 Updated for NPRR863 Updated for NPRR863 Updated for NPRR863 | June 9, 2023 |

| 3.1 3.3 3.5 3.7 4.1 5.3 | 1.0 / 41 1.0 / 33 1.0 / 25 1.0 / 9 1.0 / 23 1.0 / 38 | Updated Deploy to Release Updated Deployments to Instructions Updated Deploy to Release Updated Note Updated Deploy to Release Updated Deploy to Release | June 30, 2023 |
| --- | --- | --- | --- |
| 5.3 | 1.0 / 39 | Updated Q#7 Script Name | October 4, 2023 |
| 5.2 5.3 5.4 | 1.0 / 22 1.0 / 40 1.0 / 25 | Updated for NPRR1176 Updated for NPRR1176 Updated for NPRR1176 | November 1, 2023 |
| 3.1 3.5 | 1.0 / 42 1.0 / 26 | Updated for NPRR1176 Added Valley Units | November 7, 2023 |
| 3.4 | 1.0 / 13 | Updated for NPRR1176 | December 1, 2023 |