- Power Operations Bulletin # 1120

ERCOT has posted/revised the Reliability Risk Desk manual.

A copy of the procedure can be found at:

- http://www.ercot.com/mktrules/guides/procedures/index.html

# 8.	Weather Events

## 8.1  	Significant Weather Events

Procedure Purpose:  To monitor the wind forecast during operations with severe weather conditions.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | EOP-011-2 R2, R2.1, R2.2, R2.2.9, R2.2.9.1, R2.2.9.2 |  |  |  |

| Version: 1 | Revision: 5 | Effective Date: December 29, 2023 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Loss of Wind Farm Turbines due to Severe Weather |  |
| Note | Significant weather events can consist of, but are not limited to the following: - Tornados - Strong straight-line winds - Flooding - Freezing precipitation - Wild Fires |
| Manually Override Short Term Wind Power Forecast | The ERCOT Operator will contact the Operations Analysis Engineer to conduct further analysis and to override system: IF: - A severe weather-related de-rate has occurred at a given wind farm, and - The telemetry, Outage Scheduler and COP have not been correctly updated by the QSE. Contact Operations Analysis Engineer to do further analysis and potentially override the forecast given the description above after checking the following: - Number of turbines online - Number of turbines offline - Outage scheduler - Telemetered wind speed (MPH) |
| Note | The QSE should: - Update wind generating unit’s telemetry to reflect the number of turbines lost. - NTON – number of turbines online - NTOF – number of turbines offline - NTUN – number of turbines unknown - Update ERCOT Outage Scheduler for updated HSL information that correctly reflects the number of turbines lost. This follows procedure for forced outages and should be done immediately. - Update unit’s COP in relation to the most recent forecast for the next hour(s) that pertains to the duration the turbines will be lost and accurately reflects the number of turbines lost. Notification to the QSE may be necessary if the above are not complete within the designated time frame. |
| Post | Coordinate with the Real-Time Operator for making hotline calls and the posting of the notices on the ERCOT Website. |
| Cancel Posting | Coordinate with the Real-Time Operator for the cancelation of the postings on the ERCOT Website and making hotline calls. |
| Log | Log all actions. |
| ### High Wind Output Forecast with Forecasted Severe Weather in a Region |  |
| Manually Override Short Term Wind Power Forecast | The ERCOT Operator will contact the Operations Analysis Engineer to conduct further analysis and to override the system if all the following conditions are met: - The wind forecast is persistently higher than the actual output (the over-forecast error will exceed 20% of installed capacity of wind farms affected or 1000 MW in a region) for a future period of time. - Weather forecasts from multiple sources indicate a winter/tropical storm will occur at the same timeline as the high forecasted output. |
| Action | Further analysis could potentially reduce the forecasted value of the region in question to a lower output. |
| Example | Below is an example of the STWPF being much higher due to turbines freezing. You will see the light blue line much lower than the multiple-colored lines that are forecasts. When the actual output begins to dip away from the forecast and icing conditions exist, it is likely an override is needed. |

| Log | Log all actions. |
| --- | --- |

## 8.2 	Extreme Hot Weather

Procedure Purpose:  Ensure when ERCOT issues extreme hot weather OCN, Advisory, Watch, or Emergency Notice, System Operators utilize the Extreme Weather Capacity Monitor as a check against QSE’s COP to verify accuracy of weather limitations for Resources during event.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | EOP-011-2 R2, R2.1, R2.2.9, R2.2.9.2 |  |  |  |

| Version: 1 | Revision: 1 | Effective Date: December 29, 2023 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Note | The purpose of this section is to monitor Resource COPs for accuracy against their submitted temperature limitations any time an extreme hot weather notice is in effect. |
| Note | A high risk Resource is any Resource shown to be operating in forecasted temperatures that are 3 degrees Fahrenheit higher than the highest maximum operating value submitted for weather limitations. |
| 1 | IF: - ERCOT issues an OCN, Advisory, Watch, or Emergency Notice due to forecasted or actual extreme hot weather; THEN: - For the timeframe an extreme hot weather Notice is issued, prior to DRUC execution, monitor the Extreme Weather Capacity Monitor for any Resources considered at high risk with COPs that are exceeding their extreme hot weather operating limits daily. IF: - The Extreme Weather Capacity Monitor displays 3000 MW or more of high risk generation due to Resources’ COP exceeding their hot weather operating limits; THEN: - Inform the Shift Supervisor, - Coordinate with the Real-time operator for Hotline calls and Resource operator for posting message, and - Confirm message on ERCOT Website for large amount of high risk generation. Q#66/67/68/69 - Typical Hotline Script for Extreme Hot Weather [OCN/Advisory/Watch/Emergency] Typical ERCOT Website Posting for Large Amount of Generation At Risk: At [time] ERCOT has [XXXX MW] shown to be at risk due to temperature limitations, for operating day [date]. All QSEs are instructed to update their COP to reflect known planned or forced outages of Resources due to the extreme hot weather. |
| Log | Log all actions, including when notification to QSE’s are made. |

## 8.3 	Extreme Cold Weather

Procedure Purpose:  When ERCOT issues an extreme cold weather OCN, Advisory, Watch, or Emergency Notice, System Operations will utilize the Extreme Weather Capacity Monitor as a check against QSE’s COP to verify accuracy of weather limitations for Resources during event.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | EOP-011-2 R2, R2.1, R2.2, R2.2.9, R2.2.9.1 |  |  |  |

| Version: 1 | Revision: 1 | Effective Date: December 29, 2023 |
| --- | --- | --- |

| Step |  | Action |
| --- | --- | --- |
| Note | The purpose of this section is to monitor Resource COPs for accuracy against their submitted temperature limitations any time an extreme cold weather notice is in effect. |  |
| Note | A high risk Resource is any Resource shown to be operating in forecasted temperatures that are 3 degrees Fahrenheit lower than the lowest minimum operating value submitted for weather limitations. |  |
| Extreme Weather Capacity Monitor | IF: - ERCOT issues an OCN, Advisory, Watch, or Emergency Notice due to forecasted or actual extreme cold weather; THEN: - For the timeframe an extreme cold weather Notice is issued, prior to DRUC execution, monitor the Extreme Weather Capacity Monitor for any Resources considered at high risk with COPs that are exceeding their extreme cold weather operating limits daily. IF: - The Extreme Weather Capacity Monitor displays 3000 MW or more of high risk generation due to Resources’ COP exceeding their cold weather operating limits; THEN: - Inform the Shift Supervisor, - Coordinate with the Real-time operator for Hotline calls and Resource operator for posting message, and - Confirm message on ERCOT Website for large amount of at-risk generation. Q#62/63/64/65 - Typical Hotline Script for Extreme Cold Weather [OCN/Advisory/Watch/Emergency] Typical ERCOT Website Posting for Large Amount of Generation At Risk: At [time] ERCOT has [XXXX MW] shown to be at risk, due to temperature limitations, for operating day [date]. All QSEs are instructed to update their COP to reflect known planned or forced outages of Resources due to the extreme cold weather. |  |
| Log | Log all actions, including when notification to QSE’s are made. |  |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Hartmann, Gaddy, Self, and Frosch | Preparers | January 24, 2017 |
| Hartmann, Gaddy and Frosch | Procedure writers and editors | March 27, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | May 26, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | June 23, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | July 24, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | September 27, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | December 22, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | February 22, 2018 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | March 26, 2018 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | April 27, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | May 25, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | August 24, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | December 21, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | January 25, 2019 |
| Hartmann, Gaddy and Pence | Procedure writers and editors | July 29, 2019 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | October 29, 2019 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | December 20, 2019 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | January 27, 2020 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | February 24, 2020 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | June 25, 2020 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | September 23, 2020 |
| Hartmann, Gaddy, Cyphers, and Sheets | Procedure writers and editors | December 23, 2020 |
| Hartmann, Gaddy, Cyphers, and Sheets | Procedure writers and editors | April 29, 2021 |
| Hartmann, Gaddy, Cyphers, and Sheets | Procedure writers and editors | June 11, 2021 |
| Hartmann, Gaddy, Cyphers, and Sheets | Procedure writers and editors | August 27, 2021 |
| Hartmann, Gaddy, Cyphers and Frosch | Procedure writers and editors | December 17, 2021 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | January 27, 2022 |
| Hartmann, Gaddy, Cyphers and Frosch | Procedure writers and editors | February 24, 2022 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | March 31, 2022 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | August 29, 2022 |
| Hartmann, Gaddy, Cyphers, and Frosch | Procedure writers and editors | December 22, 2022 |
| Hartmann, Gaddy, Cyphers, and Herrera | Procedure writers and editors | March 27, 2023 |
| Hartmann, Gaddy, Cyphers, and Luker | Procedure writers and editors | July 26, 2023 |
| Hartmann, Cyphers, and Luker | Procedure writers and editors | October 26, 2023 |
| Hartmann, Cyphers, and Luker | Procedure writers and editors | December 20, 2023 |

Manual Change History

| Procedure | Ver/Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All | 1.0 / 0 | New procedures | January 30, 2017 |
| 2.1 3.1 4.4 5.1 7.1 7.2 9.1 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Updated System Operator Responsibility and Authority Updated Up Ramp Event step 2 Updated Panhandle Region Updated Reliability Risk Desk performs STNET Study Updated title and all 1st steps Updated Implement EEA Level 3 steps Updated Title | March 31, 2017 |
| 3.1 | 1.0 / 2 | Updated Down Ramp Event step 1, 2 & 3 Updated Up Ramp Event step 1 & 2 | June 1, 2017 |
| 3.1 7.2 | 1.0 / 3 1.0 / 2 | Updated Down Ramp Event step 2 Updated 1st note, step 1 changed to EEA Level 3 | June 30, 2017 |
| 7.2 | 1.0 / 3 | Added note Implement EEA Level 2 and Level 3 | July 28, 2017 |
| 7.2 | 1.0 / 4 | Updated Implement EEA Level 3 | September 29, 2017 |
| 8.1 | 1.0 / 1 | All procedures in this manual have been reviewed Updated Primary Control Center 4th note | December 28, 2017 |
| 3.3 | 1.0 / 1 | Updated Day Ahead RRS Sufficiency Monitoring, moved Real-time RRS Sufficiency Monitoring down, added Look Ahead Critical Inertia Level Sufficiency Monitoring and Real-time Critical Inertia Level Sufficiency Monitoring | February 28, 2018 |
| 9.1 | 1.0 / 2 | Updated Note | March 30, 2018 |
| 2.2 | 1.0 / 1 | Updated procedure purpose | May 1, 2018 |
| 5.1 | 1.0 / 2 | Added Phase Angles steps | May 31, 2018 |
| 5.1 | 1.0 / 3 | Updated and named step to Voltage contingencies | August 31, 2018 |
| 4.1 4.2 | 1.0 / 1 1.0 / 1 | Updated procedure purpose, added note and updated step Updated procedure purpose, added note and updated step All procedures in this manual have been reviewed | December 28, 2018 |
| 4.2 | 1.0 / 2 | Updated steps | January 31, 2019 |
| 3.1 4.1 | 1.0 / 3 1.0 / 2 | Deleted all steps Monitor Large Ramp Events Added Intra-Hour Wind Forecast and added Note Updated STWPF Selection Change due to forecast vs. output deviation and added Note | August 1, 2019 |
| 4.1 4.7 5.1 | 1.0 / 3 1.0 / 0 1.0 / 4 | Removed Weather Forecast Created section Weather Forecast Errors Updated Voltage Contingencies | November 1, 2019 |
| 7.2 7.3 | 1.0 / 5 1.0 / 1 | Updated MSSC Updated MSSC All procedures in this manual have been reviewed | January 1, 2020 |
| 3.3 5.1 7.3 8.1 | 1.0 / 2 1.0 / 5 1.0 / 2 1.0 / 2 | Clarified RUC-commits/decommits Clarified RUC-commits/decommits Clarified RUC-commits/decommits Updated Primary Control Center steps 1 & 3 | January 31, 2020 |
| 3.4 4.1 4.3 4.4 4.5 4.6 8.1 | 1.0 / 1 1.0 / 4 1.0 / 1 1.0 / 2 1.0 / 1 1.0 / 1 1.0 / 3 | Updated 3rd Note Updated 1st Note Updated Procedure Purpose & steps Updated Procedure Purpose & steps Updated Procedure Purpose Updated Procedure Purpose, Title & steps Updated Title and removed Alternate Control Center | February 28, 2020 |
| 2.1 7.1 | 1.0 / 2 1.0 / 2 | Added Advance Action Notice per NPRR930 Added Advance Action Notice section per NPRR930 | July 1, 2020 |
| 2.1 | 1.0 / 3 | Updated System Operator Responsibility and Authority | October 1, 2020 |
| 4.5 6.1 7.1 9.1 | 1.0 / 2 1.0 / 1 1.0 / 3 1.0 / 3 | Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 & added Note Updated for NPRR1039 All procedures in this manual have been reviewed | December 31, 2020 |
| 3.3 | 1.0 / 3 | Updated Real-time Critical Inertia Level Sufficiency Monitoring step 3 | May 6, 2021 |
| 4.6 4.7 | 1.0 / 2 1.0 / 1 | Updated for SCR 811 Updated Load Forecast email | June 16, 2021 |
| 7.2 | 1.0 / 6 | Updated 1st Note | September 1, 2021 |
| 2.2 7.1 7.2 | 1.0 / 2 1.0 / 4 1.0 / 7 | Updated step 1 Updated all steps Updated steps 1 & 2 All procedures in this manual have been reviewed | December 31, 2021 |
| 4.5 | 1.0 / 3 | Updated Note | February 1, 2022 |
| 2.3 | 1.0 / 0 | New procedure section | March 1, 2022 |
| 4.1 4.2 | 1.0 / 5 1.0 / 3 | Updated Note Updated Note | April 7, 2022 |
| 4.1 4.6 | 1.0 / 6 1.0 / 3 | Updated section Updated section | September 1, 2022 |
|  |  | All procedures in this manual have been reviewed | December 30, 2022 |
| 4.5 4.6 8.1 8.2 8.3 9.1 10.1 | 1.0 / 4 1.0 / 2 1.0 / 4 1.0 / 0 1.0 / 0 1.0 / 4 1.0 / 4 | Updated section number Updated section number Section 4.5 moved to section 8.1 and updated title New procedure New procedure Updated section number Updated section number | March 31, 2023 |
| 7.2 | 1.0 / 8 | Updated Note for NPRR1143 | August 1, 2023 |
| 7.2 7.3 | 1.0 / 9 1.0 / 3 | Updated For NPRR1176 Updated For NPRR1176 | November 1, 2023 |
| 8.0 8.1 8.2 8.3 | 1.0 / 1 1.0 / 5 1.0/ 1 1.0 / 1 | Updated Title to Weather Events Updated first Note Updated step Log Updated step Log All procedures in this manual have been reviewed | December 29, 2023 |