- Power Operations Bulletin # 1124

ERCOT has posted/revised the Shift Supervisor Desk manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

## http://www.ercot.com/mktrules/guides/procedures/index.html

## 6.1	Reports

Procedure Purpose: Provide reporting criteria and instructions for the daily reports sent to the PUC, the process to report certain events to the Texas Reliability Entity, posting EEA notices to RCIS and the process for reporting system disturbances to NERC and DOE.

| Protocol Reference | 22 (B) | 6.5.1.2 (4) |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 3.2.3 | 4.7 |  |  |
| NERC Standard | EOP-004-4 R1, R2 | EOP-010-1 R1, R1.1, R2 | EOP-011-2 R2, R2.1, R2.2, R2.2.3, R2.2.3.2, R2.2.3.3, R2.2.5 |  |

| Version: 1 | Revision: 9 | Effective Date: December 29, 2023 |
| --- | --- | --- |

| Step | Action |  |  |
| --- | --- | --- | --- |
| ### PUCT Daily Report |  |  |  |
| Note | The PUCT Daily Report is automatically sent at 0530 and again at 1430 each day during the summer. During the Fall, Winter and Spring the PUCT Daily Report is automatically sent at 0230 and again at 1430 each day. Notify Grid Applications Development if the report fails to automatically send. |  |  |
| Prepare Report | During the Summer prepare the PUCT Daily Report between 0530 – 0600 and again between 1430 – 1500 each day. During the Fall, Winter and Spring prepare the PUCT Daily Report between 0230 – 0300 and again between 1430 – 1500 each day. Management will coordinate the transition of reports so that everyone knows the appropriate times that the report should be sent. |  |  |
| Review Report | Open up the PUCT Report site and review at any time. If required to send out the report manually, Refer to Desktop Guide Shift Supervisor Section 2.7. |  |  |
| E-Mail Report | E-mail the report to the distribution list entitled “PUC-Available Generating Resources.” Subject line example: 0600 PUCT Report June 1, 2019 |  |  |
| ### Unit Trip Posting |  |  |  |
| Report | Complete the Unit Trip posting for the previous day between 0000 – 0800 each day of the week. |  |  |
| Analyze | Review: - Any unit trips from the previous day, - Post an Operational Information message, low priority, on the ERCOT Website |  |  |
| <450 MW | IF: - No trips are greater than 450 MW, - Post the following message example on the ERCOT Website |  |  |
| Post | No sudden loss of generation greater than 450 MW occurred on <Date>. |  |  |
| ≥450 MW | IF: - A trip was 450 MW or more, - Post the following message example on the ERCOT Website |  |  |
| Post | On <Date>, a sudden loss of generation occurred at <Time> totaling *** MW. Frequency declined to **.*** Hz, ERCOT load was **,*** MW. |  |  |
| Multiple Trip Example | On <Date>, a sudden loss of generation occurred at <Time> totaling *** MW. Frequency declined to **.*** Hz, ERCOT load was **,*** MW. Another sudden loss of generation occurred at <Time> totaling *** MW. Frequency declined to **.*** Hz, ERCOT load was **,*** MW. |  |  |
| ### Load Curtailment due to Transmission Problem Posting |  |  |  |
| Note |  |  | If the Emergency Condition is the result of a transmission problem, ERCOT shall act immediately to return the ERCOT System to a reliable condition, including instructing any QSE representing a Resource to change the Resource’s output, curtailing any remaining DC Tie Load, and instructing TSPs or DSPs to drop Load. In addition, ERCOT may instruct any QSE representing an ESR to suspend ESR charging if ERCOT determines that a Load reduction by the ESR is capable of mitigating the transmission problem. An ESR co-located behind a POI with onsite generation that is incapable of exporting additional power to the ERCOT System may continue to charge as long as maximum output to the ERCOT System is maintained |
| Analyze |  |  | REVIEW: - Any instructed Load Curtailment, Load Resource Deployment, ERS Resource Deployment, or DC Tie curtailments from the current day; IF: - An event occurred during the current day; THEN: - Complete the Load Curtailment due to Transmission Problem posting prior to midnight on the day of the event if Resources output is curtailed, any remaining DC Tie load is curtailed, TSPs and DSPs instructed load is curtailed, ESR has been instructed to suspend charging, or Load Resource(s) or ERS Resource(s) are deployed due to a transmission problem; POST: - An Operational Information message, low priority, on the ERCOT Website. |
| ERCOT Website Posting Example |  |  | Typical ERCOT Website posting: On <Date>, at <Time>, ERCOT instructed a(n) <Load Curtailment/Load Resource Deployment/ERS Resource Deployment/DC Tie Curtailment> totaling *** MW in the <substation(s) or geographic area>. All < Load/Load Resources/ERS Resources/DC Tie Curtailments> were restored at <Time>. |
| ### Event Analysis Reporting |  |  |  |
| 1 | WHEN an event occurs that is listed on the “event list” below, before shift is over: - E-mail information to Director Control Room Operations and Designee - The subject line of the e-mail should read “TRE Event.” |  |  |
| Event List | For purposes of the event analysis program, brief reports must be completed with 10 days (Responsibility of Grid Analysis group). Most events listed are either DOE-417 or EOP-004 reportable, those timelines and forms will be used in place of the EA brief report. Category 1 Events: - An outage, contrary to design, of three or more BES Facilities caused by an event: - The outage of a combination of three or more BES Facilities (excluding successful automatic reclosing) - The outage of an entire generation station of three or more generators (aggregate generation of 500 MW to 1,999 MW); each combined cycle unit is counted as one generator - Retired on January 1, 2024 - Failure or misoperation of a BES RAS - Retired on January 1, 2024 - BES system separation contrary to design results in an island of 100 MW to 999 MW. This excludes BES radial connections, and non-BES (distribution) level islanding - Retired on January 1, 2016 - The loss of generation of 1,400 MW to 1,999 MW - Loss of monitoring and/or control, at a Control Center, such that it degrades the entity’s ability to make Real-time operating decisions that are necessary to maintain reliability of the BES in the entity’s footprint for 30 continuous minutes or more Some examples that should be considered include, but are not limited to the following: - Loss of operator ability to remotely monitor or control BES elements - Loss of communications from SCADA RTU - Unavailability of ICCP links reducing BES visibility - Loss of the ability to remotely monitor and control generating units via AGC - Unacceptable state estimator or contingency analysis solutions - A non-consequential interruption of inverter type resources aggregated to 500 MW or more not caused by a fault on its inverters, or its AC terminal equipment - A non-consequential interruption of a DC tie, between two separate asynchronous systems, loaded at 500 MW or more, when the outage is not caused by a fault on the DC tie, its inverters, or its AC terminal equipment. Category 2 Events: - Complete loss of Interpersonal Communication and Alternative Interpersonal Communication capability affecting its staffed BES control center for 30 continuous minutes or more - Retired on January 1, 2016 refer to Category 1h - BES Emergency resulting in a voltage deviation of equal to or greater than 10% difference of nominal voltage sustained for 15 continuous minutes - Complete loss of off-site power (LOOP) to a nuclear generating station per the Nuclear Plant Interface Requirement - System separation contrary to design, that results in an island of 1,000 MW to 4,999 MW - Simultaneous loss of 300 MW or more of firm load due to a BES event, contrary to design, for more than 15 minutes - IROL exceedance for greater than 30 minutes. Category 3 Events: - Loss of firm load, contrary to design, of 2,000 MW or more - System separation contrary to design, that results in an island of 5,000 MW or more - Not applicable to ERCOT - Loss of 2,000 MW or more provided by DC ties(s) connected to asynchronous resources - Loss of generation (including inverter-based resources) of 2,000 MW or more. This excludes RAS action that performed as designed. |  |  |
| ### NERC and DOE Reporting Operating Plan |  |  |  |
| Note | - Send an email to “SysOpsMgrs” when a NERC or DOE reporting event occurs or if suspected to occur and verify it was received due to potential time constraints on report submissions - Within 72 hours of incident a Final Report must be filed unless an interim update has been provided |  |  |
| DOE-417 Reporting Events | DOE-417 forms can be downloaded at: https://www.oe.netl.doe.gov/docs/OE417_Form_Instructions_05312024.pdf The events listed below must be reported within 1 hour of the incident: - Physical attack that causes major interruptions or impacts to critical infrastructure facilities or to operations - Reportable Cyber Security Incident - Cyber event that is not a Reportable Cyber Security Incident that causes interruptions of electrical system operations - Complete operational failure or shut-down of the transmission and/or distribution electrical system - Electrical System separation (Islanding) where part or parts of a power grid remain(s) operational in an otherwise blacked out area or within the partial failure of an integrated electrical system - Uncontrolled loss of 300 MW or more of firm system loads for more than 15 minutes from a single incident - Firm Load shedding of 100 MW or more implemented under emergency operational policy - System-wide voltage reduction of 3% or more - Public appeal to reduce the use of electricity for purpose of maintaining the continuity of the electric power system The events listed below must be reported within 6 hours of the incident: - Physical attack that could potentially impact electric power system adequacy or reliability; or vandalism which target components of any security systems - Cyber event that could potentially impact electric power system adequacy or reliability - Loss of electric service to more than 50,000 customers for 1 hour or more - Fuel supply emergencies that could impact electric power system adequacy or reliability The events listed below must be reported by the later of 24 hours of recognition of meeting an event threshold for reporting or by the end of the next business day (4 p.m. local time will be considered the end of the business day): - Damage or destruction of a Facility that results in action(s) to avoid a Bulk Electric System Emergency - Damage or destruction of its Facility that results from actual or suspected intentional human action - Physical threat to its Facility excluding weather or natural disaster related threats, which has the potential to degrade the normal operation of the Facility. Or suspicious device or activity at its Facility - Physical threat to its Bulk Electric System control center, excluding weather or natural disaster related threats, which has the potential to degrade the normal operation of the control center. Or suspicious device or activity at its Bulk Electric System control center - Bulk Electric System Emergency resulting in voltage deviation on a Facility; A voltage deviation equal to or greater than 10% of nominal voltage sustained for greater than or equal to 15 continuous minutes - Uncontrolled loss of 200 Megawatts or more of firm system loads for 15 minutes or more from a single incident for entities with previous year’s peak demand less than or equal to 3,000 Megawatts - Total generation loss, within one minute of: greater than or equal to 1,400 Megawatts in the ERCOT Interconnection - Complete loss of off-site power (LOOP) affecting a nuclear generating station per the Nuclear Plant Interface Requirements - Unexpected Transmission loss within its area, contrary to design, of three or more Bulk Electric System Facilities caused by a common disturbance (excluding successful automatic reclosing) - Unplanned evacuation from its Bulk Electric System control center facility for 30 continuous minutes or more - Complete loss of Interpersonal Communication and Alternative Interpersonal Communication capability affecting its staffed Bulk Electric System control center for 30 continuous minutes or more - Complete loss of monitoring or control capability at its staffed Bulk Electric System control center for 30 continuous minutes or more Attempted Cyber Compromise: Within 1 calendar day of determination of the attempted cyber compromise: - Cyber Security Incident that was an attempt to compromise High or Medium Impact Bulk Electric System Cyber Systems or their associated Electronic Access Control or Monitoring Systems |  |  |
| Event Reporting EOP-004-4 | If an EOP-004 reportable event is also a reportable event under the DOE-417 requirements, the DOE-417 form can be used to report to NERC and DOE. The events listed below must be reported by the later of 24 hours of recognition of meeting an event threshold for reporting or by the end of the next business day (4 p.m. local time will be considered the end of the business day). - Damage or destruction of a Facility that results in actions to avoid a BES Emergency - Damage or destruction of a Facility that results from actual or suspected intentional human action - Physical threats to a Facility excluding weather or natural disaster related threats, which has the potential to degrade the normal operation of the Facility or suspicious device or activity at a Facility - Physical threats to its BES control center, excluding weather or natural disaster related threats, which has the potential to degrade the normal operation of the control center or suspicious device or activity at its BES control center - Public appeal for load reduction to maintain continuity of the BES - System wide voltage reduction of 3% or more - Firm load shedding ≥ 100 MW (manual or automatic) - Voltage deviation of =/> 10% of nominal voltage sustained for ≥ 15 continuous minutes - Uncontrolled loss of firm load for greater than 15 minutes from a single incident: - ≥ 300 MW for entities with a previous year’s demand of ≥ 3,000 MW OR - ≥ 200 MW for all other entities - Each system separation resulting in an island ≥ 100 MW - Loss of generation of ≥ 1,400 MW - Complete loss of off-site power affecting a nuclear generating station per the Nuclear Plant Interface Requirement - Unexpected loss within its area, contrary to design, of three or more BES Elements caused by a common disturbance (excluding successful automatic reclosing) - Unplanned evacuation from BES control center facility for 30 continuous minutes or more - Complete loss of Interpersonal Communication and Alternative Interpersonal Communication capability affecting its staffed BES control center for 30 continuous minutes or more - Complete loss of monitoring or control capability at its staffed BES control center for 30 continuous minutes or more |  |  |
| Reporting To Entities | When required to file or forward a report from other entities, the Director Control Room Operations or the Designee will be responsible. File or forward the disturbance report to the following entities: - NERC System Awareness (systemawareness@nerc.net) - NERC (operations@eisac.com), requirement for cyber and courtesy copy for all other reports - Fax (404) 446-9770, if internet down - Phone (404) 446-9780 - DOE when required above (doehqeoc@hq.doe.gov) - Fax (202) 586-8485, if internet down - Phone (202) 586-8100 - NERC and DOE Disturbance Reporting distribution list In the body of the e-mail, type the following: - "Contains Privileged Information and/or Critical Energy Infrastructure Information - Do Not Release". |  |  |
| Note | - If adverse conditions prevent reporting the damage caused by an event and issuing a written Event Report within the timing of the Standard, notify NERC and Texas RE and provided as much information as is available at the time of the notification. - Please be aware that for phone calls to NERC, you will be prompted by a computerized auto-attendant to press 1 for operational issues or 2 for cyber-security issues. |  |  |
| ### RCIS Reporting |  |  |  |
| EEA Postings | There are four levels of Emergency Energy Alert (EEA). As ERCOT enters each level, postings must be made on the RCIS under “Energy Emergency Alert”: - “ERCOT is declaring EEA 1” - “ERCOT is declaring EEA 2” - “ERCOT is declaring EEA 3” - “ERCOT is in EEA 0 and back to normal operations.” |  |  |
| ### NXT Notification Requirements |  |  |  |
| Beginning of each Shift |  | Log into the NXT Communicator at the beginning of each shift in order to make the required notification quickly. - If issues arise and you are unable to log into the NXT Communicator with your user name, notify the helpdesk and request immediate assistance. |  |
| Note |  | NXT notification should be coordinated with the Shift Engineer. |  |
| Watch |  | IF: - A Watch for Physical Responsive Capability is initiated, THEN: - Select the “SO Watch PRC below 3000” Scenario and activate notification, WHEN: - A Watch for Physical Responsive Capability has been cancelled, THEN: - Select the “SO Watch for PRC Cancelled” Scenario and activate notification. |  |
| EEA Implementation Levels |  | IF: - ERCOT initiates EEA Level 1, THEN: - Select the “SO EEA Level 1” Scenario and activate notification, IF: - ERCOT initiates EEA Level 2, THEN: - Select the “SO EEA Level 2” Scenario and activate notification, IF: - ERCOT initiates EEA Level 3 with Load Shed, THEN: - Select the “SO EEA Level 3, WITH Load Shed” Scenario and activate notification. |  |
| EEA Termination Levels |  | WHEN: - EEA Level 3 is terminated, THEN: - Select the “SO EEA Level 3 to EEA Level 2” Scenario and activate notification, WHEN: - EEA Level 2 is terminated, THEN: - Select the “SO EEA Level 2 to EEA Level 1” Scenario and activate notification, WHEN: - EEA Level 1 is terminated, THEN: - Select the “SO EEA Level 1 Cancellation” Scenario and activate notification. |  |
| Loss of Firm Load |  | IF: - An Operator (ERCOT or TO) has issued a request for firm load shed of ≤ 100 MW, THEN: - Notify the Director Control Room Operations and/or Designee immediately. WHEN: - An Operator (ERCOT or TO) has issued a request for firm load shed of ≥ 100 MW, THEN: - Notify the Director Control Room Operations and/or Designee immediately, - Select the “SO Request Firm Load Shed” Scenario and activate notification. |  |
| NXT Testing |  | WHEN: - Performing Shift Supervisor Procedure 9.2 Monthly Testing of Non-Routinely used Telecommunications Facilities, THEN: - Select the “SO ENS Test” Scenario and activate notification. |  |
| ### ERCOT Morning Report |  |  |  |
| Note | - This report is currently only required Monday – Friday. - The Morning Report form is located on the _Operations Official Spreadsheets folder |  |  |
| 1 | Weather Information: - The temperatures are automatically pulled from the EMS, however please verify temperatures from a National or Local Weather Service for each city listed and adjust as necessary. - Enter the current day forecast conditions for each city listed. |  |  |
| 2 | Load Data: - The All-Time Peak MW and Seasonal Peak MW will be provided as needed. - Verify the Projected Peak MW and peak hour for the current day. Use the most reasonable forecast, which may not be the highest. - Verify the Previous Day Actual MW. |  |  |
| 3 | Interchange: - Verify the net flow across the DC-Ties for the peak hour. This can be obtained from the MOI under “DC Tie Scheduling” or from the Excel MAI. |  |  |
| 4 | Transmission Line Outages: - Verify the number of 345 kV line segment outages for the peak hour. |  |  |
| 5 | Generation MW Totals: - Verify the Generation scheduled outage MW total. - Verify the Generation forced outage MW total. |  |  |
| 6 | Projected MW Reserves: - Verify the Responsive Reserve requirement at the Project Peak. - Verify the anticipated operating reserves available at time of peak. - The anticipated operating reserves can be found by adding the “Max Cap. Room” and Responsive Reserve requirement. |  |  |
| 7 | Recent ERCOT Congestion Activity: - No action needed |  |  |
| 8 | Comments: - List any active OCNs, Advisories, Watches or Emergency notices. |  |  |
| 9 | Select: - Create Report |  |  |
| Email | The file is transferred to P:\SYSTEM OPERATIONS drive in the NERC Morning Report Folder. This report should be sent as an attachment by 0700 using the e-mail distribution list entitled “ERCOT Morning Report.” The subject line of the e-mail should read “ERCOT Morning Report for <date>” |  |  |
| ### RMR Unexcused Misconduct Events |  |  |  |
| Note | - For a RMR unit, a “Misconduct Event” means any hour or hours during which Participant is requested to, but does not; deliver the energy at a level of at least 98% on each hour of the level shown in the Availability Plan. - For a Synchronous Condenser Unit, a “Misconduct Event” means any hour or hours during which Participant is requested to, but does not, synchronize the Unit to the ERCOT Transmission Grid during any hour in which the Unit is shown in the Availability Plan |  |  |
| 1 | IF: - An RMR or Synchronous Condenser fail to deliver the energy when requested to; THEN: - Notify the Director Control Room Operations and/or Designee. - The management will gather the detailed information and send an e-mail to “Nodal Settlements and Billing” with the subject line “Action Required – RMR Unexcused Misconduct Event”. |  |  |
| ### Shift Schedule |  |  |  |
| Note | - Operations Shift Schedules will be posted to the ERCOT Website under Data Products>Grid on the Transmission Page in the Reports & Extracts section. - The posting of the schedule will be current at all time to be compliant with the Protocols. |  |  |
| ### Geomagnetic Disturbance (GMD) |  |  |  |
| Note | Solar storms or Geomagnetic disturbances (GMDs) are caused by the interaction of coronal mass ejections (solar flares) with the Earth’s Ionosphere. This interaction produces ionospheric currents in the magnitude of millions of amperes which disturb Earth’s magnetic field. This disturbance induces voltage potential at Earth’s surface which results in geomagnetically induced currents (GICs) in conducting paths such as long transmission lines, pipelines, cables etc. GICs are low frequency or quasi-DC currents which enter and exit the power system at transformer groundings and grounded transmission lines. GICs of 100’s of amperes in magnitude have been recorded. Hence the GICs have the potential to disrupt the normal operation of power system and may damage transformers. GICs may also lead to the loss of reactive power support and hence may cause voltage instabilities. |  |  |
| Monitor | Monitor forecasted and current space weather: - Reliability Coordinator Information System (RCIS) at https://rcis.nerc.net - NOAA’s Space Weather Prediction Center http://www.swpc.noaa.gov/ |  |  |
| Warning (Forecasted) | WHEN: - A forecasted GMD Warning is issued for K-7 and greater or G3 and greater; THEN: - Post message on the ERCOT Website - Notice Type: Operational Information - Notice Priority: Low Typical ERCOT Website Posting: The Space Weather Prediction Center has issued a GMD Warning of [state level] until [date and time]. Notify Operations Support to run power flow studies to identify 345kV transformers loaded above 70% and develop a mitigation plan if needed. |  |  |
| Extend | IF: - The Warning is extended or K level increases/decreases; THEN: - Post new message on the ERCOT Website and - Cancel the older message Typical ERCOT Website Posting: The Space Weather Prediction Center has extended the GMD Warning of [state level] until [date and time]. |  |  |
| Cancel | WHEN: - The Warning is no longer valid; THEN: - Cancel the ERCOT Website posting. |  |  |
| Alert (Current) | WHEN: - An Alert for a GMD is issued for K-7 and greater or G3 and greater, or the K level increases/decreases; THEN: - Instruct the Transmission & Security and Real-Time Operators to implement their GMD procedures to make additional postings and Hotline calls. |  |  |
| Extend | IF: - The Alert is extended or the K level is increased/decreases; THEN: - Instruct the Operators to extend the Alert and/or make notifications regarding storm severity. |  |  |
| Cancel | WHEN: - K levels drop below K7 or when the Warning is no longer valid; THEN: - Instruct the Operators to cancel the Advisory for the Alert. |  |  |
| Issues | IF: - Any TO reports an issue due to the GMD event; THEN: - Send e-mail to the following with the details - Operations Analysis - Operations Support - Shiftsupv |  |  |
| ### Gas Restrictions |  |  |  |
| 1 | Once notified by a QSE of gas restrictions - Send an e-mail to “Gas Company Notifications”. This will notify all appropriate ERCOT staff. |  |  |
| 2 | Determine: - If the gas restriction could impact electric power system adequacy or reliability, THEN: - Proceed to “Reports” procedure for NERC/DOE reporting requirements, AND - Consider discussing fuel switching with affected QSE for the generation that has this capability This data can be viewed at ERCOT SharePoint > System Operations – Control Center > Quick Links > Fuel Oil Capability |  |  |
| ### FFSSR Restocking Request |  |  |  |
| Initial Request | IF: - During or following the deployment of FFSS, the QSE for an FFSSR may request an approval from ERCOT to restock their fuel reserve to restore their FFSS capability. THEN: - Request the QSE to submit a written request to the ERCOT Shift Supervisors email. |  |  |
| Request Received | IF: - An email request is received; THEN: - Notify the Director Control Room Operations and/or Designee. |  |  |
| Log | Log all actions. |  |  |
| ### Remedial Action Schemes (RAS) |  |  |  |
| 1 | IF: - A Monthly RAS report is received by e-mail; THEN: - Forward reports to: - OPS Support Engineering - Operations Analysis - Shift Supervisors |  |  |

## 7.2	EEA Implementation Guideline

Procedure Purpose:  To provide general guidelines on the actions and sequence of steps required prior to and during an EEA event.

| Protocol Reference | 6.5.7.6.2.2(16) | 6.5.9.3.4(6) | 6.5.9.4 | 6.5.9.4.2 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.4.3 |  |  |  |
| Guide Reference | 4.5.3 | 4.5.3.1 | 4.5.3.2 | 4.5.3.3 |
|  | 4.5.3.4 |  |  |  |
| NERC Standard | EOP-011-2 R1, R1.1, R1.2, R1.2.2, R1.2.6, R2, R2.1, R2.2 |  |  |  |

| Version: 1 | Revision: 33 | Effective Date: December 29, 2023 |
| --- | --- | --- |

| Note | - ERCOT shall use the PRC and system frequency to determine the appropriate Emergency Notice and EEA levels. - Manually deploy Load Resources other than Controllable Load Resources providing ECRS or RRS before entering into an Energy Emergency Alert (EEA), to maintain a minimum 500 MWs of Physical Responsive Capability (PRC) reserves on Generation Resources. - ERCOT will declare an EEA Level 1 when PRC falls below 2,500 MW and is not projected to be recovered above 2,500 MW within 30 minutes without the use of the following actions that are prescribed for EEA Level 1 - ERCOT MAY immediately implement EEA Level 2 when clock-minute average system frequency falls below 59.91 Hz for 15 consecutive minutes. - ERCOT may immediately implement EEA Level 3 any time the clock-minute average system frequency falls below 59.91 Hz for 20 consecutive minutes OR when steady-state frequency falls below 59.8 Hz for any duration of time. - ERCOT SHALL immediately implement EEA Level 3 any time the steady-state frequency is below 59.5 Hz for any duration. |
| --- | --- |
| Note | Energy Storage Resources (ESR) are instructed to suspend charging. For ESRs, ERCOT shall issue the suspension instruction via a SCED Base Point instruction, or, if otherwise necessary, via a manual Dispatch Instruction. An ESR shall suspend charging unless it is providing Primary Frequency Response, has received a charging instruction via SCED Base Point, or is carrying Reg-Down and has received a charging instruction from LFC. However, an ESR co-located behind a POI with onsite generation that is incapable of exporting additional power to the ERCOT System may continue to charge as long as maximum output to the ERCOT System is maintained. |

Prior to entering EEA - To be considered when ERCOT anticipates entering an EEA Event or one is imminent

Action

- Media Appeal for voluntary energy conservation

- Commit available Resources that can respond in the timeframe of the emergency, including RMR

- Non-Spin deployed

- Request Large Load Curtailment Program

- 30 MIN & 10 MIN ERS deployed. This includes Weather-Sensitive if available and Time Periods TP3 & TP4 - Ensure XML deployment made prior to QSE hotline call

- Distribution voltage reduction, if deemed beneficial when EEA2 and/or EEA3 load shed is not anticipated

- TOs load management program deployed during June - September or when available during only in EEA 2 or EEA3 if not already self-deployed by TO

- TCEQ exercising enforcement discretion for exceedance of generating plants environmental limits

- ERCOT and the TO agree to use a 15-minute Rating - Identify the appropriate double-circuit contingency and constrain on the single-circuit contingency to make more generation available

- ERCOT notifies MISO or SPP to request one or more SWGRs be switched into ERCOT

Administrative tasks applicable to each step:

- Hotline calls made

- NXT System activated

- ERCOT Website message posted

- SPP RC Notified

- RCIS Posting

- Ensure 3-part communication is used

- Update EEA Dashboard, if EEA3 update Load Shed amounts each time it changes

- Ensure ERS XML deployment made prior to QSE hotline call with time period changes

EEA Level 1 Implementation

- PRC <2500 MW and is not projected to be recovered above 2500 MW within 30 minutes without the use of EEA Level 1

- EMS EEA Flag activated

- TCEQ exercising enforcement discretion for exceedance of generating plants environmental limits

- Non-Spin deployed if not already deployed

- SCED dispatchable ECRS released, if not already released

- 30 MIN ERS deployed, if deploying in Level 1. This includes Weather-Sensitive if available and Time Periods TP3 & TP4 if not already deployed - Ensure XML deployment made prior to QSE hotline call

- Resource testing suspended

- Online RMRs loaded to full output

- Emergency Energy procedures implemented across CENACE DC-Ties

- EEA 1 Schedule requested across SPP DC-Ties

- RUC VDI/electronic Dispatch Instruction confirmation, as appropriate/including EMR

- DOE-417 for public appeals

- PRC <2000, Manually released RRS

- If available, deploy the Resources providing ECRS using ONECRS Resource Status

EEA Level 2 Implementation

- Maintain steady state system frequency at a minimum of 59.91 Hz and maintain PRC above 1500 MW - ERCOT may immediately implement EEA Level 2 when the clock-minute average system frequency falls below 59.91 Hz for 15 consecutive minutes. - ERCOT will declare an EEA Level 2 when PRC <2000 MW or unable to maintain system frequency at a minimum of 59.91 Hz and is not projected to be recovered above 2000 MW within 30 minutes without the use of EEA Level 2

- Media Appeal for voluntary energy conservation (if not already issued)

- Load Resources deployed and/or ERS Resources (if not already deployed) - Group 0/ Group 0+1a/ Group 0+1a+1b/ Group 0+1a+1b+1c/ Group 0+1a+1b+1c+2/ Group 0+1a+1b+1c+2+3 (<2000MW) - All (<1500MW) - Ensure XML deployment made prior to QSE hotline call

- ERS deployed, if not already deployed. This includes Weather-Sensitive - Ensure XML deployment made prior to QSE hotline call

- ERCOT and the TO agree to use a 15-minute Rating - De-activate the appropriate double-circuit contingency and constrain on the single-circuit contingency to make more generation available

- TOs load management program deployed if not already deployed during June - September or when available

- Emergency Energy Procedures implemented across SPP DC-Ties

- TOs notified of Load Resource deployment

- Distribution voltage reduction, as appropriate if not already implemented.

- RUC VDI/electronic Dispatch Instruction confirmation, as appropriate/including EMR

EEA Level 3 Implemention FIRM LOAD SHED

- ERCOT may immediately implement EEA Level 3 when the clock-minute average system frequency falls below 59.91 Hz for 20 consecutive minutes. - ERCOT will declare an EEA Level 3 when PRC cannot be maintained above 1500 MW - PRC < 1500 MW and is not projected to be recovered above 1,500 MW within 30 minutes, or when the clock-minute average frequency falls below 59.91 Hz for 25 consecutive minutes OR when steady-state frequency falls below 59.8 Hz for any duration of time.

- Implement any measures associated with EEA Levels 1 and 2 that have not already been implemented

- Verify all ERS and Load Resources deployed prior to firm load shed - Ensure XML deployment made prior to QSE hotline call

- Energy Storage Resources (ESR) are instructed to suspend charging. For ESRs, ERCOT shall issue the suspension instruction via a SCED Base Point instruction, or, if otherwise necessary, via a manual Dispatch Instruction. An ESR shall suspend charging unless it is providing Primary Frequency Response, has received a charging instruction via SCED Base Point, or is carrying Reg-Down and has received a charging instruction from LFC. However, an ESR co-located behind a POI with onsite generation that is incapable of exporting additional power to the ERCOT System may continue to charge as long as maximum output to the ERCOT System is maintained.

- Firm Load shed ordered (100 MW blocks)

- QSEs notified of Firm Load shed

- Load shed achieved

## 7.7	Significant Weather Events

Procedure Purpose:  Monitor severe weather conditions for the ERCOT Region and regions outside of ERCOT which can arise with little or no warning that could potentially impact the ERCOT Grid.

| Protocol Reference | 3.1.4.6 | 6.3.2(3)(a)(ii) | 6.5.9.3.1 | 6.5.9.3.2(4) |
| --- | --- | --- | --- | --- |
|  | 6.5.9.3.4 |  |  |  |
| Guide Reference | 4.2.1 | 4.2.2 | 4.2.3 | 4.2.4 |
| NERC Standard | EOP-011-2 R1, R1.1, R1.2, R1.2.2, R1.2.6, R1.2.6.1, R2, R2.1, R2.2, R2.2.9, R2.2.9.1, R2.2.9.2 | TOP-001-5 R8 |  |  |

| Version: | Revision: 3 | Effective Date: December 29, 2023 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Note | - Significant weather events are those that do not meet the criteria of the extreme hot, extreme cold, hurricane, or tropical storm procedures - Significant weather events can consist of, but are not limited to the following: - Tornados - Strong straight-line winds - Flooding - Freezing precipitation - Wild Fires - The ERCOT Meteorologist may provide forecasts to supplement other Weather Service data information - The sequence of actions taken, or notifications issued may vary due to system conditions or other operational issues and it may be necessary to skip actions due to the severity of the situation. To the extent possible, and when prudent, actions that were skipped may be implemented at a later time or date |
| OCN/ Advisory/ Watch | When a significant weather event arises that could or does impact the ERCOT Region, ensure the proper notifications are issued. |
| Post | Coordinate with the Real-Time Operator for the posting of the notices on the ERCOT Website. |
| Issues | Notify the ERCOT Director Control Room Operations or Designee of any issues. |
| Log | Log all actions |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Frosch, Hartmann, Stone, and Barcalow | Preparers | November 10, 2010 |
| Frosch and Hartmann | Procedure writers and editors | November 29, 2010 |
| Frosch, Hartmann, and Moore | Procedure writers and editors | January 26, 2011 |
| Frosch and Hartmann | Procedure writers and editors | March 23, 2011 |
| Frosch and Hartmann | Procedure writers and editors | April 20, 2011 |
| Frosch and Hartmann | Procedure writers and editors | June 6, 2011 |
| Frosch and Hartmann | Procedure writers and editors | July 18, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 30, 2011 |
| Frosch and Hartmann | Procedure writers and editors | September 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | October 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 16, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | April 25, 2012 |
| Frosch and Hartmann | Procedure writers and editors | May 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | May 30, 2012 |
| Frosch and Hartmann | Procedure writers and editors | July 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | August 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | October 26, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 26, 2013 |
| Frosch and Hartmann | Procedure writers and editors | May 28, 2013 |
| Frosch and Hartmann | Procedure writers and editors | July 10, 2013 |
| Frosch and Hartmann | Procedure writers and editors | August 7, 2013 |
| Frosch and Hartmann | Procedure writers and editors | August 28, 2013 |
| Frosch and Hartmann | Procedure writers and editors | December 11, 2013 |
| Frosch and Hartmann | Procedure writers and editors | January 27, 2014 |
| Frosch, Gaddy, and Hartmann | Procedure writers and editors | April 1, 2014 |
| Frosch and Hartmann | Procedure writers and editors | May 27, 2014 |
| Frosch and Hartmann | Procedure writers and editors | July 29, 2014 |
| Frosch and Hartmann | Procedure writers and editors | September 29, 2014 |
| Frosch and Hartmann | Procedure writers and editors | December 10, 2014 |
| Frosch and Hartmann | Procedure writers and editors | February 25, 2015 |
| Frosch and Hartmann | Procedure writers and editors | March 25, 2015 |
| Frosch and Hartmann | Procedure writers and editors | April 29, 2015 |
| Frosch and Hartmann | Procedure writers and editors | July 13, 2015 |
| Frosch, Hartmann and Gaddy | Procedure writers and editors | September 25, 2015 |
| Frosch, Hartmann and Gaddy | Procedure writers and editors | December 22, 2015 |
| Frosch, Hartmann and Gaddy | Procedure writers and editors | February 23, 2016 |
| Hartmann and Gaddy | Procedure writers and editors | April 22, 2016 |
| Frosch, Hartmann and Gaddy | Procedure writers and editors | June 24, 2016 |
| Frosch, Hartmann and Gaddy | Procedure writers and editors | September 26, 2016 |
| Hartmann, Gaddy and Frosch | Procedure writers and editors | December 23, 2016 |
| Hartmann, Gaddy and Frosch | Procedure writers and editors | March 27, 2017 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | May 26, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | June 23, 2017 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | September 27, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | October 27, 2017 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | December 22, 2017 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | February 22, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | March 26, 2018 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | April 27, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | May 25, 2018 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | August 28, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | September 26, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | October 29, 2018 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | December 21, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | January 25, 2019 |
| Hartmann, Gaddy, Luker and Frosch | Procedure writers and editors | March 25, 2019 |
| Hartmann, Gaddy, and Luker | Procedure writers and editors | April 26, 2019 |
| Hartmann, Gaddy, and Pence | Procedure writers and editors | May 13, 2019 |
| Hartmann, Gaddy, and Pence | Procedure writers and editors | May 28, 2019 |
| Hartmann, Gaddy, Pence and Frosch | Procedure writers and editors | July 29, 2019 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | October 29, 2019 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | December 20, 2019 |
| Hartmann, Gaddy, Cyphers and Frosch | Procedure writers and editors | January 27, 2020 |
| Hartmann, Gaddy, Cyphers and Frosch | Procedure writers and editors | February 24, 2020 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | June 25, 2020 |

| Hartmann, Gaddy and Cyphers | Procedure writers and editors | August 28, 2020 |
| --- | --- | --- |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | September 23, 2020 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | October 26, 2020 |
| Hartmann, Gaddy, Cyphers, and Sheets | Procedure writers and editors | December 23, 2020 |
| Hartmann, Gaddy, Cyphers, and Sheets | Procedure writers and editors | March 26, 2021 |
| Hartmann, Gaddy, Cyphers, and Sheets | Procedure writers and editors | April 29, 2021 |
| Hartmann, Gaddy, Cyphers, and Sheets | Procedure writers and editors | July 8, 2021 |
| Hartmann, Gaddy, Cyphers, and Sheets | Procedure writers and editors | July 28, 2021 |
| Hartmann, Gaddy, and Cyphers | Procedure writers and editors | November 29, 2021 |
| Hartmann, Gaddy, and Cyphers | Procedure writers and editors | December 1, 2021 |
| Hartmann, Gaddy, Cyphers, and Frosch | Procedure writers and editors | December 17, 2021 |
| Hartmann, Gaddy, Cyphers, and Frosch | Procedure writers and editors | January 27, 2022 |
| Hartmann, Gaddy, Cyphers, and Frosch | Procedure writers and editors | February 24, 2022 |
| Hartmann, Gaddy, Cyphers, and Frosch | Procedure writers and editors | March 31, 2022 |
| Hartmann, Gaddy, and Cyphers | Procedure writers and editors | May 20, 2022 |
| Hartmann, Gaddy, Cyphers, and Frosch | Procedure writers and editors | July 25, 2022 |
| Hartmann, Gaddy, and Cyphers | Procedure writers and editors | October 3, 2022 |
| Hartmann, Gaddy, Cyphers, and Frosch | Procedure writers and editors | December 22, 2022 |
| Hartmann, Gaddy, and Cyphers | Procedure writers and editors | January 26, 2023 |
| Hartmann, Gaddy, Cyphers, and Herrera | Procedure writers and editors | March 27, 2023 |
| Hartmann, Gaddy, Cyphers and Luker | Procedure writers and editors | May 1, 2023 |
| Hartmann, Gaddy, Cyphers and Luker | Procedure writers and editors | June 5, 2023 |
| Hartmann, Gaddy, Cyphers and Luker | Procedure writers and editors | June 26, 2023 |
| Hartmann, Gaddy, Cyphers and Luker | Procedure writers and editors | July 26, 2023 |
| Hartmann, Cyphers and Luker | Procedure writers and editors | October 26, 2023 |
| Hartmann, Cyphers and Luker | Procedure writers and editors | November 2, 2023 |
| Hartmann, Cyphers, Luker and Frosch | Procedure writers and editors | December 20, 2023 |

Manual Change History

| Procedure | Ver/Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All Sections | 1.0 / 0 | New procedures for all sections for Nodal implementation | November 28, 2010 |
| 3.1 4.2 6.1 10.2 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Updated steps 1 and 5, deleted steps 6, 7 and 8 Updated VDI, Testing Rules and Retest Updated PUCT Daily Report step “Update Report”. Updated all steps of Texas RE Event Reporting. Updated Title (Dynamic Rating, SCED Status, EMBP, SE, RTCA or RLC Alarms), 1st Note and Monitor | December 1, 2010 |
| 3.2 3.3 3.7 4.2 6.1 10.2 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 2 1.0 / 2 - / 2 | Updated step 1,3 and added step 4 in “Capacity Monitoring” Updated step 4 Updated step No SCED Solution Updated VDI, Retest, and Notify, added Completion Updated step OE-417 Reporting Events in NERC, DOE Reporting and step 2 on GEO-Magnetic Disturbance (GMD) Updated step Monitor on “Dynamic Rating, SCED Status, EMBP, SE, RTCA or RLC Alarms” | January 31, 2011 |
| 3.2 5.3 5.5 6.1 7.2 7.3 9.2 | 1.0 / 2 1.0 / 1 1.0 / 1 1.0 / 3 1.0 / 1 1.0 / 1 1.0 / 1 | Updated step 3 “Capacity Monitoring” Updated step 1 & 3 Updated 1st note & step 2 Updated PUCT Daily Report, Texas RE Event Reporting & NXT Notification Updated EEA Checklist Updated EEA Restoration Checklist Added new steps “SAT modem testing” & updated NXT Tests | March 25, 2011 |
| 4.2 5.1 7.1 7.3 | 1.0 / 3 1.0 / 1 1.0 / 1 1.0 / 1 | Updated “Unannounced Resource Testing” 1st note Updated 2nd & 6th paragraphs Updated “System Disturbance” NERC, step 2 and “Degraded Weather” step 3 Updated Table | April 22, 2011 |
| 5.3 5.7 6.1 7.1 7.4 7.5 7.6 8.3 | 1.0 / 2 1.0 / 1 1.0 / 4 1.0 / 2 1.0 / 1 1.0 / 0 1.0 / 1 1.0 / 1 | Updated step 2 Updated all steps Updated all steps in Texas RE Event Reporting and NERC and DOE Reporting Updated steps in Degraded Weather Updated all steps Added new procedure Updated all steps Updated step 2 and deleted step 3 | June 8, 2011 |
| 3.6 4.1 4.2 6.1 7.2 7.3 9.2 | 1.0 / 1 1.0 / 1 1.0 / 4 1.0 / 5 1.0 / 1 1.0 / 1 1.0 / 2 | Updated step 3 Removed Initial Synchronization of New Resource Updated Testing Rules Updated step Event List Updated EEA Implementation Checklist Updated EEA Restoration Checklist Added Notice Builder test in Primary Control Center section | July 20, 2011 |
| 4.2 5.5 6.1 7.2 7.3 7.7 9.2 10.1 | 1.0 / 5 1.0 / 2 1.0 / 6 1.0 / 2 1.0 / 3 1.0 / 0 1.0 / 3 1.0 / 1 | Updated step Caution Updated 1st Note Updated step 1 in Texas RE Event Reporting and NXT Testing in NXT Notification Requirements Updated EEA Implementation checklist Updated EEA Restoration checklist Added Extreme Hot Weather Updated NXT Test in Alternate Control Center Updated step 3 | September 1, 2011 |
| 3.4 6.1 7.2 7.3 9.2 | 1.0 / 1 1.0 / 7 1.0 / 2 1.0 / 3 1.0 / 4 | Grammar changes Combined EEA 2A & B per NPRR 379 Updated to implement NPRR 379 Updated to implement NPRR 379 Updated Phone Test in Alternate Control Center | October 1, 2011 |
| 3.7 7.2 10.2 | 1.0 / 2 1.0 / 3 1.0 / 3 | Changed title & all steps Updated EEA checklist Updated 1st Note | November 1, 2011 |
| 3.3 6.2 6.3 | 1.0 / 2 1.0 / 1 1.0 / 1 | Updated all steps Updated step 2 Updated step 1 & 2 All procedures in this manual have been reviewed. | December 15, 2011 |
| 1.2 4.2 5.7 | - / 1 - / 6 - / 2 | Updated Scope Updated all steps of procedure Updated Market Participant Backup Control Center Transfer | January 19, 2012 |
| 2.1 3.3 3.4 3.7 3.8 4.1 4.2 5.3 5.6 5.8 6.1 7.1 9.1 9.2 10.2 | 1.0 / 1 1.0 / 3 1.0 / 2 1.0 / 3 1.0 / 1 1.0 / 2 1.0 / 7 1.0 / 3 1.0 / 1 1.0 / 1 1.0 / 8 1.0 / 3 1.0 / 1 1.0 / 5 1.0 / 4 | Updated paragraph 4 Updated Step 3 Updated Threat & Emergency Classifications & Desktop Guide reference Changed Shift Engineer to Operations Support Corrected grammar on step 1 Changed Shift Engineer to Operations Support Updated procedure Changed Shift Engineer to Operations Support Corrected grammar on step 2 Updated step 2 Updated Texas RE Event Reporting, OE-417 reporting & Desktop Guide reference Updated Desktop Guide reference Updated Desktop Guide reference Updated Desktop Guide reference Changed Shift Engineer to Operations Support and updated Desktop Guide reference | March 1, 2012 |
| 2.1 3.3 3.6 5.6 6.1 7.1 7.4 7.5 7.6 | 1.0 / 2 1.0 / 4 1.0 / 2 1.0 / 2 1.0 / 9 1.0 / 4 1.0 / 2 1.0 / 2 1.0 / 2 | Changed TSP/DSP to TO Updated 3rd Note Updated purpose Changed TSP to TO and Transmission Facility Updated step Update Report & changed ARR to PRC and ERCOT Morning Report Updated step NERC and Degraded Weather Updated OCN, Advisory, & Watch steps Deleted Cold Weather, not Extreme Cold Weather Section number changed, Added OCN, Advisory and Emergency Notice | May 1, 2012 |
| 3.2 | 1.0 / 3 | Updated to reflect changes in the TAC approved Non-Spin document | May 14, 2012 |
| 7.2 7.3 | 1.0 / 3 1.0 / 4 | Updated EILS to ERS per NPRR 451 & added TO load management program Updated EILS to ERS per NPRR 451 & added TO load management program | June 1, 2012 |
| 3.3 4.2 6.1 | 1.0 / 5 1.0 / 8 1.0 / 10 | Updated step 3 Added Desktop Guide to VDI reference Updated PUCT Daily Report, NERC and DOE Reporting and RCIS Posting | July 16, 2012 |
| 3.4 4.2 5.9 6.1 7.2 | 1.0 / 3 1.0 / 9 1.0 / 1 1.0 / 11 1.0 / 4 | Added CPT to procedure and Typical Subject line for e-mail Added Log to procedure Deleted Procedure Updated NERC and DOE Reporting Added 30 MIN ERS deployed to EEA 1 | August 29, 2012 |
| 2.2 3.1 5.3 6.1 7.6 9.1 | 1.0 / 1 1.0 / 2 1.0 / 4 1.0 / 12 1.0 / 3 1.0 / 2 | Added Hotline Call Communication Updated step 5 Updated and added Planned and Forced Outage sections. Added Weather Information section to PUCT Daily Report. Updated step 1 in NERC and DOE Reporting and ERCOT Morning Report section. Updated OCN, Advisory, & Watch Updated step E-mail All procedures in this manual have been reviewed. | November 1, 2012 |
| 3.2 3.3 3.4 3.5 3.6 3.7 3.8 4.1 5.2 5.3 5.5 5.6 5.8 6.1 6.2 6.3 7.4 7.5 7.6 8.3 8.6 9.2 10.1 10.2 11.0 | 1.0 / 4 1.0 / 6 1.0 / 4 1.0 / 1 1.0 / 3 1.0 / 4 1.0 / 2 1.0 / 3 1.0 / 1 1.0 / 5 1.0 / 3 1.0 / 3 1.0 / 2 1.0 / 13 1.0 / 2 1.0 / 2 1.0 / 3 1.0 / 3 1.0 / 4 1.0 / 2 1.0 / 1 1.0 / 6 1.0 / 2 1.0 / 5 1.0 / 1 | Updated step 1, Capacity Monitoring and deleted Reserve Monitoring Updated step 3 Updated notes and Management Notifications Updated purpose and step 1 Updated step 2 Updated step TCM & renamed LMP Map Delete procedure for large wind ramp events Updated step 1 Grammatical correction Updated step 3 Protective Relay or Equipment Failure Added MISO Reliability Coordinator Updated step 2 TO Temporary Equipment Limitation Notifications Updated purpose Updated step 1 Texas RE Event Reporting, Note and step 1 NERC and DOE Reporting, Loss of Firm Load NXT Notification Requirements, step 1 Weather Information section to ERCOT Morning Report, step 1 RMR Unexcused Misconduct Events, GMD, step 2 Gas Restrictions and added Special Protection Systems (SPSs) Deleted procedure Renamed to 6.2 and updated procedure Updated step Reporting Updated step Reporting Updated Log Updated step 2 Updated procedure Deleted Notice Builder Updated step 3 Updated step monitor, step 4 Building Security and Fire Alarms and step 3 Failure of the Emergency Generator Updated procedure Review New Communications from Manager and/or Control Room Operations Manager and step 4 Implement ERCOT Personnel and Company Standards | March 1, 2013 |
| 3.3 3.4 6.1 | 1.0 / 7 1.0 / 5 1.0 / 14 | Updated all steps Added 1st Note, deleted 2nd & 3rd Notes, Management Notification, updated QSE Notification, TO Notification Updated step Update Report | June 1, 2013 |
| 4.1 5.1 6.1 10.2 | 1.0 / 4 1.0 / 2 1.0 / 15 1.0 / 6 | Updated Ancillary Service Testing Coordination and added Coordinated Reactive Tests Added MISO Updated PUCT Daily Report & step 1 on NERC and DOE Reporting and added Note to NXT Notification Requirements Updated 1st Note and step #3 on Building Security and Fire Alarms | July 15, 2013 |
| 3.4 4.1 6.1 7.3 | 1.0 / 6 1.0 / 5 1.0 / 16 1.0 / 5 | Updated QSE Notification, TO Notification & Send E-mail Updated Coordinated Reactive Tests Added 7-Day Outlook, updated Event List on Texas RE Event Reporting & step 2 on GEO-Magnetic Disturbance (GMD) Updated table | August 9, 2013 |
| 3.3 | 1.0 / 8 | Removed HHGT TO reference | August 30, 2013 |
| 3.3 3.4 4.1 4.2 5.3 5.4 5.6 5.7 6.1 7.6 8.1 8.2 8.3 9.1 9.2 10.2 | 1.0 / 9 1.0 / 7 1.0 / 6 1.0 / 10 1.0 / 6 1.0 / 1 1.0 / 4 1.0 / 3 1.0 / 17 1.0 / 5 1.0 / 1 1.0 / 1 1.0 / 3 1.0 / 3 1.0 / 7 1.0 / 7 | Updated step 1 and Log Updated step Log Updated step Log Updated step Log Updated step 4, Planned Outage, Forced Outage and added Log Updated step Log Updated step Log Updated step 1 and added Log Updated step Update Report, TRE Event Reporting changed to Event Analysis Report and event list updated, and NERC and DOE Reporting updated Added step Issues and updated Log Updated step 3 and added Log Updated step 3, 5 and added Log Updated step 3 Updated step Log Updated steps Log Added step 4 and updated Log All procedures in this manual have been reviewed. | December 13, 2013 |
| 4.1 6.1 7.2 7.3 | 1.0 / 7 1.0 / 18 1.0 / 5 1.0 / 6 | Updated for NOGRR125 & OK to test on Coordinated Reactive Tests Updated NERC and DOE Reporting Updated EEA Implementation Checklist Updated EEA Restoration Checklist | January 29, 2014 |
| 3.2 4.2 5.5 6.1 6.2 | 1.0 / 5 1.0 / 11 1.0 / 4 1.0 / 19 1.0 / 3 | Updated VDI information Updated VDI information Updated Note Updated Update Report on PUCT Daily Report and step 1 on NERC and DOE Reporting Updated step 1 | April 4, 2014 |
| 2.2 7.1 | 1.0 / 2 1.0 / 5 | Added VDIs to Master QSEs Updated step 1 | June 1, 2014 |
| 4.2 6.1 6.2 7.2 | 1.0 / 12 1.0 / 20 1.0 / 4 1.0 / 6 | Updated 1st Note, Retest and added Demonstration Test Updated step Update Report Updated steps 1 & 4 Updated checklist | August 1, 2014 |
| 3.3 3.4 4.1 4.2 9.2 | 1.0 / 10 1.0 / 8 1.0 / 8 1.0 / 13 1.0 / 8 | Added step 2 Corrected spelling on Send E-mail Updated script for Unit Testing Added new reference Updated new section on Phone Tests | October 1, 2014 |
| 3.6 3.7 4.2 6.1 | 1.0 / 4 1.0 / 5 1.0 / 14 1.0 / 21 | Changed title and removed references to W-N Added step RTMONI Updated Testing Rules and Scripts Added 2nd note to NERC and DOE Reporting & updated GMD procedure All procedures in this manual have been reviewed | December 15, 2014 |
| 2.2 3.2 3.3 4.2 5.3 5.5 6.1 7.2 7.5 | 1.0 / 3 1.0 / 6 1.0 / 11 1.0 / 14 1.0 / 7 1.0 / 5 1.0 / 22 1.0 / 7 1.0 / 4 | Added Dispatch and VDI definitions Updated step 4 Updated step 1 in Suspected Sabotage or Sabotage Events Moved procedure to Resource desk Updated title and added Protection System Setting Notifications Added Switchable Generation Resource Added Unit Trip Posting Updated checklist Updated Note | March 1, 2015 |
| 5.3 6.1 | 1.0 / 8 1.0 / 23 | Clarification to step 2 Clarifications to GMD procedure | March 30, 2015 |
| 3.3 3.4 3.6 3.7 4.1 5.6 6.1 6.2 7.6 8.3 8.6 10.1 10.2 11 | 1.0 / 12 1.0 / 9 1.0 / 5 1.0 / 6 1.0 / 9 1.0 / 5 1.0 / 24 1.0 / 5 1.0 / 6 1.0 / 4 1.0 / 2 1.0 / 3 1.0 / 8 1.0 / 2 | Updated contact information Updated contact information Updated contact information Updated contact information Updated contact information Updated contact information Updated contact information Updated contact information Updated contact information Updated contact information Updated contact information Updated contact information Updated contact information Updated contact information | May 1, 2015 |
| 6.1 10.2 | 1.0 / 25 1.0 / 9 | Updated GMD procedure Added new Telemetering, Control Equipment and Communication Outages process | July 15, 2015 |
| 9.1 9.2 9.3 9.4 | 1.0 / 0 1.0 / 0 1.0 / 9 1.0 / 4 | New procedure for COM-001-2 New procedure for COM-001-2 Updated procedure for COM-001-2 Updated section number | October 1, 2015 |
| 6.1 7.2 9.3 | 1.0 / 26 1.0 / 8 1.0 / 10 | Updated Event Analysis Reporting step Event List Implement NPRR708 for EEA Added Primary Control Center step Replacement/Alternative Device Examples Added Alternate Control System step Replacement/Alternative Device Examples All procedures in this manual have been reviewed | December 31, 2015 |
| 2.1 6.1 | 1.0 / 3 1.0 / 27 | Updated System Operator Responsibility and Authority Updated Guidelines for Determining EEA Potential | March 1, 2016 |
| 5.3 10.2 | 1.0 / 9 1.0 / 10 | Updated Protective Relay or Equipment Failure step 2 Deleted step 2 and updated step 3 | April 29, 2016 |
| 2.1 2.2 3.2 4.1 5.3 7.2 7.3 8.2 8.6 10.2 | 1.0 / 4 1.0 / 4 1.0 / 7 1.0 / 10 1.0 / 10 1.0 / 9 1.0 / 7 1.0 / 2 1.0 / 3 1.0 / 11 | Updated steps for COM-002-4 Updated steps for COM-002-4 Updated steps for COM-002-4 Updated steps for COM-002-4 Updated Protection System Setting Notification Updated steps for COM-002-4 Updated steps for COM-002-4 Updated steps for COM-002-4 Updated steps for COM-002-4 Updated steps for COM-002-4 | June 30, 2016 |
| 3.3 6.1 7.2 10.1 | 1.0 / 13 1.0 / 28 1.0 / 9 1.0 / 4 | Updated step Updated Step 1 of NERC and DOE Reporting Updated checklist Updated step 2 | September 30, 2016 |
| 3.3 4.1 5.5 6.1 | 1.0 / 14 1.0 / 11 1.0 / 6 1.0 / 29 | Updated Note Added Unit Testing Note Updated Approved Resources to be ONTEST Step Approval Deleted Turbine Governor Updated Note, renamed SPS to RAS & updated RAS Updated Event Analysis Reporting Step Event List, Event Reporting EOP-004-2 & Step 1 Renamed Special Protection Systems (SPS) to Remedial Action Schemes (RAS) & updated Remedial Action Schemes (RAS) All procedures in this manual have been reviewed | December 30, 2016 |
| 2.1 3.4 4.1 5.1 5.3 5.4 5.5 5.6 5.7 5.9 6.1 7.2 7.6 9.1 9.2 9.3 10.2 | 1.0 / 5 1.0 / 10 1.0 / 12 1.0 / 3 1.0 / 11 1.0 / 2 1.0 / 7 1.0 / 6 1.0 / 4 1.0 / 0 1.0 / 30 1.0 / 10 1.0 / 7 1.0 / 1 1.0 / 1 1.0 / 11 1.0 / 12 | Updated for IRO-001-4 Updated Threat & Emergency Classifications step Updated In Service Approval step 1 Deleted paragraph to create new procedure in 5.9 Updated CFE to CENACE Updated Protective Relay Outages step Updated second note, step 5 & 6 Updated CFE to CENACE Updated TO Temporary Equipment Limitation Notifications step 2 Updated Heading title and step 1 New procedure for IRO-002-4 R2 Updated with Event Analysis v3.1 changes and EOP-004-3 and EOP-011 Updated checklist Updated title Updated step 1 Updated step 2 Updated Satellite Modem Updated TOs, QSEs along with Telemetering, Control Equipment and Communication Outages | March 31, 2017 |
| 1.1 3.2 5.3 7.2 9.1 | 1.0 / 1 1.0 / 8 1.0 / 12 1.0 / 11 1.0 / 2 | Updated Purpose to add Reliability Risk desk Updated Capacity Monitoring step 3 & 4 Updated step 3 and Protective Relay Outages Updated EEA 3 checklist Updated Interpersonal Communication | June 1, 2017 |
| 7.2 | 1.0 / 12 | Updated checklist | June 30, 2017 |
| 9.1 | 1.0 / 3 | Updated steps & deleted Note | September 29, 2017 |
| 9.3 | 1.0 / 12 | Updated 1st Weekend of Every Month | October 31, 2017 |
| 6.1 7.1 8.6 | 1.0 / 31 1.0 / 6 1.0 / 4 | All procedures in this manual have been reviewed Updated PUCT Daily Report step Update Report Updated System Disturbance step NERC Updated Root Cause Analysis step NOTE | December 28, 2017 |
| 6.1 7.2 9.3 10.2 | 1.0 / 32 1.0 / 13 1.0 / 13 1.0 / 13 | Updated NERC and DOE Reporting OE-417 Reporting Events Updated Checklist Added Form an Email steps Updated step 1 & 2 | February 28, 2018 |
| 6.1 10.2 | 1.0 / 33 1.0 / 14 | Updated NERC and DOE Reporting step OE-417 Reporting Events Updated Title & EMS Alarm Heartbeat, Dynamic Rating, SCED Status, EMBP, SE, RTCA or RLC Alarms steps note and Monitor | March 30, 2018 |
| 2.2 7.2 7.3 | 1.0 / 5 1.0 / 14 1.0 / 8 | Updated procedure purpose Updated Checklist Updated Checklist | May 1, 2018 |
| 5.5 | 1.0 / 8 | Update EEA and Switchable Generation Resource | May 31, 2018 |
| 3.2 6.1 7.2 9.3 9.4 | 1.0 / 9 1.0 / 34 1.0 / 15 1.0 / 14 1.0 / 5 | Added step 2 & Log, updated step 3 and renumbered 2, 3 &4 Deleted 7-Day Outlook Report Updated Checklist Multiple changes to clarify the roles and responsibilities Updated forms | August 31, 2018 |
| 5.5 6.1 | 1.0 / 9 1.0 / 35 | Removed Monticello RAS Removed Reportable Balancing Contingency Event from the PUCT Daily Report update and updated step 1 on the ERCOT Morning Report | October 1, 2018 |
| 6.1 | 1.0 / 36 | Updated PUCT Daily Report | November 1, 2018 |
| 9.1 9.2 9.3 | 1.0 / 4 1.0 / 2 1.0 / 15 | Updated Alternative Interpersonal Communication Updated step 1 & 2 Clarified notification times All procedures in this manual have been reviewed | December 28, 2018 |
| 7.2 | 1.0 / 16 | Updated Checklist | January 31, 2019 |
| 6.1 7.4 10.1 | 1.0 / 37 1.0 / 4 1.0 / 5 | Updated NERC and DOE Reporting Operating Plan Updated step Emergency Notice and added steps Issues and Log Updated steps and deleted note | March 29, 2019 |
| 3.7 4.1 | 1.0 / 7 1.0 / 13 | Added Note Updated Coordinated Reactive Tests step 2 | May 01, 2019 |
| 5.5 | - / 10 | Updated Sharyland to ONCOR DC Tie Desk Added step 3 and Typical Scripts to Switchable Generation Resource | May 16, 2019 |
| 5.5 6.1 7.2 | 1.0 / 11 1.0 / 38 1.0 / 17 | Updated Switchable Generation Resource steps Updated process Moved TOs load management from EEA1 to EEA2 | May 31, 2019 |
| 4.1 6.1 10.2 | 1.0 / 14 1.0 / 39 1.0 / 15 | Updated Coordinated Reactive Tests step 1 Added Note to PUCT Daily Report Updated NERC and DOE Reporting Operating Plan steps Updated Building Security and Fire Alarms step 2 | August 1, 2019 |
| 6.1 7.2 | 1.0 / 40 1.0 / 18 | Updated Remedial Action Schemes (RAS) step Updated Checklist | November 1, 2019 |
| 3.3 3.4 3.6 3.7 4.1 5.3 5.6 6.1 6.2 7.1 7.2 7.3 7.4 7.6 8.3 8.6 9.3 9.4 10.1 10.2 11 | 1.0 / 15 1.0 / 11 1.0 / 6 1.0 / 8 1.0 / 15 1.0 / 13 1.0 / 7 1.0 / 41 1.0 / 6 1.0 / 7 1.0 / 19 1.0 / 9 1.0 / 5 1.0 / 8 1.0 / 5 1.0 / 5 1.0 / 16 1.0 / 6 1.0 / 6 1.0 / 16 1.0 / 3 | Updated Suspected Sabotage or Sabotage Events Updated Note Updated step 2 Updated step LMP Map Updated Unit Testing step 1 Deleted step NERC Updated TO Temporary Equipment Limitation Notifications step 2 Updated steps Updated steps Updated NERC step Updated checklist Updated checklist Updated step Issues Updated step Issues Updated step 2 Updated steps Updated step Cell Phone Update Note and added issues step Updated step 3 Updated steps Updated Title and steps All procedures in this manual have been reviewed | January 1, 2020 |
| 3.2 3.7 7.4 7.5 9.1 9.2 9.3 9.4 | 1.0 / 10 1.0 / 9 1.0 / 6 1.0 / 5 1.0 / 5 1.0 / 3 1.0 / 17 1.0 / 7 | Clarified RUC commits/decommits Clarified RUC commits/decommits Clarified RUC commits/decommits Clarified RUC commits/decommits Updated AIC step Updated all steps Updated title and steps Updated title and steps | January 31, 2020 |
| 9.2 | 1.0 / 4 | Updated step 2 | February 28, 2020 |
| 2.1 3.2 | 1.0 / 6 1.0 / 11 | Added Advance Action Notice per NPRR930 Added Advance Action Notice section per NPRR930 | July 1, 2020 |
| 9.1 9.3 | 1.0 / 6 1.0 / 18 | Updated Nortel to Cisco Updated Nortel to Cisco | September 1, 2020 |
| 3.6 | 1.0 / 7 | Updated Title, Purpose and added new IROL’s | October 1, 2020 |
| 3.6 | 1.0 / 8 | Updated each step IROL and step 2 | October 31, 2020 |
| 3.2 3.5 5.4 5.5 6.1 7.2 7.3 10.2 | - / 12 - / 2 1.0 / 3 1.0 / 12 1.0 / 42 1.0 / 20 1.0 / 10 1.0 / 17 | Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1031 and NPRR1039 Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 All procedures in this manual have been reviewed | December 31, 2020 |
| 3.4 4.1 5.5 5.8 5.9 7.4 10.1 10.2 | 1.0 / 12 1.0 / 16 1.0 / 13 1.0 / 3 1.0 / 1 1.0 / 7 1.0 / 7 1.0 / 18 | Organization change Organization change Updated Note Updated procedure Organization change Organization change Organization change Organization change | April 1, 2021 |
| 3.6 5.5 7.5 | 1.0 / 9 1.0 / 14 1.0 / 6 | Removed McCamey IROL Changed Notice Builder to Grid Conditions Communications (GCC) Notices Updated Advisory & Watch | May 6, 2021 |
| 3.2 | 1.0 / 13 | Updated for OBDRR031 | July 12, 2021 |
| 3.2 6.1 | 1.0 / 14 1.0 / 43 | Updated for OBDRR031 Updated for NPRR1031 | July 31, 2021 |
| 3.2 7.2 | 1.0 / 15 1.0 / 21 | Updated Capacity Monitoring step 4 & AAN steps Updated for NPRR1105 & NPRR 1106 | December 1, 2021 |
| 7.2 | 1.0 / 22 | Updated for NOGRR236 | December 17, 2021 |
| 2.2 3.2 3.6 6.1 7.1 7.2 7.3 7.4 7.5 7.6 7.7 | - / 6 1.0 / 16 - / 10 - / 44 - / 9 - / 23 - / 11 - / 8 - / 7 - / 9 - / 0 | Updated step 1 Updated step 1 & step 4 Added McCamey Export Updated Gas Restrictions & DOE email address Updated Other Significant Weather Events Updated all steps Updated Level 1 & Level 2 Updated all steps Updated all steps Updated all steps Added new procedure All procedures in this manual have been reviewed | December 31, 2021 |
| 6.1 6.2 7.2 7.3 7.5 7.7 | - / 45 - / 7 1.0 / 24 1.0 / 12 1.0 / 8 1.0 / 1 | Updated NERC and DOE Reporting Operating Plan with DOE-417 reporting changes Updated OE-417 to DOE-417 Updated steps Updated steps Corrected typo Updated Note | February 1, 2022 |
| 3.3 | 1.0 / 16 | Updated for Cyber Event | March 1, 2022 |
| 5.9 9.2 10.1 10.2 | 1.0 / 2 1.0 / 5 1.0 / 8 1.0 / 19 | Added Note Updated step 2 Added Note Added Note | April 7, 2022 |
| 3.2 7.2 | 1.0 / 17 1.0 / 25 | Updated for NPRR1093 Updated for NPRR939, NPRR1093 & NOGRR191 | May 26, 2022 |
| 7.2 7.3 7.6 | 1.0 / 26 1.0 /13 1.0 / 10 | Added version history Added version history Updated Note | July 29, 2022 |
| 10.2 | 1.0 / 20 | Updated EMS Heartbeat Alarm note | October 7, 2022 |
| 3.2 6.1 7.2 | 1.0 / 18 1.0 / 6 1.0 / 27 | Updated Capacity Monitoring and Added Large Load Curtailment Program Added FFSSR Restocking Request Updated Prior to Entering EEA guideline All procedures in this manual have been reviewed | December 30, 2022 |
| 3.2 | 1.0 / 19 | Updated Large Load Curtailment Program | February 1, 2023 |
| 7.1 7.5 7.6 7.7 | 1.0 / 10 1.0 / 9 1.0 / 11 1.0 / 2 | Updated procedure title and first step Updated steps for Extreme Weather Monitor Updated steps for Extreme Weather Monitor Updated procedure title | March 31, 2023 |
| 3.4 | 1.0 / 13 | Updated Phone Number | May 4, 2023 |
| 7.2 7.3 | 1.0 / 28 1.0 / 14 | Updated for NPRR863 Updated for NPRR863 | June 9, 2023 |
| 3.3 7.2 | 1.0 / 17 1.0 / 29 | Updated SSRG Hotline script Updated deployed to released | June 30, 2023 |
| 6.1 7.2 | 1.0 / 7 1.0 / 30 | Updated Note for PUCT Report Updated For NPRR1143 | August 1, 2023 |
| 6.1 7.2 | 1.0 / 8 1.0 / 31 | Updated for NPRR1176 Updated for NPRR1176 | November 1, 2023 |
| 7.2 | 1.0 / 32 | Updated for NPRR1176 | November 7, 2023 |
| 6.1 7.2 7.7 | 1.0 / 9 1.0 / 33 1.0 / 3 | Updated Event Analysis Reporting Updated EEA Checklist Updated Note All procedures in this manual have been reviewed | December 29, 2023 |