- Power Operations Bulletin # 1134

ERCOT has posted/revised the Shift Supervisor Desk manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

## http://www.ercot.com/mktrules/guides/procedures/index.html

## 3.6	Monitoring IROL’s

Procedure Purpose: To collect data on the IROL’s stability limits for the NERC Reliability Metric. The actual flow should not be allowed to exceed the limit. If necessary, the System Operator has the authority to instruct load shedding or removing generation before this IROL has been exceeded.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | IRO-002-7 R5 | TOP-001-6 R12 |  |  |

| Version: 1 | Revision: 12 | Effective Date: March 29, 2024 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| IROL Comms | WHEN: - A TOs ICCP status indicates both links are down. ENSURE: - All appropriate steps are being conducted for manual communications as required in T/S procedure, section 3.8, “SOL Exceedance Communications, TO ICCP Links Down”. |
| ### North-Houston Import IROL |  |
| IROL | The North to Houston Import stability limit is an IROL; the actual flow MUST NOT be allowed to exceed its limit.. This is a violation of the NERC Reliability Standards. |
| NERC | Ensure that the transmission system is operated so that instability, uncontrolled separation, or cascading outages will not occur as a result of the most severe single Contingency and specified multiple Contingencies. |
| 1 | Monitor N-H voltage limits. |
| 2 | If the N-H Import voltage stability exceeds the limit at any time: - Log it under log type “Exceeding Limits”. - Include the date and time of the violation - The system conditions that caused the violation. - Run a System Security Analysis (Real Time Snapshot) Study near the highest flow. (usually run by the Operations Support Engineer) - Save the snapshot in the STNET directory. If the N-H voltage stability limit is exceeded, notify the Director Control Room Operations and/or Designee immediately. |
| 3 | Notify by e-mail (including data from step 2) - Shift Supervisors - Ops Support Engineering - Operations Analysis |

| ### Valley Import IROL |  |
| --- | --- |
| IROL | The Valley Import is an IROL; the actual flow MUST NOT be allowed to exceed its limit.. This is a violation of the NERC Reliability Standards. |
| NERC | Ensure that the transmission system is operated so that instability, uncontrolled separation, or cascading outages will not occur as a result of the most severe single Contingency and specified multiple Contingencies. |
| 1 | Monitor Valley Import limits. |
| 2 | If the Valley Import stability exceeds the limit at any time: - Log it under log type “Exceeding Limits”. - Include the date and time of the violation - The system conditions that caused the violation. - Run a System Security Analysis (Real Time Snapshot) Study near the highest flow. (usually run by the Operations Support Engineer) - Save the snapshot in the STNET directory. If the Valley Import stability limit is exceeded, notify the Director Control Room Operations and/or Designee immediately. |
| 3 | Notify by e-mail (including data from step 2) - Shift Supervisors - Ops Support Engineering - Operations Analysis |

| ### West Texas Export IROL |  |
| --- | --- |
| IROL | The West Texas Export is an IROL; the actual flow MUST NOT be allowed to exceed its limit. This is a violation of the NERC Reliability Standards. |
| NERC | Ensure that the transmission system is operated so that instability, uncontrolled separation, or cascading outages will not occur as a result of the most severe single Contingency and specified multiple Contingencies. |
| 1 | Monitor West Texas Export limits. |
| 2 | If the West Texas Export stability exceeds the limit at any time: - Log it under log type “Exceeding Limits”. - Include the date and time of the violation - The system conditions that caused the violation. - Run a System Security Analysis (Real Time Snapshot) Study near the highest flow. (usually run by the Operations Support Engineer) - Save the snapshot in the STNET directory. If the West Texas Export stability limit is exceeded, notify the Director Control Room Operations and/or Designee immediately. |
| 3 | Notify by e-mail (including data from step 2) - Shift Supervisors - Ops Support Engineering - Operations Analysis |

| ### Panhandle Export IROL |  |
| --- | --- |
| IROL | The Panhandle Export is an IROL; the actual flow MUST NOT be allowed to exceed its limit. This is a violation of the NERC Reliability Standards. |
| NERC | Ensure that the transmission system is operated so that instability, uncontrolled separation, or cascading outages will not occur as a result of the most severe single Contingency and specified multiple Contingencies. |
| 1 | Monitor Panhandle Export limits. |
| 2 | If the Panhandle Export stability exceeds the limit at any time: - Log it under log type “Exceeding Limits”. - Include the date and time of the violation - The system conditions that caused the violation. - Run a System Security Analysis (Real Time Snapshot) Study near the highest flow. (usually run by the Operations Support Engineer) - Save the snapshot in the STNET directory. If the Panhandle Export stability limit is exceeded, notify the Director Control Room Operations and/or Designee immediately. |
| 3 | Notify by e-mail (including data from step 2) - Shift Supervisors - Ops Support Engineering - Operations Analysis |
| ### McCamey Export IROL |  |
| IROL | The McCamey Export is an IROL; the actual flow MUST NOT be allowed to exceed its limit. This is a violation of the NERC Reliability Standards. |
| NERC | Ensure that the transmission system is operated so that instability, uncontrolled separation, or cascading outages will not occur as a result of the most severe single Contingency and specified multiple Contingencies. |
| 1 | Monitor McCamey Export limits. |
| 2 | If the McCamey Export stability exceeds the limit at any time: - Log it under log type “Exceeding Limits”. - Include the date and time of the violation - The system conditions that caused the violation. - Run a System Security Analysis (Real Time Snapshot) Study near the highest flow. (usually run by the Operations Support Engineer) - Save the snapshot in the STNET directory. If the McCamey Export stability limit is exceeded, notify the Director Control Room Operations and/or Designee immediately. |
| 3 | Notify by e-mail (including data from step 2) - Shift Supervisors - Ops Support Engineering - Operations Analysis |

| ### South Texas Export IROL |  |
| --- | --- |
| IROL | The South Texas Export is an IROL; the actual flow MUST NOT be allowed to exceed its limit. This is a violation of the NERC Reliability Standards. |
| NERC | Ensure that the transmission system is operated so that instability, uncontrolled separation, or cascading outages will not occur as a result of the most severe single Contingency and specified multiple Contingencies. |
| 1 | Monitor South Texas Export limits. |
| 2 | If the South Texas Export stability exceeds the limit at any time: - Log it under log type “Exceeding Limits”. - Include the date and time of the violation - The system conditions that caused the violation. - Run a System Security Analysis (Real Time Snapshot) Study near the highest flow. (usually run by the Operations Support Engineer) - Save the snapshot in the STNET directory. If the South Texas Export stability limit is exceeded, notify the Director Control Room Operations and/or Designee immediately. |
| 3 | Notify by e-mail (including data from step 2) - Shift Supervisors - Ops Support Engineering - Operations Analysis |
| ### South Texas Import IROL |  |
| IROL | The South Texas Import is an IROL; the actual flow MUST NOT be allowed to exceed its limit. This is a violation of the NERC Reliability Standards. |
| NERC | Ensure that the transmission system is operated so that instability, uncontrolled separation, or cascading outages will not occur as a result of the most severe single Contingency and specified multiple Contingencies. |
| 1 | Monitor South Texas Import limits. |
| 2 | If the South Texas Import stability exceeds the limit at any time: - Log it under log type “Exceeding Limits”. - Include the date and time of the violation - The system conditions that caused the violation. - Run a System Security Analysis (Real Time Snapshot) Study near the highest flow. (usually run by the Operations Support Engineer) - Save the snapshot in the STNET directory. If the South Texas Import stability limit is exceeded, notify the Director Control Room Operations and/or Designee immediately. |
| 3 | Notify by e-mail (including data from step 2) - Shift Supervisors - Ops Support Engineering - Operations Analysis |

## 3.7	Monitoring Transmission Congestion

Procedure Purpose:  Monitoring transmission congestion to ensure ERCOT remains in a secure state.

| Protocol Reference | 6.3(3) |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 3.7 (2) |  |  |  |
| NERC Standard | IRO-008-3 R5, R6 |  |  |  |

| Version: 1 | Revision: 10 | Effective Date: March 29, 2024 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| TCM | VERIFY: - Constraints with a 2% shift factor or greater are activated at 98%. IF: - A constraint is unsolved in SCED; ENSURE: - All appropriate steps have been taken to resolve (T/S desk section 4.1 Managing Constraints in SCED step 2) IF: - Constraint remains unsolved in SCED; ENSURE: - The Operations Support Engineer is developing a TOAP or MP. IF: - A post-contingency overload reaches 125%; ENSURE: - The Operations Support Engineer has validated whether it is an IROL. |
| RTMONI | VERIFY: - The GTLs in RTMONI are being updated in a timely manner. - Assign this task to another desk if needed |
| LMP Map | Monitor the real-time LMP map: IF: - Any LMP appears unreasonable; THEN: - Notify Director Control Room Operations or Designee, and - Ensure transmission congestion is solvable and not being over-constrained. |
| South DC Ties | Ensure all available generation has been RUC committed and the constraint binding before curtailing any South DC-Ties. Curtail only enough to maximize the flow across the South DC-Ties at all times. |
| SOL Comms | Monitor the SOL Exceedance tool: WHEN: - Notified the MIS Posting of System Limit Exceedances AND Grid Geo are unavailable; ENSURE: - All appropriate steps are being conducted for manual communications as required in T/S procedure, section 3.8, “SOL Exceedance Communications, Both Methods of Electronic Communication are unavailable”. WHEN: - A TO reports both its MIS Posting of System Limit Exceedances AND Grid Geo are unavailable; AND: - The MIS Posting of System Limit Exceedances AND Grid Geo are available on the ERCOT side; ENSURE: - All appropriate steps are being conducted for manual communications as required in T/S procedure, section 3.8, “SOL Exceedance Communication Thresholds”, when a TO reports both methods of System Limit Exceedances are unavailable”. IF: - Manual communications are required during a declared Watch or Emergency, or when there are multiple high priority tasks; an exception to the timeframe of SOL exceedance communication may be utilized if needed; THEN: - Log the exception, and why it is being used; ENSURE: - Manual communications are made as required in the T/S procedure, section 3.8, “SOL Exceedance Communications Thresholds”, as timely as possible. |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Frosch, Hartmann, Stone, and Barcalow | Preparers | November 10, 2010 |
| Frosch and Hartmann | Procedure writers and editors | November 29, 2010 |
| Frosch, Hartmann, and Moore | Procedure writers and editors | January 26, 2011 |
| Frosch and Hartmann | Procedure writers and editors | March 23, 2011 |
| Frosch and Hartmann | Procedure writers and editors | April 20, 2011 |
| Frosch and Hartmann | Procedure writers and editors | June 6, 2011 |
| Frosch and Hartmann | Procedure writers and editors | July 18, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 30, 2011 |
| Frosch and Hartmann | Procedure writers and editors | September 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | October 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 16, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | April 25, 2012 |
| Frosch and Hartmann | Procedure writers and editors | May 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | May 30, 2012 |
| Frosch and Hartmann | Procedure writers and editors | July 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | August 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | October 26, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 26, 2013 |
| Frosch and Hartmann | Procedure writers and editors | May 28, 2013 |
| Frosch and Hartmann | Procedure writers and editors | July 10, 2013 |
| Frosch and Hartmann | Procedure writers and editors | August 7, 2013 |
| Frosch and Hartmann | Procedure writers and editors | August 28, 2013 |
| Frosch and Hartmann | Procedure writers and editors | December 11, 2013 |
| Frosch and Hartmann | Procedure writers and editors | January 27, 2014 |
| Frosch, Gaddy, and Hartmann | Procedure writers and editors | April 1, 2014 |
| Frosch and Hartmann | Procedure writers and editors | May 27, 2014 |
| Frosch and Hartmann | Procedure writers and editors | July 29, 2014 |
| Frosch and Hartmann | Procedure writers and editors | September 29, 2014 |
| Frosch and Hartmann | Procedure writers and editors | December 10, 2014 |
| Frosch and Hartmann | Procedure writers and editors | February 25, 2015 |
| Frosch and Hartmann | Procedure writers and editors | March 25, 2015 |
| Frosch and Hartmann | Procedure writers and editors | April 29, 2015 |
| Frosch and Hartmann | Procedure writers and editors | July 13, 2015 |
| Frosch, Hartmann and Gaddy | Procedure writers and editors | September 25, 2015 |
| Frosch, Hartmann and Gaddy | Procedure writers and editors | December 22, 2015 |
| Frosch, Hartmann and Gaddy | Procedure writers and editors | February 23, 2016 |
| Hartmann and Gaddy | Procedure writers and editors | April 22, 2016 |
| Frosch, Hartmann and Gaddy | Procedure writers and editors | June 24, 2016 |
| Frosch, Hartmann and Gaddy | Procedure writers and editors | September 26, 2016 |
| Hartmann, Gaddy and Frosch | Procedure writers and editors | December 23, 2016 |
| Hartmann, Gaddy and Frosch | Procedure writers and editors | March 27, 2017 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | May 26, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | June 23, 2017 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | September 27, 2017 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | October 27, 2017 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | December 22, 2017 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | February 22, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | March 26, 2018 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | April 27, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | May 25, 2018 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | August 28, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | September 26, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | October 29, 2018 |
| Hartmann, Gaddy, Ballew and Frosch | Procedure writers and editors | December 21, 2018 |
| Hartmann, Gaddy and Ballew | Procedure writers and editors | January 25, 2019 |
| Hartmann, Gaddy, Luker and Frosch | Procedure writers and editors | March 25, 2019 |
| Hartmann, Gaddy, and Luker | Procedure writers and editors | April 26, 2019 |
| Hartmann, Gaddy, and Pence | Procedure writers and editors | May 13, 2019 |
| Hartmann, Gaddy, and Pence | Procedure writers and editors | May 28, 2019 |
| Hartmann, Gaddy, Pence and Frosch | Procedure writers and editors | July 29, 2019 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | October 29, 2019 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | December 20, 2019 |
| Hartmann, Gaddy, Cyphers and Frosch | Procedure writers and editors | January 27, 2020 |
| Hartmann, Gaddy, Cyphers and Frosch | Procedure writers and editors | February 24, 2020 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | June 25, 2020 |

| Hartmann, Gaddy and Cyphers | Procedure writers and editors | August 28, 2020 |
| --- | --- | --- |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | September 23, 2020 |
| Hartmann, Gaddy and Cyphers | Procedure writers and editors | October 26, 2020 |
| Hartmann, Gaddy, Cyphers, and Sheets | Procedure writers and editors | December 23, 2020 |
| Hartmann, Gaddy, Cyphers, and Sheets | Procedure writers and editors | March 26, 2021 |
| Hartmann, Gaddy, Cyphers, and Sheets | Procedure writers and editors | April 29, 2021 |
| Hartmann, Gaddy, Cyphers, and Sheets | Procedure writers and editors | July 8, 2021 |
| Hartmann, Gaddy, Cyphers, and Sheets | Procedure writers and editors | July 28, 2021 |
| Hartmann, Gaddy, and Cyphers | Procedure writers and editors | November 29, 2021 |
| Hartmann, Gaddy, and Cyphers | Procedure writers and editors | December 1, 2021 |
| Hartmann, Gaddy, Cyphers, and Frosch | Procedure writers and editors | December 17, 2021 |
| Hartmann, Gaddy, Cyphers, and Frosch | Procedure writers and editors | January 27, 2022 |
| Hartmann, Gaddy, Cyphers, and Frosch | Procedure writers and editors | February 24, 2022 |
| Hartmann, Gaddy, Cyphers, and Frosch | Procedure writers and editors | March 31, 2022 |
| Hartmann, Gaddy, and Cyphers | Procedure writers and editors | May 20, 2022 |
| Hartmann, Gaddy, Cyphers, and Frosch | Procedure writers and editors | July 25, 2022 |
| Hartmann, Gaddy, and Cyphers | Procedure writers and editors | October 3, 2022 |
| Hartmann, Gaddy, Cyphers, and Frosch | Procedure writers and editors | December 22, 2022 |
| Hartmann, Gaddy, and Cyphers | Procedure writers and editors | January 26, 2023 |
| Hartmann, Gaddy, Cyphers, and Herrera | Procedure writers and editors | March 27, 2023 |
| Hartmann, Gaddy, Cyphers and Luker | Procedure writers and editors | May 1, 2023 |
| Hartmann, Gaddy, Cyphers and Luker | Procedure writers and editors | June 5, 2023 |
| Hartmann, Gaddy, Cyphers and Luker | Procedure writers and editors | June 26, 2023 |
| Hartmann, Gaddy, Cyphers and Luker | Procedure writers and editors | July 26, 2023 |
| Hartmann, Cyphers and Luker | Procedure writers and editors | October 26, 2023 |
| Hartmann, Cyphers and Luker | Procedure writers and editors | November 2, 2023 |
| Hartmann, Cyphers, Luker and Frosch | Procedure writers and editors | December 20, 2023 |
| Hartmann, Cyphers, Luker and Frosch | Procedure writers and editors | February 27, 2024 |
| Hartmann, Cyphers, Luker, Frosch, and Smith | Procedure writers and editors | March 26, 2024 |

Manual Change History

| Procedure | Ver/Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All Sections | 1.0 / 0 | New procedures for all sections for Nodal implementation | November 28, 2010 |
| 3.1 4.2 6.1 10.2 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Updated steps 1 and 5, deleted steps 6, 7 and 8 Updated VDI, Testing Rules and Retest Updated PUCT Daily Report step “Update Report”. Updated all steps of Texas RE Event Reporting. Updated Title (Dynamic Rating, SCED Status, EMBP, SE, RTCA or RLC Alarms), 1st Note and Monitor | December 1, 2010 |
| 3.2 3.3 3.7 4.2 6.1 10.2 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 2 1.0 / 2 - / 2 | Updated step 1,3 and added step 4 in “Capacity Monitoring” Updated step 4 Updated step No SCED Solution Updated VDI, Retest, and Notify, added Completion Updated step OE-417 Reporting Events in NERC, DOE Reporting and step 2 on GEO-Magnetic Disturbance (GMD) Updated step Monitor on “Dynamic Rating, SCED Status, EMBP, SE, RTCA or RLC Alarms” | January 31, 2011 |
| 3.2 5.3 5.5 6.1 7.2 7.3 9.2 | 1.0 / 2 1.0 / 1 1.0 / 1 1.0 / 3 1.0 / 1 1.0 / 1 1.0 / 1 | Updated step 3 “Capacity Monitoring” Updated step 1 & 3 Updated 1st note & step 2 Updated PUCT Daily Report, Texas RE Event Reporting & NXT Notification Updated EEA Checklist Updated EEA Restoration Checklist Added new steps “SAT modem testing” & updated NXT Tests | March 25, 2011 |
| 4.2 5.1 7.1 7.3 | 1.0 / 3 1.0 / 1 1.0 / 1 1.0 / 1 | Updated “Unannounced Resource Testing” 1st note Updated 2nd & 6th paragraphs Updated “System Disturbance” NERC, step 2 and “Degraded Weather” step 3 Updated Table | April 22, 2011 |
| 5.3 5.7 6.1 7.1 7.4 7.5 7.6 8.3 | 1.0 / 2 1.0 / 1 1.0 / 4 1.0 / 2 1.0 / 1 1.0 / 0 1.0 / 1 1.0 / 1 | Updated step 2 Updated all steps Updated all steps in Texas RE Event Reporting and NERC and DOE Reporting Updated steps in Degraded Weather Updated all steps Added new procedure Updated all steps Updated step 2 and deleted step 3 | June 8, 2011 |
| 3.6 4.1 4.2 6.1 7.2 7.3 9.2 | 1.0 / 1 1.0 / 1 1.0 / 4 1.0 / 5 1.0 / 1 1.0 / 1 1.0 / 2 | Updated step 3 Removed Initial Synchronization of New Resource Updated Testing Rules Updated step Event List Updated EEA Implementation Checklist Updated EEA Restoration Checklist Added Notice Builder test in Primary Control Center section | July 20, 2011 |
| 4.2 5.5 6.1 7.2 7.3 7.7 9.2 10.1 | 1.0 / 5 1.0 / 2 1.0 / 6 1.0 / 2 1.0 / 3 1.0 / 0 1.0 / 3 1.0 / 1 | Updated step Caution Updated 1st Note Updated step 1 in Texas RE Event Reporting and NXT Testing in NXT Notification Requirements Updated EEA Implementation checklist Updated EEA Restoration checklist Added Extreme Hot Weather Updated NXT Test in Alternate Control Center Updated step 3 | September 1, 2011 |
| 3.4 6.1 7.2 7.3 9.2 | 1.0 / 1 1.0 / 7 1.0 / 2 1.0 / 3 1.0 / 4 | Grammar changes Combined EEA 2A & B per NPRR 379 Updated to implement NPRR 379 Updated to implement NPRR 379 Updated Phone Test in Alternate Control Center | October 1, 2011 |
| 3.7 7.2 10.2 | 1.0 / 2 1.0 / 3 1.0 / 3 | Changed title & all steps Updated EEA checklist Updated 1st Note | November 1, 2011 |
| 3.3 6.2 6.3 | 1.0 / 2 1.0 / 1 1.0 / 1 | Updated all steps Updated step 2 Updated step 1 & 2 All procedures in this manual have been reviewed. | December 15, 2011 |
| 1.2 4.2 5.7 | - / 1 - / 6 - / 2 | Updated Scope Updated all steps of procedure Updated Market Participant Backup Control Center Transfer | January 19, 2012 |
| 2.1 3.3 3.4 3.7 3.8 4.1 4.2 5.3 5.6 5.8 6.1 7.1 9.1 9.2 10.2 | 1.0 / 1 1.0 / 3 1.0 / 2 1.0 / 3 1.0 / 1 1.0 / 2 1.0 / 7 1.0 / 3 1.0 / 1 1.0 / 1 1.0 / 8 1.0 / 3 1.0 / 1 1.0 / 5 1.0 / 4 | Updated paragraph 4 Updated Step 3 Updated Threat & Emergency Classifications & Desktop Guide reference Changed Shift Engineer to Operations Support Corrected grammar on step 1 Changed Shift Engineer to Operations Support Updated procedure Changed Shift Engineer to Operations Support Corrected grammar on step 2 Updated step 2 Updated Texas RE Event Reporting, OE-417 reporting & Desktop Guide reference Updated Desktop Guide reference Updated Desktop Guide reference Updated Desktop Guide reference Changed Shift Engineer to Operations Support and updated Desktop Guide reference | March 1, 2012 |
| 2.1 3.3 3.6 5.6 6.1 7.1 7.4 7.5 7.6 | 1.0 / 2 1.0 / 4 1.0 / 2 1.0 / 2 1.0 / 9 1.0 / 4 1.0 / 2 1.0 / 2 1.0 / 2 | Changed TSP/DSP to TO Updated 3rd Note Updated purpose Changed TSP to TO and Transmission Facility Updated step Update Report & changed ARR to PRC and ERCOT Morning Report Updated step NERC and Degraded Weather Updated OCN, Advisory, & Watch steps Deleted Cold Weather, not Extreme Cold Weather Section number changed, Added OCN, Advisory and Emergency Notice | May 1, 2012 |
| 3.2 | 1.0 / 3 | Updated to reflect changes in the TAC approved Non-Spin document | May 14, 2012 |
| 7.2 7.3 | 1.0 / 3 1.0 / 4 | Updated EILS to ERS per NPRR 451 & added TO load management program Updated EILS to ERS per NPRR 451 & added TO load management program | June 1, 2012 |
| 3.3 4.2 6.1 | 1.0 / 5 1.0 / 8 1.0 / 10 | Updated step 3 Added Desktop Guide to VDI reference Updated PUCT Daily Report, NERC and DOE Reporting and RCIS Posting | July 16, 2012 |
| 3.4 4.2 5.9 6.1 7.2 | 1.0 / 3 1.0 / 9 1.0 / 1 1.0 / 11 1.0 / 4 | Added CPT to procedure and Typical Subject line for e-mail Added Log to procedure Deleted Procedure Updated NERC and DOE Reporting Added 30 MIN ERS deployed to EEA 1 | August 29, 2012 |
| 2.2 3.1 5.3 6.1 7.6 9.1 | 1.0 / 1 1.0 / 2 1.0 / 4 1.0 / 12 1.0 / 3 1.0 / 2 | Added Hotline Call Communication Updated step 5 Updated and added Planned and Forced Outage sections. Added Weather Information section to PUCT Daily Report. Updated step 1 in NERC and DOE Reporting and ERCOT Morning Report section. Updated OCN, Advisory, & Watch Updated step E-mail All procedures in this manual have been reviewed. | November 1, 2012 |
| 3.2 3.3 3.4 3.5 3.6 3.7 3.8 4.1 5.2 5.3 5.5 5.6 5.8 6.1 6.2 6.3 7.4 7.5 7.6 8.3 8.6 9.2 10.1 10.2 11.0 | 1.0 / 4 1.0 / 6 1.0 / 4 1.0 / 1 1.0 / 3 1.0 / 4 1.0 / 2 1.0 / 3 1.0 / 1 1.0 / 5 1.0 / 3 1.0 / 3 1.0 / 2 1.0 / 13 1.0 / 2 1.0 / 2 1.0 / 3 1.0 / 3 1.0 / 4 1.0 / 2 1.0 / 1 1.0 / 6 1.0 / 2 1.0 / 5 1.0 / 1 | Updated step 1, Capacity Monitoring and deleted Reserve Monitoring Updated step 3 Updated notes and Management Notifications Updated purpose and step 1 Updated step 2 Updated step TCM & renamed LMP Map Delete procedure for large wind ramp events Updated step 1 Grammatical correction Updated step 3 Protective Relay or Equipment Failure Added MISO Reliability Coordinator Updated step 2 TO Temporary Equipment Limitation Notifications Updated purpose Updated step 1 Texas RE Event Reporting, Note and step 1 NERC and DOE Reporting, Loss of Firm Load NXT Notification Requirements, step 1 Weather Information section to ERCOT Morning Report, step 1 RMR Unexcused Misconduct Events, GMD, step 2 Gas Restrictions and added Special Protection Systems (SPSs) Deleted procedure Renamed to 6.2 and updated procedure Updated step Reporting Updated step Reporting Updated Log Updated step 2 Updated procedure Deleted Notice Builder Updated step 3 Updated step monitor, step 4 Building Security and Fire Alarms and step 3 Failure of the Emergency Generator Updated procedure Review New Communications from Manager and/or Control Room Operations Manager and step 4 Implement ERCOT Personnel and Company Standards | March 1, 2013 |
| 3.3 3.4 6.1 | 1.0 / 7 1.0 / 5 1.0 / 14 | Updated all steps Added 1st Note, deleted 2nd & 3rd Notes, Management Notification, updated QSE Notification, TO Notification Updated step Update Report | June 1, 2013 |
| 4.1 5.1 6.1 10.2 | 1.0 / 4 1.0 / 2 1.0 / 15 1.0 / 6 | Updated Ancillary Service Testing Coordination and added Coordinated Reactive Tests Added MISO Updated PUCT Daily Report & step 1 on NERC and DOE Reporting and added Note to NXT Notification Requirements Updated 1st Note and step #3 on Building Security and Fire Alarms | July 15, 2013 |
| 3.4 4.1 6.1 7.3 | 1.0 / 6 1.0 / 5 1.0 / 16 1.0 / 5 | Updated QSE Notification, TO Notification & Send E-mail Updated Coordinated Reactive Tests Added 7-Day Outlook, updated Event List on Texas RE Event Reporting & step 2 on GEO-Magnetic Disturbance (GMD) Updated table | August 9, 2013 |
| 3.3 | 1.0 / 8 | Removed HHGT TO reference | August 30, 2013 |
| 3.3 3.4 4.1 4.2 5.3 5.4 5.6 5.7 6.1 7.6 8.1 8.2 8.3 9.1 9.2 10.2 | 1.0 / 9 1.0 / 7 1.0 / 6 1.0 / 10 1.0 / 6 1.0 / 1 1.0 / 4 1.0 / 3 1.0 / 17 1.0 / 5 1.0 / 1 1.0 / 1 1.0 / 3 1.0 / 3 1.0 / 7 1.0 / 7 | Updated step 1 and Log Updated step Log Updated step Log Updated step Log Updated step 4, Planned Outage, Forced Outage and added Log Updated step Log Updated step Log Updated step 1 and added Log Updated step Update Report, TRE Event Reporting changed to Event Analysis Report and event list updated, and NERC and DOE Reporting updated Added step Issues and updated Log Updated step 3 and added Log Updated step 3, 5 and added Log Updated step 3 Updated step Log Updated steps Log Added step 4 and updated Log All procedures in this manual have been reviewed. | December 13, 2013 |
| 4.1 6.1 7.2 7.3 | 1.0 / 7 1.0 / 18 1.0 / 5 1.0 / 6 | Updated for NOGRR125 & OK to test on Coordinated Reactive Tests Updated NERC and DOE Reporting Updated EEA Implementation Checklist Updated EEA Restoration Checklist | January 29, 2014 |
| 3.2 4.2 5.5 6.1 6.2 | 1.0 / 5 1.0 / 11 1.0 / 4 1.0 / 19 1.0 / 3 | Updated VDI information Updated VDI information Updated Note Updated Update Report on PUCT Daily Report and step 1 on NERC and DOE Reporting Updated step 1 | April 4, 2014 |
| 2.2 7.1 | 1.0 / 2 1.0 / 5 | Added VDIs to Master QSEs Updated step 1 | June 1, 2014 |
| 4.2 6.1 6.2 7.2 | 1.0 / 12 1.0 / 20 1.0 / 4 1.0 / 6 | Updated 1st Note, Retest and added Demonstration Test Updated step Update Report Updated steps 1 & 4 Updated checklist | August 1, 2014 |
| 3.3 3.4 4.1 4.2 9.2 | 1.0 / 10 1.0 / 8 1.0 / 8 1.0 / 13 1.0 / 8 | Added step 2 Corrected spelling on Send E-mail Updated script for Unit Testing Added new reference Updated new section on Phone Tests | October 1, 2014 |
| 3.6 3.7 4.2 6.1 | 1.0 / 4 1.0 / 5 1.0 / 14 1.0 / 21 | Changed title and removed references to W-N Added step RTMONI Updated Testing Rules and Scripts Added 2nd note to NERC and DOE Reporting & updated GMD procedure All procedures in this manual have been reviewed | December 15, 2014 |
| 2.2 3.2 3.3 4.2 5.3 5.5 6.1 7.2 7.5 | 1.0 / 3 1.0 / 6 1.0 / 11 1.0 / 14 1.0 / 7 1.0 / 5 1.0 / 22 1.0 / 7 1.0 / 4 | Added Dispatch and VDI definitions Updated step 4 Updated step 1 in Suspected Sabotage or Sabotage Events Moved procedure to Resource desk Updated title and added Protection System Setting Notifications Added Switchable Generation Resource Added Unit Trip Posting Updated checklist Updated Note | March 1, 2015 |
| 5.3 6.1 | 1.0 / 8 1.0 / 23 | Clarification to step 2 Clarifications to GMD procedure | March 30, 2015 |
| 3.3 3.4 3.6 3.7 4.1 5.6 6.1 6.2 7.6 8.3 8.6 10.1 10.2 11 | 1.0 / 12 1.0 / 9 1.0 / 5 1.0 / 6 1.0 / 9 1.0 / 5 1.0 / 24 1.0 / 5 1.0 / 6 1.0 / 4 1.0 / 2 1.0 / 3 1.0 / 8 1.0 / 2 | Updated contact information Updated contact information Updated contact information Updated contact information Updated contact information Updated contact information Updated contact information Updated contact information Updated contact information Updated contact information Updated contact information Updated contact information Updated contact information Updated contact information | May 1, 2015 |
| 6.1 10.2 | 1.0 / 25 1.0 / 9 | Updated GMD procedure Added new Telemetering, Control Equipment and Communication Outages process | July 15, 2015 |
| 9.1 9.2 9.3 9.4 | 1.0 / 0 1.0 / 0 1.0 / 9 1.0 / 4 | New procedure for COM-001-2 New procedure for COM-001-2 Updated procedure for COM-001-2 Updated section number | October 1, 2015 |
| 6.1 7.2 9.3 | 1.0 / 26 1.0 / 8 1.0 / 10 | Updated Event Analysis Reporting step Event List Implement NPRR708 for EEA Added Primary Control Center step Replacement/Alternative Device Examples Added Alternate Control System step Replacement/Alternative Device Examples All procedures in this manual have been reviewed | December 31, 2015 |
| 2.1 6.1 | 1.0 / 3 1.0 / 27 | Updated System Operator Responsibility and Authority Updated Guidelines for Determining EEA Potential | March 1, 2016 |
| 5.3 10.2 | 1.0 / 9 1.0 / 10 | Updated Protective Relay or Equipment Failure step 2 Deleted step 2 and updated step 3 | April 29, 2016 |
| 2.1 2.2 3.2 4.1 5.3 7.2 7.3 8.2 8.6 10.2 | 1.0 / 4 1.0 / 4 1.0 / 7 1.0 / 10 1.0 / 10 1.0 / 9 1.0 / 7 1.0 / 2 1.0 / 3 1.0 / 11 | Updated steps for COM-002-4 Updated steps for COM-002-4 Updated steps for COM-002-4 Updated steps for COM-002-4 Updated Protection System Setting Notification Updated steps for COM-002-4 Updated steps for COM-002-4 Updated steps for COM-002-4 Updated steps for COM-002-4 Updated steps for COM-002-4 | June 30, 2016 |
| 3.3 6.1 7.2 10.1 | 1.0 / 13 1.0 / 28 1.0 / 9 1.0 / 4 | Updated step Updated Step 1 of NERC and DOE Reporting Updated checklist Updated step 2 | September 30, 2016 |
| 3.3 4.1 5.5 6.1 | 1.0 / 14 1.0 / 11 1.0 / 6 1.0 / 29 | Updated Note Added Unit Testing Note Updated Approved Resources to be ONTEST Step Approval Deleted Turbine Governor Updated Note, renamed SPS to RAS & updated RAS Updated Event Analysis Reporting Step Event List, Event Reporting EOP-004-2 & Step 1 Renamed Special Protection Systems (SPS) to Remedial Action Schemes (RAS) & updated Remedial Action Schemes (RAS) All procedures in this manual have been reviewed | December 30, 2016 |
| 2.1 3.4 4.1 5.1 5.3 5.4 5.5 5.6 5.7 5.9 6.1 7.2 7.6 9.1 9.2 9.3 10.2 | 1.0 / 5 1.0 / 10 1.0 / 12 1.0 / 3 1.0 / 11 1.0 / 2 1.0 / 7 1.0 / 6 1.0 / 4 1.0 / 0 1.0 / 30 1.0 / 10 1.0 / 7 1.0 / 1 1.0 / 1 1.0 / 11 1.0 / 12 | Updated for IRO-001-4 Updated Threat & Emergency Classifications step Updated In Service Approval step 1 Deleted paragraph to create new procedure in 5.9 Updated CFE to CENACE Updated Protective Relay Outages step Updated second note, step 5 & 6 Updated CFE to CENACE Updated TO Temporary Equipment Limitation Notifications step 2 Updated Heading title and step 1 New procedure for IRO-002-4 R2 Updated with Event Analysis v3.1 changes and EOP-004-3 and EOP-011 Updated checklist Updated title Updated step 1 Updated step 2 Updated Satellite Modem Updated TOs, QSEs along with Telemetering, Control Equipment and Communication Outages | March 31, 2017 |
| 1.1 3.2 5.3 7.2 9.1 | 1.0 / 1 1.0 / 8 1.0 / 12 1.0 / 11 1.0 / 2 | Updated Purpose to add Reliability Risk desk Updated Capacity Monitoring step 3 & 4 Updated step 3 and Protective Relay Outages Updated EEA 3 checklist Updated Interpersonal Communication | June 1, 2017 |
| 7.2 | 1.0 / 12 | Updated checklist | June 30, 2017 |
| 9.1 | 1.0 / 3 | Updated steps & deleted Note | September 29, 2017 |
| 9.3 | 1.0 / 12 | Updated 1st Weekend of Every Month | October 31, 2017 |
| 6.1 7.1 8.6 | 1.0 / 31 1.0 / 6 1.0 / 4 | All procedures in this manual have been reviewed Updated PUCT Daily Report step Update Report Updated System Disturbance step NERC Updated Root Cause Analysis step NOTE | December 28, 2017 |
| 6.1 7.2 9.3 10.2 | 1.0 / 32 1.0 / 13 1.0 / 13 1.0 / 13 | Updated NERC and DOE Reporting OE-417 Reporting Events Updated Checklist Added Form an Email steps Updated step 1 & 2 | February 28, 2018 |
| 6.1 10.2 | 1.0 / 33 1.0 / 14 | Updated NERC and DOE Reporting step OE-417 Reporting Events Updated Title & EMS Alarm Heartbeat, Dynamic Rating, SCED Status, EMBP, SE, RTCA or RLC Alarms steps note and Monitor | March 30, 2018 |
| 2.2 7.2 7.3 | 1.0 / 5 1.0 / 14 1.0 / 8 | Updated procedure purpose Updated Checklist Updated Checklist | May 1, 2018 |
| 5.5 | 1.0 / 8 | Update EEA and Switchable Generation Resource | May 31, 2018 |
| 3.2 6.1 7.2 9.3 9.4 | 1.0 / 9 1.0 / 34 1.0 / 15 1.0 / 14 1.0 / 5 | Added step 2 & Log, updated step 3 and renumbered 2, 3 &4 Deleted 7-Day Outlook Report Updated Checklist Multiple changes to clarify the roles and responsibilities Updated forms | August 31, 2018 |
| 5.5 6.1 | 1.0 / 9 1.0 / 35 | Removed Monticello RAS Removed Reportable Balancing Contingency Event from the PUCT Daily Report update and updated step 1 on the ERCOT Morning Report | October 1, 2018 |
| 6.1 | 1.0 / 36 | Updated PUCT Daily Report | November 1, 2018 |
| 9.1 9.2 9.3 | 1.0 / 4 1.0 / 2 1.0 / 15 | Updated Alternative Interpersonal Communication Updated step 1 & 2 Clarified notification times All procedures in this manual have been reviewed | December 28, 2018 |
| 7.2 | 1.0 / 16 | Updated Checklist | January 31, 2019 |
| 6.1 7.4 10.1 | 1.0 / 37 1.0 / 4 1.0 / 5 | Updated NERC and DOE Reporting Operating Plan Updated step Emergency Notice and added steps Issues and Log Updated steps and deleted note | March 29, 2019 |
| 3.7 4.1 | 1.0 / 7 1.0 / 13 | Added Note Updated Coordinated Reactive Tests step 2 | May 01, 2019 |
| 5.5 | - / 10 | Updated Sharyland to ONCOR DC Tie Desk Added step 3 and Typical Scripts to Switchable Generation Resource | May 16, 2019 |
| 5.5 6.1 7.2 | 1.0 / 11 1.0 / 38 1.0 / 17 | Updated Switchable Generation Resource steps Updated process Moved TOs load management from EEA1 to EEA2 | May 31, 2019 |
| 4.1 6.1 10.2 | 1.0 / 14 1.0 / 39 1.0 / 15 | Updated Coordinated Reactive Tests step 1 Added Note to PUCT Daily Report Updated NERC and DOE Reporting Operating Plan steps Updated Building Security and Fire Alarms step 2 | August 1, 2019 |
| 6.1 7.2 | 1.0 / 40 1.0 / 18 | Updated Remedial Action Schemes (RAS) step Updated Checklist | November 1, 2019 |
| 3.3 3.4 3.6 3.7 4.1 5.3 5.6 6.1 6.2 7.1 7.2 7.3 7.4 7.6 8.3 8.6 9.3 9.4 10.1 10.2 11 | 1.0 / 15 1.0 / 11 1.0 / 6 1.0 / 8 1.0 / 15 1.0 / 13 1.0 / 7 1.0 / 41 1.0 / 6 1.0 / 7 1.0 / 19 1.0 / 9 1.0 / 5 1.0 / 8 1.0 / 5 1.0 / 5 1.0 / 16 1.0 / 6 1.0 / 6 1.0 / 16 1.0 / 3 | Updated Suspected Sabotage or Sabotage Events Updated Note Updated step 2 Updated step LMP Map Updated Unit Testing step 1 Deleted step NERC Updated TO Temporary Equipment Limitation Notifications step 2 Updated steps Updated steps Updated NERC step Updated checklist Updated checklist Updated step Issues Updated step Issues Updated step 2 Updated steps Updated step Cell Phone Update Note and added issues step Updated step 3 Updated steps Updated Title and steps All procedures in this manual have been reviewed | January 1, 2020 |
| 3.2 3.7 7.4 7.5 9.1 9.2 9.3 9.4 | 1.0 / 10 1.0 / 9 1.0 / 6 1.0 / 5 1.0 / 5 1.0 / 3 1.0 / 17 1.0 / 7 | Clarified RUC commits/decommits Clarified RUC commits/decommits Clarified RUC commits/decommits Clarified RUC commits/decommits Updated AIC step Updated all steps Updated title and steps Updated title and steps | January 31, 2020 |
| 9.2 | 1.0 / 4 | Updated step 2 | February 28, 2020 |
| 2.1 3.2 | 1.0 / 6 1.0 / 11 | Added Advance Action Notice per NPRR930 Added Advance Action Notice section per NPRR930 | July 1, 2020 |
| 9.1 9.3 | 1.0 / 6 1.0 / 18 | Updated Nortel to Cisco Updated Nortel to Cisco | September 1, 2020 |
| 3.6 | 1.0 / 7 | Updated Title, Purpose and added new IROL’s | October 1, 2020 |
| 3.6 | 1.0 / 8 | Updated each step IROL and step 2 | October 31, 2020 |
| 3.2 3.5 5.4 5.5 6.1 7.2 7.3 10.2 | - / 12 - / 2 1.0 / 3 1.0 / 12 1.0 / 42 1.0 / 20 1.0 / 10 1.0 / 17 | Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1031 and NPRR1039 Updated for NPRR1039 Updated for NPRR1039 Updated for NPRR1039 All procedures in this manual have been reviewed | December 31, 2020 |
| 3.4 4.1 5.5 5.8 5.9 7.4 10.1 10.2 | 1.0 / 12 1.0 / 16 1.0 / 13 1.0 / 3 1.0 / 1 1.0 / 7 1.0 / 7 1.0 / 18 | Organization change Organization change Updated Note Updated procedure Organization change Organization change Organization change Organization change | April 1, 2021 |
| 3.6 5.5 7.5 | 1.0 / 9 1.0 / 14 1.0 / 6 | Removed McCamey IROL Changed Notice Builder to Grid Conditions Communications (GCC) Notices Updated Advisory & Watch | May 6, 2021 |
| 3.2 | 1.0 / 13 | Updated for OBDRR031 | July 12, 2021 |
| 3.2 6.1 | 1.0 / 14 1.0 / 43 | Updated for OBDRR031 Updated for NPRR1031 | July 31, 2021 |
| 3.2 7.2 | 1.0 / 15 1.0 / 21 | Updated Capacity Monitoring step 4 & AAN steps Updated for NPRR1105 & NPRR 1106 | December 1, 2021 |
| 7.2 | 1.0 / 22 | Updated for NOGRR236 | December 17, 2021 |
| 2.2 3.2 3.6 6.1 7.1 7.2 7.3 7.4 7.5 7.6 7.7 | - / 6 1.0 / 16 - / 10 - / 44 - / 9 - / 23 - / 11 - / 8 - / 7 - / 9 - / 0 | Updated step 1 Updated step 1 & step 4 Added McCamey Export Updated Gas Restrictions & DOE email address Updated Other Significant Weather Events Updated all steps Updated Level 1 & Level 2 Updated all steps Updated all steps Updated all steps Added new procedure All procedures in this manual have been reviewed | December 31, 2021 |
| 6.1 6.2 7.2 7.3 7.5 7.7 | - / 45 - / 7 1.0 / 24 1.0 / 12 1.0 / 8 1.0 / 1 | Updated NERC and DOE Reporting Operating Plan with DOE-417 reporting changes Updated OE-417 to DOE-417 Updated steps Updated steps Corrected typo Updated Note | February 1, 2022 |
| 3.3 | 1.0 / 16 | Updated for Cyber Event | March 1, 2022 |
| 5.9 9.2 10.1 10.2 | 1.0 / 2 1.0 / 5 1.0 / 8 1.0 / 19 | Added Note Updated step 2 Added Note Added Note | April 7, 2022 |
| 3.2 7.2 | 1.0 / 17 1.0 / 25 | Updated for NPRR1093 Updated for NPRR939, NPRR1093 & NOGRR191 | May 26, 2022 |
| 7.2 7.3 7.6 | 1.0 / 26 1.0 /13 1.0 / 10 | Added version history Added version history Updated Note | July 29, 2022 |
| 10.2 | 1.0 / 20 | Updated EMS Heartbeat Alarm note | October 7, 2022 |
| 3.2 6.1 7.2 | 1.0 / 18 1.0 / 6 1.0 / 27 | Updated Capacity Monitoring and Added Large Load Curtailment Program Added FFSSR Restocking Request Updated Prior to Entering EEA guideline All procedures in this manual have been reviewed | December 30, 2022 |
| 3.2 | 1.0 / 19 | Updated Large Load Curtailment Program | February 1, 2023 |
| 7.1 7.5 7.6 7.7 | 1.0 / 10 1.0 / 9 1.0 / 11 1.0 / 2 | Updated procedure title and first step Updated steps for Extreme Weather Monitor Updated steps for Extreme Weather Monitor Updated procedure title | March 31, 2023 |
| 3.4 | 1.0 / 13 | Updated Phone Number | May 4, 2023 |
| 7.2 7.3 | 1.0 / 28 1.0 / 14 | Updated for NPRR863 Updated for NPRR863 | June 9, 2023 |
| 3.3 7.2 | 1.0 / 17 1.0 / 29 | Updated SSRG Hotline script Updated deployed to released | June 30, 2023 |
| 6.1 7.2 | 1.0 / 7 1.0 / 30 | Updated Note for PUCT Report Updated For NPRR1143 | August 1, 2023 |
| 6.1 7.2 | 1.0 / 8 1.0 / 31 | Updated for NPRR1176 Updated for NPRR1176 | November 1, 2023 |
| 7.2 | 1.0 / 32 | Updated for NPRR1176 | November 7, 2023 |
| 6.1 7.2 7.7 | 1.0 / 9 1.0 / 33 1.0 / 3 | Updated Event Analysis Reporting Updated EEA Checklist Updated Note All procedures in this manual have been reviewed | December 29, 2023 |
| 3.6 | 1.0 / 11 | Added South Texas Export IROL Added South Texas Import IROL | March 1, 2024 |
| 3.6 3.7 | 1.0 / 12 1.0 / 10 | Added step IROL Comms Added step SOL Comms | March 29, 2024 |