Power Operations Bulletin # 2003
ERCOT has posted/revised the Reliability Unit Commitment manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html
2.3
Publish A/S Requirements and Review System Conditions 

Procedure Purpose:  To publish and verify daily Ancillary Service requirements are posted to the market.

	Protocol Reference
	4.2.1.1(1)
	4.2.1.1(2)
	4.2.1.2(2)
	4.3(2)

	Guide Reference
	
	
	
	

	NERC Standard
	EOP-011-4

R2, R2.1, R2.2, R2.2.3, R2.2.3.2, R2.2.3.3
	TOP-002-4

R4, R4.4
	
	


	Version: 2 
	Revision: 0
	Effective Date:  December 5, 2025


	Step
	Action

	Note
	· Review and update A/S Requirements must be completed prior to 0500.

· The Shift Supervisor must verify the posted ancillary service requirements for the 1st day of the month.

	Review Weather Data Information

	1
	REVIEW the Weather Data for the next operating day in the EMS.

	2
	REVIEW REFERENCE DISPLAY:

EMS Applications>Weather Details>Real Time Displays>Weather Forecast Directory
IF: 

· The Last Weather Source Update or Last Weather Read is less than one (1) hour old;

THEN:  

· Using the usual sources, review the weather forecast for at least two days out.

IF: 

· The data update or read is more than one (1) hour old;

THEN:

· Notify the Shift Supervisor and the Service Desk.

	3
	Evaluating the weather forecast for several days ahead is needed to help determine if there is a potential for fuel supply problems.  The trigger will usually be an extreme weather event.  It may be necessary to discuss fuel switching with the Supervisor and appropriate QSE to optimize fuel supply if a reliability concern exists.

	Fuel Switching
	IF:

· Notified of fuel limitations;

THEN:

· Consult with Supervisor and determine if reliability concerns exist

· Identify potential transmission issues

· Identify potential capacity issues

IF:

· Reliability concerns exists;

THEN:

· Consider fuel switching options (gas to oil) by discussing with appropriate QSE if capability exists. Refer to Fuel oil capability spreadsheet on System Operations SharePoint.

	Optimize Fuel Supply
	IF:

· A particular fuel supply is at risk;

THEN:

· Consult with Supervisor and determine if reliability concerns exist

· Identify potential transmission issues

· Identify potential capacity issues

IF:

· Reliability concerns exists;

THEN:

· Consider RUC committing Resources with fuel that is not at risk.

	Review and Select Load Forecast 

	1
	Review and Select load forecast for next day (Refer to Desktop Guide RUC Section 2.17.

	2


	IF:

· There is a large difference between the load forecasts, AND

· There is uncertainty on which load forecast is correct;

THEN:

· Call the Load Forecasting group for guidance on updating the weather or load forecast.

	3
	Notify by e-mail the following distribution lists of the issue:

· Load Forecasting Department 

· 1 ERCOT Shift Supervisors

	Publish A/S Requirements

	1
	REFERENCE DISPLAY:

Market Participation  > Physical Market > AS Market > AS Plan

Before 04:00, verify the hourly ERCOT system total A/S requirements for each of the following, for each hour of the operating day:  
· Reg-Up

· RRS 

· Reg-Down

· ECRS
· Non-Spin



	2
	REFERENCE DISPLAY:

Market Participation  > Physical Market > AS Market > AS Deployment Factors
Before 04:00, verify the hourly ERCOT system total A/S Deployment Factor requirements for each of the following, for each hour of the operating day:  
· Reg-Up

· RRS 

· Reg-Down

· ECRS

· Non-Spin



	3
	REFERENCE DISPLAY:

Market Participation > Monitoring > Event Manager > Events

Search / Filter for AS_OBLIGATION_CALC

Before 06:00, verify the hourly ERCOT system total A/S requirements and A/S Deployment Factors have been automatically published at 04:55:

IF: 

· Status indicates complete, no further action is necessary, OR 

· Status indicates anything else;

THEN:

· Change status to start now and select submit to database poke point.

	Increasing A/S Requirements before A/S Obligations Publish

	Note
	This procedure would be performed when it has been determined that additional A/S is needed or A/S Deployment Factors are needed, such as to support a weather event.

	Note
	If an Emergency Condition may exist that would adversely affect system reliability, ERCOT may change the percentage of Load Resources that are allowed to provide RRS from the monthly amounts determined previously.

	Note
	If the operation day D is identified as a High Forecast Variability Day on day D-2 (2-day advance). Two days prior to the OD identified as a High Variability Day, the GMS team will update NSRS quantities and the updated AS plan will be reflected in the DAM Ancillary Service Plan report. The Control room will be notified two days in advance of a High Variability Day and the corresponding AS plan. Before 04:00, verify the updated High Variability RRS and Non Spin quantities that will be applicable.  Notify the GMS Production Support Team immediately if requirements are not correct in the AS Plan.

	1
	REFERENCE DISPLAY:

Market Participation  > Physical Market > AS Market > AS Plan

Before 04:00, increase the hourly ERCOT system total A/S requirements for each requirement needed for each hour of the next operating day:  
· Reg-Up

· RRS 

· Reg-Down

· ECRS

· Non-Spin



	2
	REFERENCE DISPLAY:

Market Participation  > Physical Market > AS Market > AS Deployment Factors

Before 04:00, increase the hourly ERCOT system total A/S Deployment Factor requirements for each requirement needed for each hour of the next operating day:  
· Reg-Up

· RRS 

· Reg-Down

· ECRS

· Non-Spin



	3
	REFERENCE DISPLAY:

Market Participation > Monitoring > Event Manager > Events

Search / Filter for AS_OBLIGATION_CALC

Before 06:00, verify the hourly ERCOT system total A/S requirements and A/S Deployment Factors have been automatically published at 04:55:

IF: 

· Status indicates complete, no further action is necessary, OR 

· Status indicates anything else;

THEN:

· Change status to start now and select submit to database poke point.

	4
	IF: 

· The A/S requirements and/or A/S Deployment Factors were increased,

THEN:

· The next day will copy the new A/S requirements unless you return the A/S requirements to the A/S Plan requirements for the month. 
· The next day will copy the new A/S Deployment Factor requirements unless you return the A/S Deployment Factors to the A/S Deployment Factor requirements for the month. 
REFERENCE DISPLAY:

Market Participation > Physical Market > AS Market > AS Plan 
Market Participation  > Physical Market > AS Market > AS Deployment Factors

Before 04:00 update the A/S requirements.

	Note
	Refer to the A/S requirements for the current month’s A/S Plan if no changes are required.

	Note
	Refer to the A/S Deployment Factor requirements for the current month’s A/S Plan if no changes are required.

	Priority Outages

	1
	A Priority Outage is one that affects generation.

Prior to 1200:

· Review the Outage Notes for the next Operating Day, make lists of Priority Outages, sorted by the affected TOs, 

· The file is located in P:\DAY AHEAD – TDSP PRIORITY OUTAGE NOTIFICATION,

· Email the Priority Outages to the appropriate TO using the email addresses provided in the RUC Desktop Guide Section 2.22,  

· Copy and paste the information into the body of the email,

· The Subject line should read “Priority Outages”, “<Company Name>”, “<Date>”

· At the bottom of each email, be sure to include a Confidentiality Notice and your signature,

· Ensure each document has a Note which states to notify ERCOT within 30 minutes of the Actual Start and Actual End times for the Priority Outages,

· If email is unavailable, follow the same guidelines using the Fax  Machine, 

· Place hard copies in Daily Log File.

	Blackstart Availability

	1
	REFERENCE DISPLAY:

Market Participation  > Physical Market > Market Participant Submissions > Availability Plan

ERCOT SharePoint > System Operations – Control Center > Documents > Blackstart Availability
REVIEW:

· Blackstart Availability Plan for next operating day (OD+1 tab)

IF:

· Blackstart Availability Plan for next operating day is missing

THEN:

· Call the QSE and request them to submit their Blackstart Availability Plan for next operating day

· Update the Blackstart Availability spreadsheet located on SharePoint

	Log
	LOG when completed and any additional actions taken.

	Verification of Published A/S Requirements

	Note
	This step may be completed after 0600.

	1
	VERIFY by spot-checking the following information posted to the ERCOT Website for the next operating day (or two days if two-day Ahead market is in effect) is posted.

· Planned Transmission line and equipment outages for the operating day.  

· ERCOT Website; Grid; Transmission; Consolidated Transmission Outage Report

· Weather assumptions used to provide the system conditions forecast.

· ERCOT Website; Data Products; Markets; Weather assumptions

· The hourly ERCOT System total Ancillary Service requirements for Regulation Down – REGDN, Regulation Up – REGUP, Responsive Reserve – RRS, ERCOT Contingency Reserve Service – ECRS, and Non-spinning Reserve – NSPIN.  

· ERCOT Website; Data Products; Markets; Day-Ahead Market; DAM Ancillary Service Plan.
· The hourly ERCOT System total Ancillary Service requirements for Regulation Down – REGDN, Regulation Up – REGUP, Responsive Reserve – RRS, ERCOT Contingency Reserve Service – ECRS, and Non-spinning Reserve – NSPIN.  

· ERCOT Website; Data Products; Markets; Day-Ahead Market; Projected Ancillary Service Deployment Factors.

	Log
	LOG any significant problems including any action taken.


3.1
Tasks prior to Execution of HRUC

Procedure Purpose:  To make manual corrections for bad/suspect telemetry, load forecast modifications, or to RUC commit/de-commit Resources prior to running the RUC process.

	Protocol Reference
	3.12.1(3)
	5.1
	5.2.2.2(11)
	5.3(3)

	
	5.5.1
	5.5.2(9)
	
	

	Guide Reference
	
	
	
	

	NERC Standard
	TOP-002-4

R4, R4.2, R4.3
	
	
	


	Version: 2 
	Revision: 0
	Effective Date:  December 5, 2025


	Step
	Action

	Tasks prior to execution of HRUC

	Note
	The RUC Study Period for DRUC is the next Operating Day. The RUC Study Period for HRUC is the balance of the current Operating Day plus the next Operating Day if the DRUC for the Operating Day has been solved or after 18:00 if DRUC did not solve.

	Continuous

Monitoring
	REVIEW REFERENCE DISPLAY:

Market Operation>EMS Interface>EMSI Workflow Parameters

Market Operation>EMS Interface>EMSI Workflow
IF:

· The EMSI Workflow Parameters does not indicate EMSI has run in the last hour and Load Forecast are NOT running (should be continuous);

THEN:

· Open EMSI Workflow, select “Start up”.  When start up is complete, select “Run”.

IF:

· EMSI Workflow does not complete;
THEN:

· Notify Service Desk and Control Room staff.

	Load   Forecast
	Periodically monitor the Load Forecast to ensure it is accurate:

IF:

· Adjustments need to be made, they will be done in the EMS and updated to the MMS;

THEN:

· Adjust (Refer to Desktop Guide RUC Section 2.17).

	Wind Forecast Updates
	Periodically monitor the Wind Forecast and verify data is updating:
IF:

· Wind forecast is not updating;

THEN:

· Notify Supply Integration & Grid Application group,

· Be aware that this could skew HRUC results.

	RMR

Consideration
	All other generation resources should be considered prior to a RMR commitment for capacity purposes: 

IF:

· An RMR unit needs to be considered in HRUC;
THEN:

· Ensure COP status is “EMR”.
IF:

· An RMR unit is needed but is not to be considered in HRUC;
THEN:

· Commit unit before HRUC is executed,
· Follow 3.2 Review, Approve and Post HRUC Results step RMR Commitment.

	COP

Validation
	REVIEW REFERENCE DISPLAY:

Market Participation>Monitoring>Event Manager>Events>filter Event Name for COP Validation

IF:

· A Resource Forced Outage has occurred and the QSE has not update their COP, OR

· COP Validation ERROR;

THEN:

· Select “START-NOW" in the Status column,

· Be aware that the results may be skewed and determine the need for procuring equivalent MW capacity elsewhere.

	

	



· 

· 

	Bad/Suspect

Telemetry
	Periodically monitor:

IF:

· Notified of bad/suspect telemetry; 

THEN:

· Determine if issues will be resolved for next HRUC run,

· Discuss with Shift Supervisor if the HRUC should be run or delayed until the issues can be resolved,

· Consider requesting Operations Support Engineer to manual over-ride SCADA values (be aware that this could skew the results),

· If it is determined to delay HRUC, follow the “HRUC Failure/Timeline Deviation” procedure.

	E-Tags
	REVIEW REFERENCE DISPLAY:

Market Operation>Reliability Unit Commitment> HRUC Displays> DSI Displays> DSI Data Processes> DSI DC Tie Schedule 

Market Operation>Reliability Unit Commitment> HRUC Displays> DSI Displays> External Input Data> MI COP

Verify that E-tags are being imported into the MMS:
IF:

· Individual schedules need to be reviewed;

THEN:

· Go to the MI COP display and filter ‘ERCOT’ as the QSE name.

	Verify
	REVIEW REFERENCE DISPLAYS:

Market Operation>EMS Interface>EMSI Workflow Parameters

Market Operation>EMS Interface>EMSI Workflow Messages
EMSI has completed successfully within the last hour 

Market Operation>Reliability Unit Commitment>HRUC Displays>UC Displays>HRUC UC Execution Control Parameters

Market Operation>Reliability Unit Commitment>HRUC Displays>NSM Displays>NSM Execution Control Parameters

Market Operation>Reliability Unit Commitment>HRUC Displays>DSI Displays>DSI Execution Control Parameters 

· “Retrieve MF Interface Data” flag set to “Yes”.

· “Retrieve MI Interface Data” flag set to “Yes”.

· “Retrieve EMS Interface Data” flag set to “Yes”.

· “Check Market Status set to “Yes”,

· “Use Save case set to “No”

	DSI
	EXECUTE:

· The DSI sequence;

VERIFY:

· For error or warning messages and take necessary action if needed to correct the errors,

· The input data is properly transferred. 

If NOT: 

· Contact Service Desk immediately to determine the cause and expected time of resolution.

	Manual Commitment
	REVIEW REFERENCE DISPLAYS:

Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP RUC Commitment/Decommitment Summary

Market Operation>Reliability Unit Commitment>HRUC Displays>DSI Displays> External Input Data>MF Generator Parameters

Market Operations>Reliability Unit Commitment>HRUC Displays>DSI Displays>DSI Data Processes> DSI Operator Manual Commitment
Market Operations>Reliability Unit Commitment>HRUC Displays>DSI Displays>External Input Data> MF Generator Parameter 

All other generation resources should be considered prior to a RMR commitment for capacity purposes: 

IF:

· An RMR unit is needed and is not to be considered in HRUC;
THEN:

· RUC commit unit before HRUC is executed,
· Follow 3.2 Review, Approve and Post HRUC Results step RMR Commitment.
IF:

· Additional resources are needed to solve for transmission congestion;

THEN:

· Consult with the Operations Support Engineer and/or the Transmission and Security Desk Operator to determine which resources should be RUC committed,  AND 
· Determine the temporal constraints for each of the units. 
IF:

· The resource start-up time doesn’t allow enough time to re-evaluate the need for its commitment in future HRUC Study Periods;

THEN:

· Change ‘blank’ to ‘Commit’,

· List reason.

	Note
	If a RMR unit was RUC committed in DSI Operator Manual Commitment and it is the only change since the DSI was last run the next step is not necessary.

	Verify
	REVIEW REFERENCE DISPLAY:

Market Operation>Reliability Unit Commitment>HRUC Displays>DSI Displays>DSI Execution Control Parameters 

IF: 

· Manual changes have been made to the HRUC input data; 

CHANGE:

· The appropriate flags are set to prevent the data from being over-written.

· “Retrieve MF Interface Data set to No”, 

· “Retrieve MI Interface Data set to No”, 

· “Retrieve EMS Interface Data set to No”, OR

· “Use Save case set to “Yes”

	Verify HRUC executed at XX: 03

	1
	REVIEW REFERENCE DISPLAYS:

Market Operation>Reliability Unit Commitment>HRUC Displays>Workflow>HRUC Workflow

Market Operation>Reliability Unit Commitment>HRUC Displays>Workflow>HRUC Workflow Messages

Verify execution of the HRUC sequence.


3.2
Review, Approve and Post HRUC Results

Procedure Purpose:  Monitor RUC applications to determine if systems are functioning properly.  Verify results and correct for any warning or error messages.  Review and approve final results for market posting.

	Protocol Reference


	4.4.8
	5.1
	5.3(3)
	5.5.1

	
	5.5.2
	5.5.3
	6.1(2)
	6.4.9.1.2

	Guide Reference
	
	
	
	

	NERC Standard


	EOP-011-4

R2, R2.2, R2.2.3, R2.2.3.1
	IRO-001-4

R1
	TOP-001-6

R1, R2
	TOP-002-4 R1, R2, R3, R4, R4.1, R4.4, R5


	Version: 2 
	Revision: 0
	Effective Date:  December 5, 2025


	Step
	Action

	Note
	See Desktop Guide Common to Multiple Desks Section 2.16 if the savecase function fails when running RUC

	Monitor
	REVIEW REFERENCE DISPLAYS:

Market Operation>Reliability Unit Commitment>HRUC Displays>Workflow>HRUC Workflow

Market Operation>Reliability Unit Commitment>HRUC Displays>Workflow>HRUC Workflow Messages

· Monitor the HRUC Workflow display to determine when it is complete, 

ENSURE: 
· The workflow has completed before the study is approved and published.  

IF:

· The study is approved before it completes,

· Incorrect RUC deployments are sent to QSE’s 

THEN:
· Make hotline call to notify QSE’s that deployments for HRUC are invalid,

· Notify Director Control Room Operations and/or Designee,

· ERCOT may use information from the DAM processes as decision support during the HRUC processes.

	System Summary
	REVIEW REFERENCE DISPLAY:

Market Operation>Reliability Unit Commitment>HRUC Displays>UC Displays>Output Display Menu>System Outputs>Summary

IF:

· All load forecasts seem unreasonable;

THEN:

· Select the most reasonable forecast, AND

· Call the Load Forecasting group for guidance on updating the weather or load forecast

· Notify by e-mail the following distribution lists of the issue:

· Load Forecasting Department

· 1 ERCOT Shift Supervisors



	Excess Generation
	During periods of low load and excess generation:

PERIODICALLY REVIEW:

· Splunk Dashboard Viewer under the MOS_DEV folder:

· “Last Approved HRUC Capacity” which is based on the last ran HRUC solution

VERIFY:

· TOTAL_LOAD is less than SS_LSL,

IF:

· Load forecast is reasonable AND the decision needs to be made in the near future,

THEN:

· Decommit generation from the HRUC next study,

· Priority should be on WGR’s or Resources that resolve congestion;

IF:

· The decision needs to be made immediately,

THEN:

· Issue an electronic Dispatch Instruction confirmation

·  Priority should be given to WGRs and Resources that resolve congestion 

· Choose “DECOMMIT” as the Instruction Type from Resource tab
· Enter “ERCOT requested RUC decommit/capacity surplus” in Other Information.
When issuing a VDI or confirmation, ensure the use of three-part communication:

· Issue the Operating Instruction

· Receive a correct repeat back

· Give an acknowledgement

	

	




· 

· 

· 

· 
· 
· 
· 

· 

· 
· 
· 

	

	



· 

· 
· 

	


	


· 

· 

	STNET Study
	The Transmission and Security Desk Operator has the primary responsibility to perform these voltage studies, however if needed as a backup this step is provided.

Each hour run a STNET study for two hours out (example it is 0100, run study for 0300) to review voltage violations. 

IF:

· Voltage contingencies exist;
THEN:

· Check “Voltage Tracking Issues” spreadsheet on SharePoint to ensure the contingency is not listed

· If not listed, convey the voltage violations to the Transmission and Security Desk Operator with the potential resolution

· Create a savecase, use naming convention “SC_RUC(HE)_(DATE)

· Make at least one detailed log entry per shift that the studies are being executed.   If any new voltage violations are identified that do not have a solution, log the information, and notify the Transmission and Security Desk Operator of the new violation(s)

· Update the “Voltage Tracking Issues” spreadsheet listing the new voltage violation with the contingency resolution.

IF:

· Unsolved contingencies exist;
THEN:

· Communicate any unsolved contingency to the Shift Engineer and Transmission and Security Desk Operator with potential solutions.

· Some potential solutions could be transmission switching, creation of a manual constraint, bringing on an additional Resource, returning a planned outage, or development of a CMP

· Validate the resolution

· Update the “Voltage Tracking Issues” spreadsheet listing the new unsolved contingency with the contingency resolution.

	Violated Constraints
	REVIEW REFERENCE DISPLAYS:

Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP Binding Constraint Summary

Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP Constraint Summary

REVIEW:

· Violated constraints.  If needed, notify Operations Support Engineer to determine the validity; 

IF:

· Invalid, no further action is required;

IF:

· Valid; AND

· Related to a phase shifter tap settings,

THEN:

· Notify Operations Support Engineer to determine if adjusting a Phase Shifter would reduce the flow, 

· Create Suggestion Plan for Constraint,

· Manually RUC commit resources as needed, 

IF:

· Valid; AND no Suggestion Plan or Resource is available to commit within the timeframe of the violated constraint,

THEN:

· Notify the Operations Support Engineer and Transmission and Security Desk Operator to determine if an outage can be withdrawn within the timeframe, 

IF:

· No outage can be withdrawn within the timeframe of the violated constraint,

THEN:

· Notify Operations Support Engineer to develop a Congestion Management Plan and provide it to the TO and Transmission and Security Desk Operator, Notify Shift Supervisor to contact the Director Control Room Operations and/or Designee of actions taken

Refer to Desktop Guide RUC Section 2.14.

	Capacity Reserve Margin
	Monitor:

· Available Committed Capacity Margin and the Available Capacity Margin columns.
IF:

· If the Available Committed Capacity Margin threshold is less than minimum requirement OR;

· If the Available Capacity Margin threshold is less than the minimum requirements:

THEN:

· Inform Shift Supervisor
Refer to Desktop Guide RUC Section 2.24

	HRUC Committed

Units
	REVIEW REFERENCE DISPLAY:

Market Operation>Reliability Unit Commitment>HRUC Displays>DSI Displays>External Input Data>MF Generator Parameter
IF:

· HRUC recommends the commitment of any unit;
THEN:

· Determine the validity, 

· Determine the temporal constraints for each of the unit’s recommendation.

· Refer to Desktop Guide RUC Section 2.23.

IF:

· Temporal constraint exceedances at the same facility do not conflict,

· The resource start-up time allows enough time to re-evaluate the need for its commitment in future HRUC Study Periods, and 

· There is no reliability reason requiring the resource commitment decision to be made immediately;

THEN:

· De-select the resource prior to approving the HRUC study by changing ‘Commit’ to ‘blank’ and list reason,

IF:

· Temporal constraint exceedances at the same facility,

· There is a reliability reason requiring the resource commitment decision to be made immediately;

· Resources returning from outages

· Congestion or Capacity deficiencies that are creating HRUC performance issues

THEN:

· Log the reason for not de-selecting the resource.

NOTE:  A reason must be entered for commit, decommit, and uncommitting, otherwise a message window will pop up in DSP approval process.

Examples below:
· Evaluate later (should be used when waiting until the last possible hour to commit)

· Short start (should be used for units that can start within 1 hour)

· Voltage support 

· Valley import

· Valley Reliability

· Capacity

· Constraint name (SLWSCRL5) * Do not use special characters

· Minimum Run Time

When issuing a confirmation, ensure the use of three-part communication:

· Issue the Operating Instruction

· Receive a correct repeat back

· Give an acknowledgement



	EMR Resources
	Resources with “EMR” Resource status can only be RUC committed during Emergency conditions.

	RMR

Resources
	QSEs will show a COP status of EMR when Resources are available.  RMR Resources will only be dispatched from the Hourly Reliability Unit Commitment (HRUC).

	RMR

Commitment
	WHEN:

· HRUC recommends a RMR unit, AND

· A capacity reserve shortage is projected, and no market Resources are available to meet the projected system demand, and there is a risk of an EEA event; 
THEN:

· Determine if an RMR Resource will need to be considered in HRUC Study Period;

ISSUE:

· Watch for projected reserve capacity shortage with no market solution;

THEN:

· Ensure COP status is “EMR”, and the resource start-up time allows enough time to procure the RMR for the hours showing to be deficient with risk of an EEA event;
SELECT:

· Commit Resource before HRUC is approved
· Commit Resource,

· List reason (RMR for Capacity).
Call QSE with any modification to the Delivery Plan as a result of a commitment.

	Hotline
	Q#77 - Typical Hotline Script for Watch for projected reserve capacity shortage 
Notify the Transmission and Security Desk Operator to make Hotline call to TOs.

	Post
	Typical ERCOT Website posting: 

ERCOT issued a Watch for a projected reserve capacity shortage with no market solution available. HRUC recommended RMR Resources have been committed.

	Cancel
	WHEN:

· Committed RMR Resources are off-line

THEN:

· Making hotline call to QSEs

· Cancelling ERCOT Website posting

· Notify the Transmission and Security Desk Operator to make hotline call to TOs.

Q#78 - Typical Hotline Script for canceling Watch for projected reserve capacity shortage 



	Manual Commitment
	REVIEW REFERENCE DISPLAYS:

Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP RUC Commitment/Decommitment Summary

Market Operation>Reliability Unit Commitment>HRUC Displays>DSI Displays> External Input Data>MF Generator Parameters

IF:

· Additional resources are needed to solve for transmission issues (such as for voltage support) and were not picked up in the HRUC run;
THEN:

· RUC commit unit before HRUC is approved
· Change ‘blank’ to ‘Commit’,

· List reason RUC commit for (constraint name, valley import or voltage support), a message window will pop up in DSP approval process if no reason is provided.

· Give courtesy call to QSE when commitments are made

	Manual Commitment to bring a Unit of a Combined Cycle On-line 
	REVIEW REFERENCE DISPLAYS:

Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays>DSP Combined Cycle Plant Suggestion Plan
IF:

· Additional resources are needed to solve for transmission issues  and were not picked up in the HRUC run;
THEN:

· RUC commit higher configuration of a Combined Cycle before HRUC is approved
· Determine the temporal constraints for the higher configuration.

· Change ‘blank’ to ‘Commit’,

· List reason RUC commit for (constraint name, valley import or voltage support), a message window will pop up in DSP approval process if no reason is provided.

· Give courtesy call to QSE when commitments are made

Refer to Desktop Guide Reliability Unit Commitment Desk 2.20

	Note
	· Resources cannot be decommitted for just a portion of a DAM-Committed Interval, which is a one-hour interval.  

· ERCOT may only decommit a Resource to resolve transmission constraints that are otherwise unsolvable or to maintain the reliability of the ERCOT System.  Qualifying Facilities (QFs) may be decommitted only after all other types of Resources have been assessed for decommitment. 

· If ERCOT communicates HRUC commitments and decommitments verbally to a QSE, then the same Resource attributes communicated programmatically must be communicated when ERCOT gives a verbal Resource commitment or decommitment.

· QSE’s shall acknowledge the notice of commit or decommit by updating their COP.

	HRUC  Decommitted

Resources
	REVIEW REFERENCE DISPLAY:

Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP RUC Commitment/Decommitment Summary
IF:

· If HRUC recommends decommitments; 

Determine if: 

· Outage related,
· Possible Network Model error/ Normal Breaker status variances,
· COP error for Combine Cycle configurations / JOU,
· Qualifying Facilities should be de-committed ONLY as a last resort, 
THEN:

· If this is a true decommitment:

· Confirm Decommitment

· List reason (most likely reason is ‘transmission outage’), a message window will pop up in DSP approval process if no reason is provided

· If Decommitment is error related:

· No action is required

	Note
	Canceling unintended RUC Commits must be completed before additional RUC Commitments are issued on the same Resource(s). Doing it after the new RUC Commitment cancels all RUC Commitments for the resource.

	Canceling

RUC

Commitments
	REVIEW REFERENCE DISPLAY:

Market Operation>Reliability Unit Commitment>HRUC Displays>DSI Displays>DSI Data Processes>DSI Operator Manual Commitment
IF:

· A Resource is RUC committed that needs to be canceled;
· Only cancel RUC commits if the ERCOT Operator Resource commitment was unintended.

THEN:

· Issue electronic Dispatch Instruction to cancel the RUC instruction
· Choose “CANCEL RUC COMMIT” as the Instruction Type

· Enter “unintended commitment” in other information
When issuing a VDI or confirmation, ensure the use of three-part communication:

· Issue the Operating Instruction

· Receive a correct repeat back

· Give an acknowledgement      


	Post
	Notice Type: Operational Information
Notice Priority: Low

Audience: Public
Typical ERCOT Website posting: 

Cancelled RUC commitment at timestamp [Date & Time] for [resource] for [Date & Time] due to unintended commitment.

	VSAT and RUC perform AC Analysis

	Note
	IF:

· RUC cannot complete the process;
THEN:

· Notify the Transmission and Security Desk Operator and additional personnel as required. 

	Validate
	REVIEW REFERENCE DISPLAY:

Market Operation>Reliability Unit Commitment>HRUC Displays>UC Displays>Output Display Menu>System Outputs>Summary

VERIFY:

· Input data

· Updated Time

· Results are reasonable

	Approval
	HRUC must be approved by XX:50

REVIEW REFERENCE DISPLAY:

Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP Execution Control Parameters

IF:

· The HRUC results are reasonable and after all necessary modifications have been made;

THEN:

· Sort the RUC Commitment column before approving so it shows commitments at the top of the screen that currently may be lower in the table but not shown in the window;
· Approve the results (all RUC commitment, operator manual commitment/decommit/blank out must have a reason, otherwise a message window will pop up), OR

IF:

· The results are unacceptable;

THEN:

· Click on Disapprove button, AND
· Follow the Manage HRUC Timeline Failure in the next section.

IF:

· Disapprove button was selected in error;

THEN:

· Contact Service Desk to open ticket for EMMS Production Support to correct it.

	After 

Approval
	AFTER:

· Approval button is pushed;

THEN:

· Double check display Market Participation>Physical Market>Market Results>HRUC> HRUC Results, 

· Make sure the records in this display matches data in display Market Operation>Reliability Unit Commitment>HRUC Displays >DSP Displays>DSP RUC Commitment/Decommitment Summary.
IF:

· Displays are different, the RUC commitments thought to be blanked out were sent out;

THEN:

· Notify the Service Desk to call the On-Call EMMS Production support, and
· Issue electronic Dispatch Instructions to cancel RUC instructions
When issuing a VDI or confirmation, ensure the use of three-part communication:

· Issue the Operating Instruction

· Receive a correct repeat back

· Give an acknowledgement

	Log
	Log actions taken.


3.5
Hold

	
	
	
	
	

	
	
	
	
	

	
	

	
	
	


	
	
	


	
	

	
	
· 
· 

· 

	

	
· 

· 
· 
· 
· 
· 
· 


· 

· 
· 
· 



	
	


3.6  Hold 


	
	
	
	
	

	
	
	
	
	

	
	

	
	
	


	
	
	


	
	

	
	

	

	
· 
· 

· 


· 

	

	
· 
· 

	

	
· 
· 

· 
· 
· 

	

	
· 
· 

· 
· 
· 

	


	
· 
· 

· 
· 
· 

	

	
· 
· 
· 
· 

· 
· 
· 

	
	


	

	

	
	
· 

· 
· 
· 


	
	


4.2
Tasks prior to Execution of DRUC

Procedure Purpose:  To make manual corrections for bad/suspect telemetry, load forecast modifications, or to commit Resources prior to running the RUC process.

	Protocol Reference
	5.1
	5.3(1)
	5.5.1
	

	Guide Reference
	
	
	
	

	NERC Standard
	TOP-002-4

R4, R4.2, R4.3
	
	
	


	Version: 2 
	Revision: 0
	Effective Date:  December 5, 2025


	Step
	Action

	By 13:00 each day, perform the following

	COP
	REVIEW REFERENCE DISPLAYS:

Market Participation>Physical Market>Market Operator Data> Missing COP Check>Market Participation>Monitoring>Event Manager>Events

VERIFY:

· “Missing COP Check” has automatically notified the QSEs of missing COPs; 

SELECT: 

· “START-NOW" in the Status column if not already completed by Market Operations. 

	Load Forecast
	Review the Day Ahead Load Forecast in the EMS:

IF:

· Adjustments need to be made in the EMS;

THEN:

· Adjust using the following: (Refer to Desktop Guide RUC Section 2.17)

Reference Displays:

· Load Forecast 

· Similar Day Function

· Load Forecast Scaling functions

· Perform load scaling or

· Perform peak scaling or

· Perform factor scaling

· Manually override forecast value(s)

· Notify the Shift Supervisor if an invalid Load Forecast exists for the study period of DRUC.

	Outage

Notes/Off-Line Studies
	IF:

· Resources are needed for identified Voltage issues;
THEN:

· Once COPs have been updated, identify the appropriate resources that can be utilized if needed.

	Review
	REVIEW REFERENCE DISPLAY:

Market Operation>EMS Interface>EMSI Workflow Parameters 

IF:

· The EMSI Workflow Controller (Time Stamped – runs XX:50  every hour) function (data transfer between EMS and MMS) and Load Forecast are NOT running (should be continuous);

THEN:

· Notify Service Desk and Control Room Staff.

	By 13:30 each day, perform the following

	Note
	· 
· By default, Resources without an entry in COP are considered to have a Resource Status of OUT and are unavailable in RUC Procedure.

	WRUC
	IF:

· Prior to 1330, ERCOT may issue a WRUC instruction to a QSE that a Resource is required to be On-Line for all or part of a future Operating Day;

THEN:

· The QSE may self-commit the Resource for the WRUC instructed hours by updating the Resource’s COP to reflect the appropriate On-Line Status for the WRUC hours prior to the DRUC process execution, OR

· The Resource will be committed as part of the DRUC process for all WRUC-instructed hours not DAM-committed or QSE self- committed.

	By 14:00 each day, perform the following

	Note
	As time permits, contact QSEs that have NOT submitted a COP for the DRUC study period.

	Long Lead Times
	Identify resources that have a lead-time greater than the DRUC timeline, WRUC results should be utilized for identifying resources with long lead-times. A Resource with a WRUC commitment can be self-committed or offered into the DAM.
IF:

· Resources are identified;

THEN:

· Issue VDI RUC Commit on the necessary resource(s) as needed.

IF:

· Resource is self-committed or DAM-committed, 
THEN:

· DRUC instructions will NOT be issued in DRUC.
IF:

· Resource is not self-committed or DAM-committed, 
THEN:

· A RUC instruction will be required for the required hours in DRUC.

IF:

· A Resource with a WRUC instruction that isn’t issued a RUC instruction has the flexibility to request a decommit.
AND:

· Resource has not updated their COP for instructed hour before DRUC is executed.
THEN:

· Issue DRUC committment on the Resource

	By 14:25 each day, perform the following

	Note
	If the DAM did not complete by 1330, then DRUC will be delayed.  MPs need an hour between the completion of DAM and the opening of DRUC to update COPs.

	Verify
	Verify that the DAM has completed.

IF:

· DAM will not complete until after 1430;

THEN:

· Follow the “Manage DAM/DRUC Timeline Deviation/Failure” procedure.

	Setting parameters for ONLINE
	REVIEW REFERENCE DISPLAY:

System Administration>Data Management

Verify that “Connect to Schema” is set to “ONLINE”.

	Verify
	REVIEW REFERENCE DISPLAYS:

Market Operation>EMS Interface>EMSI Workflow Parameters

Market Operation>EMS Interface>EMSI Workflow Messages

EMSI has completed successfully within the last hour 

Market Operation>Reliability Unit Commitment>DRUC Displays>UC Displays>DRUC UC Execution Control Parameters

Market Operation>Reliability Unit Commitment>DRUC Displays>NSM Displays>NSM Execution Control Parameters

Market Operation>Reliability Unit Commitment>DRUC Displays>DSI Displays>DSI Execution Control Parameters 

· “Retrieve MF Interface Data” flag set to “Yes”.

· “Retrieve MI Interface Data” flag set to “Yes”.

· “Retrieve EMS Interface Data” flag set to “Yes”.

· “Check Market Status set to “Yes”,

· “Use Save case set to “No”

	At ~14:32 each day, perform the following

	Note
	The DSI sequence should never be started or still be running when a SCED sequence is running.

	DSI
	EXECUTE:

· The DSI sequence

VERIFY:

· For error or warning messages and take necessary action if needed to correct the errors,

· The input data is properly transferred. 

If NOT: 

Contact EMMS production support personnel immediately to determine the cause and expected time of resolution.

	
	



	E-Tags
	REVIEW REFERENCE DISPLAY:

Market Operation>Reliability Unit Commitment> DRUC Displays> DSI Displays> DSI Data Processes> DSI DC Tie Schedule 

Market Operation>Reliability Unit Commitment> DRUC Displays> DSI Displays> External Input Data> MI COP Verify that E-tags are being imported into the MMS.
IF:

· Individual schedules need to be reviewed;

THEN:

· Go to the MI COP display and filter ‘ERCOT’ as the QSE name

	Verify
	· Identify and correct Bad/Suspect Telemetry

· Modify Input for Block Load Transfer (BLT) movement

· Modify Input for Verbal Dispatch Instructions

Refer to Desktop Guide RUC Section 2.3

	Manual

Commitment
	REVIEW REFERENCE DISPLAY:

Market Operation>Reliability Unit Commitment> DRUC Displays> DSI Displays>DSI Data Processes>DSI Operator Manual Commitment

IF:

· Additional resources are needed to solve for voltage issues;

THEN:

· Consult with the Operations Support Engineer and/or the Transmission and Security Desk Operator to determine which resources should be RUC committed,  AND 
· Determine the temporal constraints for each of the units. 
IF:

· The resource start-up time doesn’t allow enough time to re-evaluate the need for its commitment in future HRUC Study Periods;

THEN:

· Filter for the unit 

· Change ‘Auto’ to ‘On’,

· List reason.

	Set 

Flags
	REVIEW REFERENCE DISPLAY:

Market Operation>Reliability Unit Commitment>DRUC Displays>DSI Displays>DSI Execution Control Parameters 

IF: 

· Manual changes have been made to the DRUC input data; 

CHANGE:

· The appropriate flags are set to prevent the data from being over-written.

· “Retrieve MF Interface Data set to No”, 

· “Retrieve MI Interface Data set to No”, 

· “Retrieve EMS Interface Data set to No”, OR

· “Use Save case set to “Yes”

	Execute
	REVIEW REFERENCE DISPLAYS:

Market Operation>Reliability Unit Commitment>DRUC Displays>Workflow>DRUC Workflow

Market Operation>Reliability Unit Commitment>DRUC Displays>Workflow>DRUC Workflow Messages

Execute the entire DRUC sequence (Run All).

	STNET Studies
	Notify:

· Operations Support Engineer to run NSA for each hour of the next operating Day.


4.3
Review, Approve and Post DRUC Results

Procedure Purpose:  To work collaboratively with Market Operations Support Personnel in reviewing, and if necessary, modifying DRUC data, to approve and post the final DRUC results.

	Protocol Reference
	4.4.8
	5.1 (9)
	5.3(3)
	5.5.1(9)

	
	5.5.2
	5.5.3(2)
	6.4.9.1(3)
	

	Guide Reference
	
	
	
	

	NERC Standard


	IRO-008-3 

R1, R2, R3, R7
	TOP-001-6 R25
	TOP-002-4 R1, R2, R3, R4, R4.1,  R4.4, R5
	


	Version: 2 
	Revision: 0
	Effective Date:  December 5, 2025


	Step
	Action

	Note
	See Desktop Guide Common to Multiple Desks Section 2.16 if the savecase function fails when running RUC

	Monitor
	REVIEW REFERENCE DISPLAYS:

Market Operation>Reliability Unit Commitment>DRUC Displays>Workflow>DRUC Workflow

Market Operation>Reliability Unit Commitment>DRUC Displays>Workflow>DRUC Workflow Messages

	Review
	REVIEW REFERENCE DISPLAY:

Market Operation>Reliability Unit Commitment>DRUC Displays>UC Displays>Output Display Menu>System Outputs>Summary 

When DRUC has completed.  If necessary, work with Market Operations and Operations Support Engineer to review the results.

· Monitor the DRUC Workflow display to determine when it is complete, 

ENSURE: 
· The workflow has completed before the study is approved and published,  

IF:

· The study is approved before it completes,

· Incorrect RUC deployments are sent to QSE’s 

THEN:
· Make hotline call to notify QSE’s that deployments for DRUC are invalid,

· Notify the Director Control Room Operations and/or Designee immediately,

· Abnormal system condition in the summary display after IUC (Initial Unit Commitment component of MMS) and NCUC (Network Constrained Unit Commitment component of MMS). 

· For Under Generation, prepare for following “DRUC Committed Units” section of this procedure 

· For Over generation, check for COP or Load Forecast errors

· For System Lambda greater than $10, check intermediate NSM (Network Security Manager Component of MMS) results for constraint violation. 

For abnormal constraints in the NSM outputs and abnormal commitments in IUC and NCUC outputs, refer to Desktop Guide RUC  Section 2.6, step 5.

	Note
	· Resources with NO Current Operating Plan (COP) entry are considered as “Unavailable” in RUC.

· Resources with “EMR” Resource status can only be RUC committed during Emergency conditions.

	System Summary
	REVIEW REFERENCE DISPLAYS:

Market Operation>Reliability Unit Commitment>DRUC Displays>UC Displays>Output Display Menu>System Outputs>Summary

Market Operation>Reliability Unit Commitment>DRUC Displays>UC Displays>Output Display Menu>System Outputs>Summary Line Flow

DETERMINE IF:

· The load forecast is reasonable for each hour,

· Any under/over generation;

THEN:

· Be aware of these when running HRUC. 

	

	



· 

· 
· 
· 
· 


· 

· 
· 
· 



	


	


· 

· 
· 
· 
· 

	Violated Constraints
	REVIEW REFERENCE DISPLAYS:

Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP Binding Constraint Summary

Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP Constraint Summary
REVIEW:

· Violated constraints.  If needed, notify Operations Support Engineer to determine the validity; 

IF:

· Invalid, no further action is required,

· Valid;

THEN

· Locate the constraint on the DSP Constraint Summary display,

· Create a Suggestion Plan for the identified violated constraint

· Review the temporal constraints of the suggested resources

· If resource start-up time allows enough time to re-evaluate the need for its commitment, be aware of these conditions when running HRUC,

· RUC commit resources as needed prior to DRUC approval if needed due to temporal constraints.

IF:

· Valid; AND no Suggestion Plan or Resource is available to commit within the timeframe of the violated constraint,

THEN:

· Notify Operations Support Engineer and Transmission and Security Desk Operator to determine if an outage can be withdrawn within the timeframe, 

IF:

· No outage can be withdrawn within the timeframe,

THEN:

· Notify Operations Support Engineer to develop a Congestion Management Plan and provide it to the TO and Transmission and Security Desk Operator,

· Notify Shift Supervisor to contact the Director Control Room Operations and/or Designee of actions taken

Refer to Desktop Guide RUC Section 2.6.

	Note
	RUC Desk Operators can decide to postpone a commitment if the startup time is well into the future. It will be left up to future HRUC solutions to commit the unit.

	DRUC Committed

Units
	REVIEW REFERENCE DISPLAYS:

Market Operation>Reliability Unit Commitment>DRUC Displays>DSI Displays>External Input Data>MF Generator Parameter
Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays>DSP RUC Commitment/Decommitment Summary
IF:

· DRUC recommends the commitment of any unit;
THEN:

· Determine the validity,

· Determine the temporal constraints for each of the units,

IF:

· The resource start-up time allows enough time to re-evaluate the need for its commitment in future HRUC Study Period, AND 

· There is no reliability reason requiring the resource commitment decision to be made immediately;

THEN:

· De-select the resource prior to approving the DRUC study by changing ‘Commit’ to ‘blank’ and list reason.

IF:

· There is reliability reason requiring the resource commitment decision to be made immediately;

· Resources with long start-up times

· Resources returning from outages

· Congestion or Capacity deficiencies that may create HRUC performance issues

THEN:

· Log the reason for not de-selecting the resource.
NOTE:  A reason must be entered for commit, decommit, uncommitting, examples below:

· Evaluate later (should be used when waiting until the last possible hour to commit)

· Short start (should be used for units that can start within 1 hour)

· Voltage support

· Valley import

· Constraint name (SLWSCRL5) * Do not use special characters

When issuing a confirmation, ensure the use of three-part communication:

· Issue the Operating Instruction

· Receive a correct repeat back

· Give an acknowledgement



	Excess Generation
	During periods of low load and excess generation:

PERIODICALLY REVIEW:

· Splunk Dashboard Viewer under the MOS_DEV folder:

· “6 DRUC Capacity” which is based on the last ran DRUC

VERIFY:

· TOTAL_LOAD is less than SS_LASL,

IF:

· Load forecast is reasonable AND the decision can be made in the future,

THEN:

· Issue OCN for Excess Reserve Capacity
· Notify the Transmission and Security Desk Operator to make Hotline call to TOs
· Post message on the ERCOT Website
Q#87 - Typical Hotline Script for OCN for Excess Capacity
Typical ERCOT Website Posting:
ERCOT issued an OCN due to a projected excess reserve capacity for [HE XX – HE XX]. 

WHEN:

· Projected excess reserve capacity;

THEN:

· Making hotline call to QSEs

· Cancelling ERCOT Website posting

· Notify the Transmission and Security Desk Operator to make hotline call to TOs.

Q#88 - Typical Hotline Script to Cancel OCN for Excess Capacity


	DRUC

Committed 

For Capacity

Shortage
	IF:

· DRUC recommends Resource(s) for capacity;
THEN

· Determine if start-up time allows enough time to re-evaluate, and

· De-select the Resource(s) prior to approving the DRUC,

After DRUC is approved:

· Issue an OCN for projected reserve capacity shortage
· Notify the Transmission and Security Desk Operator to make Hotline call to TOs
· Post message on the ERCOT Website
Q#89 - Typical Hotline Script for OCN for committing capacity in DRUC
Typical ERCOT Website Posting:
ERCOT issued an OCN due to a projected capacity shortage for [HE XX – HE XX]. 

WHEN:

· Projected reserve capacity shortage no longer exists;

THEN:

· Making hotline call to QSEs

· Cancel ERCOT Website posting

· Notify the Transmission and Security Desk Operator to make hotline call to TOs.

Q#90 - Typical Hotline Script cancellation for OCN for committing capacity in DRUC


	Manual Commitment
	REVIEW REFERENCE DISPLAY:

Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP RUC Commitment/Decommitment Summary

IF:

· Additional resources are needed to solve for transmission issues (such as voltage support) and were not picked up in the DRUC run, 
· The resource start-up time doesn’t allow enough time to re-evaluate the need for its commitment in the HRUC Study Period, OR

· A Resource was given a WRUC instruction and chose not to self-commit for all hours needed;

THEN:

· Change ‘blank’ to ‘Commit’

· List reason (capacity, constraint name or voltage issue).
· Give courtesy call to QSE when commitments are made

	Note
	Resources cannot be decommitted for just a portion of a DAM-Committed Interval, which is a one-hour interval.  ERCOT may only decommit a Resource to resolve transmission constraints that otherwise cannot be resolved.  Qualifying Facilities (QFs) may be decommitted only after all other types of Resources have been assessed for decommitment.

	DRUC  Decommitted

Resources
	REVIEW REFERENCE DISPLAYS:

Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP RUC Commitment/Decommitment Summary
IF:

· If RUC recommends commitments/decommitments; 

DETERMINE IF: 

· Outage related’
· Possible Network Model error’
· COP error for Combine Cycle configurations / JOU,
· Qualifying Facilities should be de-committed ONLY as a last resort; 
THEN:

· If this is a true decommitment:

· Confirm Decommitment

· List reason (most likely reason is ‘transmission outage’)

· If Decommitment is error related:

· No action is required

	Note
	Once you have completed your review of DRUC, consult with Market Operations to ensure they see no issues before approving. 

	Validate
	REVIEW REFERENCE DISPLAY:

Market Participation>Physical Market>SASM Market>AS Responsibility - QSE 

Market Operation>Reliability Unit Commitment>DRUC Displays>UC Displays>Output Display Menu>System Outputs>Summary

VERIFY:

· Input data

· Updated Time

· Results are reasonable

	Approval
	DRUC must be approved by 1600

REVIEW REFERENCE DISPLAY:

Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP Execution Control Parameters

IF:

· The DRUC results are reasonable after all necessary modifications have been made;

THEN:

· Sort the RUC Commitment column before approving so it shows commitments at the top of the screen that currently may be lower in the table but not shown in the window;
· Approve the results, OR

IF:

· The results are unacceptable;

THEN:

· Click on Disapprove button
· Follow the Manage DRUC Failure/Timeline Deviation procedure.

IF:

· Disapprove button was selected in error;

THEN:

· Contact Service Desk to open ticket for EMMS Production Support to correct it.

	Note
	If the RUC Desk Operator disapproves the results, the results will be saved in the database for future analysis and will not be published to the MPs.

	After 

Approval
	AFTER:

· Approval button is pushed;

THEN:

· Double check display Market Participation>Physical Market>Market Results>DRUC> DRUC Results, 

· Make sure the records in this display matches data in display Market Operation>Reliability Unit Commitment>DRUC Displays >DSP Displays>DSP RUC Commitment/Decommitment Summary.
IF:

· Displays are different, the RUC commitments thought to be blanked out were sent out;

THEN:

· Notify the Service Desk to call the On-Call EMMS Production support, and
· Issue VDIs to cancel RUC instructions
When issuing a VDI or confirmation, ensure the use of three-part communication:

· Issue the Operating Instruction

· Receive a correct repeat back

· Give an acknowledgement

	Canceling

RUC

Commitments
	REVIEW REFERENCE DISPLAY:

Market Operation>Reliability Unit Commitment>HRUC Displays>DSI Displays>DSI Data Processes>DSI Operator Manual Commitment 

IF:

· A Resource is RUC committed and needs to be canceled;
· Only cancel RUC commits if the ERCOT Operator Resource commitment was unintended.
THEN:

· Issue an electronic Dispatch Instruction confirmation to cancel the RUC instruction
· Choose “CANCEL RUC COMMIT” as the Instruction Type

· Enter “unintended commitment” in other information

When issuing a VDI or confirmation, ensure the use of three-part communication:

· Issue the Operating Instruction

· Receive a correct repeat back

· Give an acknowledgement


4.5
Blank

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	


	
	
	


	
	

	

	

· 

· 
· 
· 
· 



	
	

	

	
· 
· 

· 
· 
· 



	


	
· 
· 

· 

· 

· 

	

	
· 
· 

· 
· 
· 




4.6
DAM Failure

Procedure Purpose:  When DAM has failed.

	Protocol Reference
	4.1.2(2)
	4.5.2(2)
	5.1(11)
	5.2.2.2

	Guide Reference
	
	
	
	

	NERC Standard
	
	
	
	


	Version: 2 
	Revision: 0
	Effective Date:  December 5, 2025


	Step
	Action

	DAM Failure
	IF:

· Notified by Market Operations that DAM has been aborted;

THEN:

· Notify Shift Supervisor and Resource Desk

· Issue a Watch by making a Hotline call to QSEs

· 
· Market Operations will post message on the ERCOT Website
· Notify the Transmission and Security Desk Operator to make Hotline call to TOs

Q#100 - Typical Hotline Script for Watch for DAM Failure


	
	
· 

· 

	Cancel

Watch
	WHEN:

· 
· HRUC has completed for the next day study period;

THEN:

· Cancel the Watch by making Hotline call to QSEs

· Cancel ERCOT Website posting

· Notify the Transmission and Security Desk Operator to make Hotline call to TOs

Q#101 - Typical Hotline Script to Cancel Watch for DAM Failure



6.1
Market Notifications

Procedure Purpose: Guidelines for issuing Emergency Conditions and the four possible levels: Operating Condition Notices (OCN), Advisories, Watches, and Emergency Notices.

	Protocol Reference


	6.3.3
	6.5.9.3
	6.5.9.3.1
	6.5.9.3.2

	
	6.5.9.3.3
	6.5.9.3.4
	
	

	Guide Reference
	4.2.1
	4.2.2
	4.2.3
	4.2.4

	NERC Standard
	
	
	
	


	Version: 2 
	Revision: 0
	Effective Date:  December 5, 2025


	Step
	Action

	Note
	· ERCOT is in an Emergency Condition whenever ERCOT Transmission Grid status is such that a violation of security criteria presents the threat of uncontrolled separation or cascading Outages and/or large-scale service disruption to Load (other than Load being served from a radial transmission line) and/or overload of a Transmission Element, and no timely solution is obtainable through SCED or CMPs.

· Consider the severity of the potential Emergency Condition prior to the issuance of a notification.  The severity of the Emergency Condition could be limited to an isolated local area, or the condition might cover large areas affecting several entities, or the condition might be an ERCOT-wide condition potentially affecting the entire ERCOT System.

· The sequence of notifications issued may vary due to changing system conditions or other operational issues and it may be necessary to skip certain notifications due to the severity of the situation.

	Operating Condition Notice (OCN)

	Note
	OCN’s are used to inform Market Participants of a possible future need for more Resources due to conditions that could affect ERCOT System reliability.  OCNs are for informational purposes only and may solicit additional information to determine whether the issuance of an Advisory, Watch, or Emergency Notice is warranted. OCNs serve as a reminder to QSEs and TSPs that some attention to the changing conditions may be warranted.

	1
	As instructed by the Shift Supervisor or when appropriate, issue an OCN.  The OCN can be issued for any of the following reasons:

· Insufficient Resources to meet forecasted conditions

· There is a projected reserve capacity shortage in DRUC that could affect reliability and may require more Resources

· When extreme cold weather is developing and forecasted to impact the ERCOT Region
· When extreme hot weather is forecasted to impact the ERCOT Region 

· When a Hurricane or Tropical Storm is developing and forecasted to impact the ERCOT Region

· Unplanned transmission Outages that may impact reliability

When anticipated adverse weather conditions are forecasted, ERCOT may confer with TOs and QSEs regarding the potential for adverse reliability impacts and contingency preparedness

	Advance Action Notice (AAN)

	Note
	Outage Adjustment Evaluation (OAE)

Outage Schedule Adjustment (OSA)

An AAN is a type of OCN, ERCOT may issue an AAN in anticipation of a possible Emergency Condition. An AAN will identify actions ERCOT expects to take to address the condition unless the need for ERCOT action is alleviated by QSE and/or TSP actions or by other system developments.

	1
	As instructed by the Shift Supervisor and in coordination with Outage Coordination and Operations Support, issue an AAN.  The AAN can be issued for any of the following reasons:

· Insufficient Resources to meet forecasted conditions

· There is a projected reserve capacity shortage in DRUC that could affect reliability and may require more Resources

· When extreme cold weather is developing and forecasted to impact the ERCOT Region
· When extreme hot weather is forecasted to impact the ERCOT Region

· When a Hurricane or Tropical Storm is developing and forecasted to impact the ERCOT Region 

· Unplanned transmission Outages that may impact reliability

When anticipated adverse weather conditions are forecasted, ERCOT may confer with TOs and QSEs regarding the potential for adverse reliability impacts and contingency preparedness

	ADVISORY

	1
	As instructed by the Shift Supervisor or when appropriate, issue an Advisory.  The Advisory can be issued for any of the following reasons:

· When the probability of an approaching Hurricane or Tropical Storm impacting the ERCOT Region increases, and concerns exist to escalate awareness  

· When the probability of extreme cold weather impacting the ERCOT Region increases, and concerns exist to escalate awareness
· When the probability of extreme hot weather impacting the ERCOT Region increases, and concerns exist to escalate awareness

· When conditions are developing or have changed and more Ancillary Services will be needed to maintain current or near-term reliability

·  ERCOT exercises its authority to increase Ancillary Service requirements above the quantities originally specified in the Day-Ahead Market (DAM) in accordance with ERCOT Procedures

· When extreme weather or ERCOT System conditions require more lead-time than the normal Day-Ahead Market (DAM) allows

· Transmission system conditions are such that operations within security criteria are not likely or possible because of Forced Outages or other conditions unless a CMP exists

· Loss of communications or control condition is anticipated or significantly limited

· ERCOT may require information from QSEs representing Resources regarding the Resources’ fuel capabilities. Requests for this type of information shall be for a time period of no more than seven days from the date of the request

	WATCH

	1
	As instructed by the Shift Supervisor or when appropriate, issue a Watch.  The Watch can be issued for any of the following reasons:

· A reserve capacity shortage is projected with no market solution available that could affect reliability

· When an approaching Hurricane or Tropical Storm is imminent and anticipated to have an adverse impact on the ERCOT Region

· When impacts from extreme cold weather is imminent and anticipated to have an adverse impact on the ERCOT Region
· When impacts from extreme hot weather is imminent and anticipated to have an adverse impact on the ERCOT Region  

· Conditions have developed such that additional Ancillary Services are needed in the Operating Period

· 
· Market-based congestion management techniques embedded in SCED will not be adequate to resolve transmission security violations

· Forced Outages or other abnormal operating conditions have occurred, or may occur that require ERCOT to operate with active transmission violations of security criteria as defined in the Operating Guides unless a CMP exists

· The SCED process fails to reach a solution, whether or not ERCOT is using one the measures in Failure of the SCED Process.

· The need to immediately procure Ancillary Services from existing offers

· ERCOT may instruct TOs to reconfigure transmission elements as necessary to improve the reliability of the system

	EMERGENCY NOTICE

	1
	As instructed by the Shift Supervisor or when appropriate, issue an Emergency Notice.  The Emergency Notice can be issued for any of the following reasons:

· Loss of Primary Control Center functionality

· Load Resource deployment for North-Houston voltage stability

· ERCOT cannot maintain minimum reliability standards (for reasons including fuel shortages) during the Operating Period using every Resource practically obtainable from the market

· Immediate action cannot be taken to avoid or relive a Transmission Element operating above its Emergency Rating

· ERCOT forecasts an inability to meet applicable reliability standards and it has exercised all other reasonable options

· A transmission condition has been identified that requires emergency energy from any of the DC-Ties or curtailment of schedules

· The Transmission Grid is such that a violation of security criteria as defined in the Operating Guides presents the threat of uncontrolled separation or cascading outages, large-scale service disruption to Load (other than Load being served from a radial transmission line) and/or overload of Transmission Elements and no timely solution is obtainable through SCED or CMP

· When extreme cold weather is beginning to have an adverse impact on the ERCOT System
· When extreme hot weather is beginning to have an adverse impact on the ERCOT System
· When a Hurricane or Tropical Storm is beginning to have an adverse impact on the System

	Operating Condition Script

	Hotline
	Notify QSEs of Notice

#46 - Typical Hotline Script for Operating Condition [OCN/Advisory/Watch/Emergency]

	Post
	· All notices must be posted on the ERCOT Website.

· For “free form” messages, the “Notice Priority” will be specified as follows:

· Operational Information/OCN type messages – low priority

· Advisory/Watch type messages – medium priority

· Emergency type messages – high priority

	Hotline Cancellation
	#47 - Typical Hotline Script to Cancel Operating Condition [OCN/Advisory/Watch/Emergency]

	Log
	Log all actions.


Document Control

Manual Change History

	Procedure
	Ver/Rev
	Reason for Issue
	Effective Date

	All Sections
	2.0 / 0
	RTC+B Implementation 

All procedures in this manual have been reviewed
	December 5, 2025


