Power Operations Bulletin # 2007
ERCOT has posted/revised the Transmission and Security manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html
1.1
Purpose
This procedure provides the ERCOT System Operator assigned to the Transmission and Security Desk with detailed procedures required for performing duties assigned to that position.  

The Transmission and Security Desk Operator shall ensure that the transmission system is operated so that instability, uncontrolled separation, or cascading outage will not occur as a result of the most severe single Contingency.  The Transmission and Security Desk Operator directs actions or issues Dispatch Instructions / Operating Instructions to the ERCOT Transmission Operators or other Market Participants as required while maintaining or restoring the security/reliability of the ERCOT System.

1.2
Scope
The instructions contained in this procedure are limited to those required for the Transmission and Security Desk.  Instructions for other ERCOT control room positions are contained in separate procedures, one for each position.  This procedure does not imply that the duties contained herein are the only duties to be performed by this position.  The individual assigned to this position will be required to follow any other instructions and to perform any other duties as required or requested by appropriate ERCOT supervision.  

Although the steps within the procedures are numbered, the numbering is for indexing purposes and are not sequential in nature.  The System Operator will determine the sequence of steps, exclude steps, or take any additional actions required to ensure system security based on the information and situational awareness available during both normal and Emergency Conditions.  

2.1
System Operator Responsibility and Authority

Procedure Purpose: To ensure the System Operators know their roles, responsibility, and authority.

	Protocol Reference
	6.5.1.1
	6.5.1.2(3)
	6.5.2
	6.5.3(1)

	
	6.5.9(3)
	
	
	

	Guide Reference
	4.5.2(1)
	
	
	

	NERC Standard
	
	
	
	


	Version: 2 
	Revision: 0
	Effective Date:  December 5, 2025


ERCOT ISO as a Transmission Operator (TOP), the single Balancing Authority (BA), and only Reliability Coordinator (RC) registered within the ERCOT Interconnection shares all information between these roles simultaneously and acts concurrently as a single entity, satisfying coordination between the TOP, BA, and RC.

The System Operator (SO) shall, in accordance with NERC Reliability Standards and ERCOT Protocols, have clear decision-making authority to act to address the reliability of its RC Area by direct actions or by issuing Dispatch Instructions / Operating Instructions during both normal and emergency conditions.  These actions shall be taken without delay and may include shedding of firm load without obtaining approval from higher-level personnel.  

The SO on duty is, in accordance with the ERCOT Protocols, Operating Guides, and NERC Reliability Standards, and acting as the BA, TOP, and RC shall request and receive information required to continually monitor the operating conditions which will assure security and reliability of the ERCOT System.

The SO issues Dispatch Instructions / Operating Instructions for the Real-Time operation of Transmission Facilities to a TO and a QSE for the Real-Time operation of a Resource. 

The SO shall, on an ERCOT-wide basis, coordinate the ERCOT System Restoration (Black Start) Plan.  The SO shall implement the Black Start Plan and shall direct the reconnection efforts of the islands, established by restoration activities.  

The SO shall consider all equipment operating limits when issuing Dispatch Instructions / Operating Instructions.  During Emergency Conditions, the SO may verbally request QSEs to operate its Resources outside normal operating parameters.  If a Dispatch Instruction / Operating Instruction conflicts with a restriction placed on equipment by a TO or QSE to protect the integrity of equipment, ERCOT shall honor the restriction.

The SO performs security analyses on a Day Ahead and Real-Time basis and ensures all Forced Outages are entered into the Outage Scheduler. The SO shall obtain or arrange to provide Emergency Energy over the DC Tie(s) on behalf of ERCOT.

The SO shall issue appropriate OCN’s, AAN’s, Advisories, Watches, and Emergency Notices, and coordinate the reduction or cancellation of clearances, re-dispatch of generation, and request, order, or take other action(s) that the SO determines is necessary to maintain safe and reliable operating conditions on the ERCOT System in accordance with ERCOT Protocols, Operating Guides, and NERC Reliability Standards.  The SO will implement and terminate ERCOT Time Corrections and will determine the need for and implement the operation of a QSE on Constant Frequency Control for loss of ERCOT’s load frequency control system.

2.4
Switching Control Centers


Procedure Purpose: To provide notice to the TOs when ERCOT is working from the Alternate Control Center.

	Protocol Reference 
	
	
	
	

	Guide Reference 
	
	
	
	

	NERC Standard
	
	
	
	


	Version: 2 
	Revision: 0
	Effective Date:  December 5, 2025


	Step
	Action

	Hotline 

Call
	When transferring operations from primary site to alternate site (and vice versa).  Make the following Hotline call to TOs:

T#19 - Typical Hotline Script for working from Alternate site
T#20 - Typical Hotline Script for working from Primary site

	ERCOT Website
Posting
	Verify with the Real-Time Desk Operator that posting was made.

Typical ERCOT Website Posting Script for working from Alternate site
ERCOT is working from alternate control center.  

Typical ERCOT Website Posting Script for working from Primary site
ERCOT is working from primary control center.  

	Log
	Log all actions.


3.2
Alarm Processing and Acknowledgement


Procedure Purpose: To monitor and acknowledge system alarms.

	Protocol Reference 
	3.10.7.5.1(5)
	6.5.7.1.6(1)
	
	

	Guide Reference 
	
	
	
	

	NERC Standard
	
	
	
	

	
	
	

	Version: 2 
	Revision: 0
	Effective Date:  December 5, 2025


	Step
	Action

	Note
	The Alarm Displays for ERCOT are primarily used to show changes in equipment status.

The alarms are categorized based on alarm criticality and prioritization on the Alarm Summary Display:

	Categories
	Tab 1: 345 KV Transmission Equipment Status

Tab 2: 138 KV Transmission Equipment Status

Tab 3: Generator Breaker, AVR, CAPS, REACTOR and RAS Status

Tab 4: RLC alerts

Tab 5: Transmission Line Overloads - Voltage Violations - Critical Alarms

Tab 6: QKNET alarms

Tab 7: ICCP status 

Tab 8: All other alarms

	1
	Monitor the Alarm Summary Display pages 3, 6 and 7 as necessary to confirm system reliability status.

	2
	Take appropriate action as system conditions warrant.

	3
	Coordinate with the Real-Time Desk Operator to clear the alarms approximately every 24 hours or as needed.


3.3
Analysis Tool Outages

Procedure Purpose: To notify TOs to monitor SOLs, IROLs and GTCs in their areas during tool outages.  Also, to ensure proper notification is made for these failures along with notification for ICCP, ERCOT Website and Outage Scheduler outages on the ERCOT systems.
	Protocol Reference
	6.3.3(1)
	
	
	

	Guide Reference
	
	
	
	

	NERC Standard


	IRO-008-3

R4
	IRO-018-1(i)

R2, R2.2
	NUC-001-4

R4, R4.3, R9, R9.3, R9.3.4, R9.4, R9.4.1
	TOP-001-6

R9, R13

	
	TOP-010-1(1)

R3, R3.2
	
	
	


	Version: 2 
	Revision: 0
	Effective Date:  December 5, 2025


	Step
	Action

	STATE ESTIMATOR/RTCA

	1
	IF:

· The SE/RTCA has not solved; 
THEN:

· Coordinate with the Operations Support Engineer for up to 15 minutes from last successful solution;

· Refer to Desktop Guide Transmission Desk Section 2.1 to assist with troubleshooting,

IF:

· The SE/RTCA remains partially solved or unsolved; 
THEN:

· Make notifications,

· Continue to monitor the system as possible,

· Coordinate with the Operations Support Engineer to ensure a Real-time Assessment (RTA) is performed within 30 minutes of the last SE/RTCA solution and within 30 minutes of each RTA conducted thereafter,

· Refer to section 3.7 to ensure congestion management continues with manual RTAs. 

	2
	Must be completed within 30 minutes of the tool outage:
Notify the two master QSEs that represent the Nuclear Plants that ERCOTs [State Estimator/RTCA] is not functioning and is expected to be functional within approximately [# minutes].

	3
	If the State Estimator/RTCA has NOT solved within the last 30 minutes: 

Make a Hotline call to issue an Advisory to the TOs:

T#21 - Typical Hotline Script for Advisory for State Estimator/RTCA Not Solved

	4
	Notify the Real-Time Desk Operator to make Hotline call to QSEs.

	5
	Post Advisory message on the ERCOT Website.

Typical Posting Script:
Advisory issued due to ERCOT’s [State Estimator/RTCA] is currently unavailable.

	6
	Once the State Estimator/RTCA is operational:

Make a Hotline call to cancel the Advisory to the TOs:

T#22 - Typical Hotline Script to Cancel Advisory for State Estimator/RTCA

	7
	Notify the two master QSEs that represent the Nuclear Plants that the [State Estimator/RTCA] is now functional.

	8
	Notify the Real-Time Desk Operator to make Hotline call to QSEs.

	9
	Cancel Advisory message on the ERCOT Website.

	Log
	Log all actions.

	Voltage Security Assessment Tool (VSAT) and Transient Security Assessment Tool (TSAT)

	1
	IF:

· VSAT and/or TSAT has not run in the last 15 - 20 minutes, OR
· VSAT and/or TSAT is indicating “Stopped”, “Incomplete”, or “Server Invalid”;

THEN:

· Continue to monitor the flows in RTMONI

· Rerun the RTNET, RTCA, and RTDCP (VSA)

· Notify the Operations Support Engineer



	2
	If VSAT and/or TSAT has NOT solved within the last 30 minutes: 

Make a Hotline call to issue an Advisory to the TOs:

T#23 - Typical Hotline Script for Advisory for VSAT and/or TSAT Tool outage

	3
	Notify the Real-Time Desk Operator to make Hotline call to QSEs.

	4
	Post Advisory message on the ERCOT Website.

Typical ERCOT Website Posting:
Advisory issued due to ERCOT’s Voltage Security Assessment Tool [and/or] Transient Security Assessment Tool is currently unavailable.

	5
	IF:

· A major topology change occurs while VSAT and/or TSAT is unavailable;

THEN:

· Notify and request the Operations Support Engineer to run a manual study to verify limits

· Update any limits in RTMONI or manual Real Time Assessments as necessary.

· Take action as necessary

	6
	Once VSAT and/or TSAT is operational:

Make a Hotline call to cancel the Advisory to the TOs:

T#24 - Typical Hotline Script to Cancel Advisory for VSAT and/or TSAT Tool

	7
	Notify the Real-Time Desk Operator to make Hotline call to QSEs.

	8
	Cancel Advisory message on the ERCOT Website.

	Log
	Log all actions.

	ICCP, ERCOT Website, and Outage Scheduler Outages

	1
	For any planned or unplanned outage of ERCOT’s ICCP, ERCOT Website (affecting COP submissions) or the Outage Scheduler lasting longer than 30 minutes, notifications to TOs are required.

IF:

· ERCOT’s ICCP, ERCOT Website (affecting COP submissions) or the Outage Scheduler has a planned or unplanned outage that is expected to last 30 minutes or more;

THEN:

· Make a Hotline call to the TOs:

T#97 - Typical Hotline Script for ERCOT’s ICCP, ERCOT Website, or the Outage Scheduler Planned or Unplanned Outage

	2
	Once ERCOT operational:

Make a Hotline call to notify TOs:

T#98 - Typical Hotline Script for ERCOT’s ICCP, ERCOT Website or Outage Scheduler back to Normal

	Log
	Log all actions.


3.5
Geomagnetic Disturbance Notification 

Procedure Purpose:  To disseminate forecasted and current space weather information when a K-7 and greater or G3 and greater GMD storm has entered a Warning and / or Alert.

	Protocol Reference
	
	
	
	

	Guide Reference
	4.7
	
	
	

	NERC Standard
	EOP-010-1

R1, R1.1, R2
	
	
	


	Version: 2 
	Revision: 0
	Effective Date:  December 5, 2025


	Step
	Action

	Note
	· The Geomagnetic Disturbance Reference Document can be found in Section 2.13 of the Common to Multiple Desks Desktop Reference Guide.

· An Advisory is issued when a GMD Alert of K-7 or higher is issued, however the Advisory will not be canceled until the GMD Warning is canceled.

	1
	WHEN:

· Notified by the Shift Supervisor that an Alert from the Space Weather Prediction Center has been issued for a K-7 and greater or G3 and greater;

THEN:

· Issue an Advisory by making a Hotline call to TOs

· Post message on the ERCOT Website
· Notify the Real-Time Desk Operator to make Hotline call to QSEs

T#25 - Typical Hotline Script for Advisory for GMD Alert

Typical ERCOT Website Posting Script:

Advisory issued for a geomagnetic disturbance of [state K-Index level] until [time].

	Extend
	IF:

· The Alert is extended;

THEN: 

· Post message on the ERCOT Website and
· Cancel the older message
Typical ERCOT Website Posting:
The Space Weather Prediction Center has extended the Alert of [state level] until [time].

	K Level

Increases / Decreases
	IF:

· Notified by the Shift Supervisor that an Alert from the Space Weather Prediction Center has been increased or decreased for a K-7 and greater or G3 and greater;

THEN:

· Making a Hotline call to TOs

· Update message on ERCOT Website
· Notify the Real-Time Desk Operator to make Hotline call to QSEs

T#26 - Typical Hotline Script for GMD K- Level Increase/Decrease
Typical ERCOT Website Posting Script:

Advisory issued for a geomagnetic disturbance of [state K-Index level] until [time].

	Mitigating

Activities
	When suspected GMD activity is observed or reported by a TO, consider the following:

· Series capacitors are in-service (where installed)

· Delay Planned outages and return outaged equipment to service where possible, especially series capacitors

· Remove transformer(s) from service if imminent damage due to overheating

· Remove transmission line(s) from service especially the lines most influenced by GMD or the lines which show wide voltage swings

· Shed load as required

	Issues
	IF:

· Any TO reports equipment outages, misoperations, etc. from a GMD event;

THEN: 

· Coordinate an action plan, if necessary, 
· Report issues to Shift Supervisor

	Cancel
	WHEN:

· Notified by the Shift Supervisor that the GMD Warning has expired;

THEN:

· Cancel the Advisory by making a Hotline call to TOs

· Cancel message on ERCOT Website
· Notify the Real-Time Desk Operator to make Hotline call to QSEs. 

T#27 - Typical Hotline Script to Cancel Advisory for GMD

	Log 
	Log all actions.


4.1
Transmission Congestion Management

Procedure Purpose:  To verify and take corrective action for post-contingency overloads for various conditions.

	Protocol Reference
	3.10.4(2)
	6.1(4)
	6.4.9.1.2(1)
	6.5.5.2(1)

	
	6.5.7.1.10
	6.5.7.6.2.3(1)
	6.5.7.1.11
	6.5.7.8

	
	6.5.9(2)
	6.5.9.2(3)
	6.5.9.3.3
	6.5.9.3.4

	Guide Reference
	2.2.2
	
	
	

	NERC Standard


	EOP-011-4

R1, R1.1, R1.2, R1.2.4
	IRO-001-4

R1
	IRO-002-7

R5
	IRO-008-3

R2, R3, R5, R6

	
	TOP-001-6

R1, R7, R10, R10.1, R10.3, R10.4, R10.6, R14, R18, R25
	TOP-002-4

R2, R3
	VAR-001-5

R2, R3
	


	Version: 2 
	Revision: 0
	Effective Date:  December 5, 2025


	Step
	Action

	Note
	Although the steps within the procedure are numbered, the numbering is for indexing purposes and are not sequential in nature.  The System Operator will determine the sequence of steps, exclude steps, or take any additional actions required to ensure system security based on the information and situational awareness available during both normal and emergency conditions.  Refer to Section 2.6 of the Transmission and  Security Desktop Guide for the contingency solution results legend.

	
	

	SOL Comms
	If both methods of electronic communication of SOL exceedances are unavailable, refer to section 3.8, “SOL Exceedance Communications Thresholds”, above for criteria of manually communicating SOL exceedances identified below.  

	Authority
	ERCOT System Operators have the authority to take or direct timely and appropriate real-time action, up to and including shedding firm load to alleviate System Operating Limit (SOL) violations.  Following a separation from the Interconnection, and following automatic under-frequency load shedding, System Operators will also instruct TOs to shed additional load manually when there is insufficient capacity to restore system frequency.  

To include directing physical operation of the ERCOT Transmission Grid, including circuit breakers, switches, voltage control equipment, and Load-shedding equipment.

	Critical

Facilities
	Critical facilities are the ERCOT defined contingencies that show up after running Real Time Contingency Analysis (RTCA) as a post-contingency overload.  This list is in the EMS and an electronic copy is located on the MIS Secure site:

Select: Grid>Generation>Reliability Unit Commitment>Standard Contingency List’

Select “Standard Contingency List” Open the zip file>Open the CIM file>Select the Standard_Contingency_List tab and view the contingencies.

A potential critical facility becomes a critical facility when the contingency appears in RTCA as a post-contingency overload.

	Note
	Congestion Management techniques consist of:

· SCED

· Phase Shifters (shift factors are on the TCM display)

· Remedial Action Plan (RAP)

· Pre-Contingency Action Plan (PCAP)

· Mitigation Plan (MP) – enacted Post-Contingency

· Temporary Outage Action Plans (TOAP)

· Building a manual constraint 

· Non-Spin 

· ECRS

The electronic and hard copy for the RAPs, PCAPs, and MPs are to be considered current.  Should a conflict exist between the electronic and hard copy, the electronic version is to be used.

· This data can be viewed at ERCOT SharePoint > System Operations – Control Center > Quick Links > Remedial Action Schemes (RAS) and/or MP/PCAP/RAP,

· OCTOAPs are in the daily Outage Notes.

	Caution
	IF:

· At any time, the prescribed measures of congestion management techniques within this procedure fail to resolve the congestion, AND
· The transmission system is in an unreliable state

THEN:

· Issue an Emergency Notice

· See Operating Condition Script in Section 7.1

· Notify the Real-Time Desk Operator to make Hotline call to QSEs.

· Coordinated with the proper TO or QSE to return the system to a reliable state

	Log
	Log all actions.

	Constraint Shift Factor Cut Off
	Basecase and post-contingency constraints which do not have generator shift factors for units greater than or equal to 2% as indicated in EMS or indicate NOSCED are not activated in SCED.  

See Section 4.6 Mitigation Plan for additional details.

	Review Planned Outage Notes

	Non-Cascading

Condition
	Review daily outage notes:

IF:

· Studies indicate a high post-contingency overload (125% of Emergency rating or greater) due to a Planned outage AND it is not a cascading condition; 

THEN:

· Allow the outage

· Activate the constraint and step the constraint down by adjusting the %Rating (increments of 5%)



	Cascading

Condition
	IF:

· Studies indicate a high post-contingency overload (125% of Emergency rating or greater), AND it is a cascading condition, OR

· An unsolved contingency, OR

· A Basecase overload;

THEN:

· Take pre-posturing measures to reduce the flow before the outage is taken

· Use RTMONI if available on a GTC, OR

· Have a manual constraint created if needed

IF:

· Constraint is ineffective

THEN:

· Use HDL/LDL overrides as required to pre-posture for an expected Outage as last resort 

· Post message on the ERCOT Website anytime manual action is taken

· Notify Shift Supervisor and send an email to 1 ERCOT Shift Supervisors

Typical ERCOT Website Posting Script:
ERCOT is taking manual actions to pre-posture for a [69/138/345] KV outage in the [geographical area].

ONCE:

· Studies show that the post-contingency is below 125% of Emergency rating, unsolved contingency, or Basecase overload is resolved 

· Give approval for the outage, 

· Activate constraint, and

· Release manual override after SCED runs

· Cancel ERCOT Website posting.

	Log
	Log all actions.

	Evaluate Real Time Contingency Analysis (RTCA) Results

	1
	IF:

· A major topology change has occurred;

THEN:

· Re-run RTCA, VSAT and TSAT.
IF:

· A constraint needs to be controlled before the next SCED run

THEN:

· Manually run RTCA after activating the constraint, AND

· Manually execute the SCED process

	Log
	Log all actions.

	Post-Contingency Overloads

	1
	IF:

· A post-contingency overload is approaching 98% of its Emergency Rating;

THEN:

· Verify the contingency definition associated with the constraint is accurate and appropriate given the current state of the grid

· Verify SCADA is of similar magnitude to the pre-contingency value (MW and MVAR flows)

· Review the limits in DYNRTG static table to ensure that the telemetry of the lines is within the acceptable range.

	2
	IF:

· Inaccurate, 

· Indicate NOSCED, OR

· There is not a unit with at least a 2% shift factor;

THEN:

· DO NOT employ congestion management techniques, 
· Notify the Shift Supervisor and Operations Support Engineer to investigate or create a CMP.
· Acknowledge the constraint and list a reason using the drop-down box,

· The comment field should be used for additional information 

	3
	IF:

· Accurate, AND

· There is a unit with at least a 2% shift factor;

THEN:

· Verify no RAS (identified as RAS in EMS), or RAP exist

· Activate constraint

· Lower the value in the % Rating column in TCM to tighten the constraint as needed (minimum of 95%, excluding GTCs)

IF:

· A PST can help solve the congestion;

THEN:

· Activate the constraint until the PST is studied and moved.

	4
	IF:

· A post-contingency overload of 98% or greater of the Load Shed Rating exist with a RAP in place;

THEN:

· Activate the constraint to reduce the predicted post-contingency loading to no more than 98% of the Load Shed Rating;

IF:

· Constraint needs to be controlled within the next 5 minutes;

THEN:
· Manually run RTCA after activating the constraint,

· Manually execute the SCED process,

· Refer to “Managing Constraints in SCED”.

	Post-Contingency Overloads of Relay Loadability Rating

	1
	IF:

· A post-contingency overload is approaching 95% to 98% of its RELAY Loadability Rating (RLAY);

THEN:

· Verify SCADA is of similar magnitude to the Actual Basecase value (MW and MVAR flows)

· Example: Review the SCADA value with Actual (state estimation value)

	2
	IF:

· Inaccurate, 

· Indicate NOSCED, OR

· There is not a unit with at least a 2% shift factor;

THEN:

· DO NOT employ congestion management techniques, 
· Notify the Shift Supervisor and Operations Support Engineer to investigate or create a CMP.
· Acknowledge the constraint and list a reason using the drop-down box,

· The comment field should be used for additional information

	3
	IF:

· Accurate, AND

· There is a unit with at least a 2% shift factor;

THEN:

· Activate constraint

· Lower the value in the % Rating column in TCM to tighten the constraint as needed to the Emergency limit (2hr rating)

IF:

· A PST can help solve the congestion;

THEN:

· Activate the constraint until the PST is studied and moved.

	4
	IF:

· All applicable steps above have been completed, AND constraint is still exceeding its Relay Loadability Rating;

THEN:

· Seek to determine what unforeseen change in system condition has arisen and where possible, seek to reverse the action, 

· Coordinate with Operations Support Engineer to develop a mitigation plan,  

· Refer to Section 4.3, Closely Monitored SOLs, AND 

· Notify Shift Supervisor to contact the Director Control Room Operations and/or Designee to investigate further as needed

	Log
	Log all actions.

	Monitoring Sub Synchronous Resonance (SSR) with Capacitor switching action

	CAUTION
	· There are two series Capacitors at Gauss substation.  One should remain bypassed all the time.  The ERCOT outage monitoring tool will verify these conditions.
· Only one set of series capacitors at either Edison or Oersted will be in service at any time.  The ERCOT outage monitoring tool will verify these conditions.
· Prior to energizing or bypassing any series capacitors from service, run a STNET power flow study and contingency analysis.

	Capacitors

With SSR issues
	Name          EMS ID          Transmission Operator 

Edison         EDISON         AEP TO

Orsted         OERSTED      AEP TO

Gauss          GAUSS           AEP TO

Kirchhoff    KIRCHHOF    AEP TO

Ctt_Cros     CTT_CROS    CROSS TEXAS TO



	Note
	· SSR Studies identify the conditions for SSR.  These outages are programmed into the EMS monitoring tool.

· TO(s) should contact ERCOT System Operations prior to energizing or bypassing any Series Capacitor.

· WARNING:  If the generator plant is three contingencies away from SSR vulnerability, a notification will inform a System Operator to review the procedural plan.

· ALARM:  If the generator plant is two or fewer contingencies away from SSR vulnerability, an alarm will inform a System Operator to implement the procedural action plan.  A Generator is allowed to reside in this condition for 8 hours.

· The ERCOT EMS system will be utilized to monitor transmission outages.  A double circuit transmission outage is considered as one contingency in Operations.

	Output

Displays
	REVIEW REFERENCE DISPLAY:

ERCOT EMS Applications>OLNETSEQ – Real-Time Network On-line Sequence

Contingency Violation Display

SSR Summary Display

IF:

· You receive an SSR alarm, but the impacted Resource is offline.

THEN:

· Take action accordingly because the SSR tool does not consider if the unit is planned ON/OFF

	Warning
	IF:

· EMS SSR Notification (Warning) Three Contingencies away from SSR vulnerability

THEN:

· Notify Shift Supervisor 

· Coordinate with Operations Support Engineer to review Action Plan

· Consider restoring planned outages with less than 8 hours restoration times

	Alarm
	IF:

· EMS SSR Notification (Alarm) Two Contingencies away from SSR vulnerability

THEN:

· Notify Shift Supervisor and Operations Support Engineer

· Assess system with series Capacitors bypassed

IF:

· Congestion is identified during the assessment 

THEN:

· Activate the Manual Constraint

· Bypass Series Capacitors promptly

Typical Script for TO:  

This is ERCOT Operator [first and last name].  At [xx:xx], ERCOT is issuing [TO] an Operating Instruction to bypass the [Edison and Oersted], [Cross and Gauss], or [Kirchhoff] Series Capacitor for SSR mitigation and update the Outage Scheduler.  Notify ERCOT when this task is complete.  Please repeat this back to me.  That is correct, thank you.”

· Post message on the ERCOT Website

Typical ERCOT Website Posting of the SSR Mitigation: 

“ERCOT is bypassing the [Series Capacitor] for SSR mitigation.”

· Activate Constraint (if any)

· Contact affected TOs, inquire if planned/forced outages can be restored within 8 hours

	1
	IF:

· There are two Contingencies away from SSR vulnerability Series Capacitor cannot be opened or the planned/forced outages cannot be restored within 8 hours

THEN:

· Notify Shift Supervisor and Operations Support Engineer

· Assess system with [Kendall – Big Hill 345 kV line], [Edith Clarke – Clear Crossing 345 kV line] and/or [Tule Canyon – Tesla 345 kV line], or [Dermott Switch – Clear Crossing 345 kV line] opened
IF:

· Congestion is identified during the assessment
THEN:

· Activate the Manual Constraint
· Instruct TO to open [Kendall – Big Hill 345 kV line], [Edith Clarke – Clear Crossing 345 kV line] and/or [Tule Canyon – Tesla 345 kV line], or [Dermott Switch – Clear Crossing 345 kV line]
· Consider RUC De-Commit of a Resource if this action is less restrictive and additional capacity is needed.  
Refer to Desktop Guide Transmission Desk 2.18 Sub-Synchronous Resonance

	2
	The ERCOT Website posting of the SSR Mitigation MUST be posted prior to SSR Notification (Alarm) One Contingency away from SSR vulnerability.

IF:

· EMS SSR Notification (Alarm) identifies one Contingency away from SSR vulnerability

THEN:

· Confirm previous steps have been completed; and
· Notify QSE with impacted resource

	Normal Operations
	WHEN: 

· Back to normal operations and there is no SSR vulnerability.

CANCEL: 

· SSR mitigation message on the ERCOT Website.
THEN:

· Assess system with series Capacitors in service

· Insert Series Capacitors

Typical Script for TO:  

This is ERCOT Operator [first and last name].  At [xx:xx], ERCOT is issuing [TO] an Operating Instruction to close the [Edison and Oersted], [Cross and Gauss], or [Kirchhoff] Series Capacitor as conditions have improved and there is no reportable SSR condition at this time.  Notify ERCOT when this task is complete.  Please repeat this back to me.  That is correct, thank you.”

	Log
	Log all actions.

	Monitoring Sub Synchronous Resonance (SSR) without Capacitor switching action

	Capacitors

With SSR issues
	Name                        EMS ID             Transmission Operator 

North Edinburg         NEDIN              AEP TO

Rio Hondo                RIOHONDO      AEP TO



	Note
	· SSR Studies identify the conditions for SSR.  These outages are programmed into the EMS monitoring tool.

· TO(s) should contact ERCOT System Operations prior to energizing or bypassing any Series Capacitor.

· WARNING:  If the generator plant is three contingencies away from SSR vulnerability, a notification will inform a System Operator to review the procedural plan.

· ALARM:  If the generator plant is two or fewer contingencies away from SSR vulnerability, an alarm will inform a System Operator to implement the procedural action plan.  A Generator is allowed to reside in this condition for 8 hours.

· The ERCOT EMS system will be utilized to monitor transmission outages.  A double circuit transmission outage is considered as one contingency in Operations.

	Output

Displays
	REVIEW REFERENCE DISPLAY:

ERCOT EMS Applications>OLNETSEQ – Real-Time Network On-line Sequence

Contingency Violation Display

SSR Summary Display

IF:

· You receive an SSR alarm, but the impacted Resource is offline.

THEN:

· Take action accordingly because the SSR tool does not consider if the unit is planned ON/OFF

	Warning
	IF:

· EMS SSR Notification (Warning) Three Contingencies away from a SSR vulnerability

THEN:

· Notify Shift Supervisor 

· Inform QSE resource may be requested offline for Valley SSR mitigation

	Alarm
	IF:

· EMS SSR Notification (Alarm) Two Contingencies away from a SSR vulnerability

THEN:

· Notify Shift Supervisor

· Issue QSE operating instruction to order the resource offline

Typical Script for TO:  

This is ERCOT Operator [first and last name].  At [xx:xx], ERCOT is issuing [QSE] an Operating Instruction to take [resource] offline for SSR mitigation.  Notify ERCOT when this task is complete.  Please repeat this back to me.  That is correct, thank you.”

· Post message on the ERCOT Website

Typical ERCOT Website Posting of the SSR Mitigation: 

“ERCOT is taking manual actions for SSR mitigation.”

	1
	Refer to Desktop Guide Transmission Desk 2.18 Sub-Synchronous Resonance

	2
	The ERCOT Website posting of the SSR Mitigation MUST be posted prior to SSR Notification (Alarm) One Contingency away from SSR vulnerability.

IF:

· EMS SSR Notification (Alarm) identifies one Contingency away from SSR vulnerability

THEN:

· Confirm previous steps have been completed; and 

· Notify QSE with impacted resource

	Normal Operations
	WHEN: 

· Back to normal operations and there is no SSR vulnerability.

CANCEL: 

· SSR mitigation message on the ERCOT Website.
THEN:

· Notify QSE resource is released to come online

Typical Script for TO:  

This is ERCOT Operator [first and last name].  At [xx:xx], ERCOT is notifying [QSE] [resource] is released to come online. Please repeat this back to me.  

That is correct, thank you.”

	Log
	Log all actions.

	Post-Contingency Overloads on the South DC Ties

	Note
	Ensure all available generation has been RUC committed and the constraint binding before curtailing any South DC-Ties.  Curtail only enough to maximize the flow across the South DC-Ties at all times.

	1
	IF:

· A post-contingency overload is approaching 98% of the Emergency Rating with shift factors for a DC-Tie export;

THEN:

· Activate the constraint if a 2% or more shift factor exists.

IF:

· Shift factors exists for a DC-Tie export only or if activating the constraint does not fully resolve the congestion;

THEN:

· Ensure appropriate Resources have been RUC committed,

· Request the DC-Tie Desk Operator to curtail the appropriate South DC-Tie to a specific MW amount to resolve the overload 

· Ensure a Mitigation Plan exists for the contingency and review with TO,
· If no Mitigation Plan exists, notify Operations Engineer to create one.  

	Basecase Overloads

	1
	IF:

· A Basecase exists

THEN:

· Verify SCADA is of similar magnitude to the Actual Basecase value (MW and MVAR flows)

· Example: Review the SCADA value with Actual (state estimation value)

	2
	IF:

· Inaccurate, 

· Indicate NOSCED, OR

· There is not a unit with at least a 2% shift factor;

THEN:

· DO NOT employ congestion management techniques, 
· Notify the Shift Supervisor and Operations Support Engineer to investigate or create a CMP.
· Acknowledge the constraint and list a reason using the drop-down box,

· The comment field should be used for additional information

	3
	IF:

· Accurate, AND

· There is a unit with at least a 2% shift factor;

THEN:

· Activate constraint

· Lower the value in the % Rating column in TCM to tighten the constraint as needed (minimum of 95%, excluding GTCs)

IF:

· A PST can help solve the congestion;

THEN:

· Activate the constraint until the PST is studied and moved.

	ONTEST
	Resources with a Resource Status of ONTEST, may not be issued dispatch instructions / Operating Instructions except:

· For Dispatch Instructions / Operating Instructions that are a part of the testing; or

· During conditions when the Resource is the only alternative for solving a transmission constraint (would need QSE to change Resource Status); or

· During Force Majeure Events that threaten the reliability of the ERCOT System. 

	QSGR
	Market Operation>Real-Time Market>SCED Displays>DSI Displays>DSI Data Processes>DSI Operator Manual Overide HDL And LDL 

IF:

· A QSGR is needed for voltage support or an unsolved contingency;

THEN:

· Override LDL to a level greater than or equal to the COP LSL

· DO NOT override while SCED is running, 

· Notify QSE as time permits

· Post message on the ERCOT Website
Typical ERCOT Website Posting Script:
ERCOT is taking manual actions for a [Basecase/Unsolved Contingency] in the [geographical area].

· These Resources can be viewed at ERCOT SharePoint > System Operations – Control Center > Quick Links > Approved Quick Start (QSGR) Resources

	Not Dispatchable to SCED
	REVIEW REFERENCE DISPLAY:

EMS Applications>Generation Control>Resource Limit Calculation>RLC Unit Input Data and RLC Unit Output Data

IF:

· A QSE has telemetered more A/S on a specific Resource that is greater than their HSL, OR

· A Resource is generating more than their telemetered HSL; 

THEN:

· SCED will set the HDL=LDL=MW making the Resource un-dispatchable,

· Request the QSE to make corrections to telemetry (Resource status, Resource limits, A/S responsibilities, etc.)

· Disregard IRRs unless transmission constraint is active.

	Qualifying

Facilities
	A list of Qualifying Facilities can be found in Desktop Guide Common to Multiple Desk section 2.20

IF:

· A Qualifying Facility (QF) is needed to operate below its LSL, or be ordered off-line to solve congestion;

THEN:

· An Emergency must be declared

· Issue an electronic Dispatch Instruction confirmation to the appropriate QSE,

· Choose “DECOMMIT or ERCOT REQUESTED QF OPERATE BELOW LSL” as the Instruction Type from Resource level

· Enter contingency name in “other information”

· If DECOMMIT also enter RUC DECOMMIT in “other information”

When issuing a VDI or confirmation, ensure the use of three-part communication:

· Issue the Operating Instruction

· Receive a correct repeat back

· Give an acknowledgement

· Issue an Emergency Notification via Hotline call to TOs, 

· Coordinate with the Real-Time Desk Operator to make Hotline call to QSEs,

· Post message to the ERCOT Website.

T#28 – Typical Hotline Script for Emergency Notice for instructing Qualifying Facility to operate offline/below LSL

	4
	IF:

· All applicable steps above have been completed, AND Basecase is still exceeding its Normal and/or its Relay Loadability Rating;

THEN:

· Seek to determine what unforeseen change in system condition has arisen and where possible, seek to reverse the action, 

· Coordinate with Operations Support Engineer to develop a mitigation plan, 

· Refer to Section 4.3, Closely Monitored SOLs, AND

· Notify Shift Supervisor to contact the Director Control Room Operations and/or Designee to investigate further as needed

	Log
	Log all actions.  If known, log the outage that is causing the congestion.

	Basecase of Relay Loadability Rating

	1
	 IF:

· A Basecase of the Relay Loadability Rating (RLAY) exists;
THEN:

· Verify SCADA is of similar magnitude to the Actual Basecase value (MW and MVAR flows)

· Example: Review the SCADA value with Actual (state estimation value)

	2
	IF:

· Inaccurate, 

· Indicate NOSCED, OR

· There is not a unit with at least a 2% shift factor;

THEN:

· DO NOT employ congestion management techniques, 
· Notify the Shift Supervisor and Operations Support Engineer to investigate or create a CMP.
· Acknowledge the constraint and list a reason using the drop-down box,

· The comment field should be used for additional information

	3
	IF:

· Accurate, AND

· There is a unit with at least a 2% shift factor;

THEN:

· Activate constraint

· Lower the value in the % Rating column in TCM to tighten the constraint as needed (minimum of 95%, excluding GTCs)

IF:

· A PST can help solve the congestion;

THEN:

· Activate the constraint until the PST is studied and moved.

	4
	IF:

· All applicable steps above have been completed, AND Basecase is still exceeding its Relay Loadability Rating;

THEN:

· Seek to determine what unforeseen change in system condition has arisen and where possible, seek to reverse the action, 

· Coordinate with Operations Support Engineer to develop a mitigation plan,  

· Refer to Section 4.3, Closely Monitored SOLs, AND

· Notify Shift Supervisor to contact the Director Control Room Operations and/or Designee to investigate further as needed

	Log
	Log all actions.

	Basecase / Post-Contingency Exceedance of Phase Angle

	1
	IF:

· A Phase Angle exceedance exists,

THEN:

· Verify SCADA is of similar magnitude to the Actual value (MW and MVAR flows)

Example: Review the SCADA value with Actual (state estimation value)

	2
	IF:

· Phase Angle exceedance is valid;

THEN:

· Notify the appropriate TO and make them aware of the potential that reclosure of breakers could be affected,  

IF:

· The TO needs assistance from ERCOT to get Phase Angle exceedance adjusted;

THEN:

· This could be transmission switching, creation of a manual constraint, bringing on an additional Resource, returning a planned outage, or development of a CMP.

	Log
	Log all actions.

	Post-Contingency Overloads on Private Use Networks (PUNs) or Customer Owned Equipment behind the Meter

	1
	IF:

· A post-contingency overload is 100% of its Emergency Rating on a PUN or customer owned equipment;

THEN:

· Contact the appropriate QSE/PUN to alert them of the post-contingency overload,

VERIFY:

· There is a plan to mitigate the overload if the contingency were to occur.

	2
	IF:

· It is determined that the QSE/PUN has no way to mitigate or correct the congestion;

THEN:

· Instruct the QSE/PUN to take action such as lower/raise generation or load (verbal Operating Instruction only, do not override HDL/LDL or activate constraint in SCED) and

· Acknowledge the post-contingency overload in TCM.

	3
	IF:

· The contingency occurs;

THEN:

· Notify the QSE/PUN to ensure action is being taken on the plan. 

	4
	IF:

· A post-contingency overload of 98% or greater of its Emergency Rating on transmission equipment (non-PUN or customer owned equipment), and the only shift factor of 2% or more is a PUN unit;

THEN:

· Activate the constraint.

	Log
	Log all actions.

	Managing Constraints in SCED

	Note
	One of the key tasks is to properly monitor and manage transmission constraints.  Keep track of non-binding constraints that have flows approaching their limits and be prepared to take action as the constraint approaches its rating.

	Output

Displays
	REVIEW REFERENCE DISPLAY:

Market Operation>Real-Time Market>SCED Displays>DSP Displays>DSP Constraint Summary

Once SCED has completed its run, check the validity of the binding/exceeded constraints, limits, shadow price, and current real-time flows.

	In 

Series


	It is common for series elements to have nearly identical shift factors for a given contingency.  If post-contingency loading of 98% or greater occurs for multiple elements which have been identified as being in series with each other, only the most limiting constraints should be activated to mitigate all the series element congestion.

Example: Contingency A overloads X, Contingency A overloads Y

	Same

Element
	If post-contingency loading of 98% or greater occurs on the same element for multiple contingencies and they have nearly identical shift factors, only one of the most limiting constraints should be activated to mitigate the congestion.

Example:  Contingency A overloads X, Contingency B overloads X

	1
	Verify that the SCED executions are reducing the flows on each constraint that is binding.

	2
	When a constraint becomes violated in SCED, which is when it has reached its max shadow price and is exceeding its Emergency rating, review the following bullets to take the appropriate action(s):
· Confirm that pre-determined relevant RAPs are properly modeled in the EMS,

· Ensure base points are being followed,

· Remove Resource from ONTEST,

· Remove A/S to increase capacity available to SCED (see procedure below),

· Determine if a unit carrying Off-line Non-Spin could be used,

· Ask the Resource Desk Operator to deploy Non-Spin for the specific unit

· The telemetered Non-Spin schedule must be changed to 0 for SCED to dispatch the Resource

· Determine if additional units could be RUC committed/decommitted,

· Confirm SCED is balancing conflicting constraints

· Ensure reactive devices are being utilized

	3
	IF:

· All applicable steps above have been completed, AND constraint is still exceeding its Emergency Rating;

THEN:

· Seek to determine what unforeseen change in system condition has arisen and where possible, seek to reverse the action, 

· Coordinate with Operations Support Engineer to develop a mitigation plan,

· Refer to Section 4.3, Closely Monitored SOLs, AND  

· Notify Shift Supervisor to contact the Director Control Room Operations and/or  Designee to investigate further as needed

	Note
	EMP Applications>TCM-Transmission Constraint Manager>Related Displays>Message Log for CAM

IF:

· No shift factors are passed for the constraint;

THEN:

· Contact Help Desk to issue a ticket to GMS Support to fix immediately.

	Log
	Log all action taken including the following:

· Reason for doing a manual override

· Any security violations that were ≥ 125% of the Emergency Rating

	Remove A/S to Increase Capacity available to SCED

	1
	RLC Unit Input Data display

IF:

· A/S needs to be removed from a specific unit to increase capacity to SCED;

THEN:

· Post message on the ERCOT Website anytime manual action is taken

· Coordinate with the Shift Supervisor and Resource Desk Operator to block or limit A/S on the resource(s) using A/S Capability Manual Override.
· 

	Log
	Log all actions.

	Unsolved Contingencies

	1
	Periodically check the “Contingency Solution Results” display:

IF:

· An unsolved contingency exists;

THEN:

· Run the State Estimator again,

· If unsolved contingency remains, notify the Operations Support Engineer to investigate

IF:

· Generation needs to be re-dispatched to solve the contingency

THEN:

· Use HDL/LDL override 

· Post message on the ERCOT Website anytime manual action is taken

· Log all actions

IF:

· EMR Generation needs to be RUC committed such as Hydro

THEN:

· Issue an Emergency Notice

· Notify the RUC Desk Operator to RUC commit the resource(s)

· Log all actions

IF:

· It has been determined that a Resource is needed in real-time for a transmission condition after the close of the Adjustment Period (Typically will be short start);

THEN:

· Notify the RUC Desk Operator to issue a VDI and an electronic Dispatch Instruction

· Refer to RUC Procedure 3.7 Manual Dispatch of Resources “Manual Commit of a Resource” 

· Post message on the ERCOT Website anytime manual action is taken

Typical ERCOT Website Posting Script:
ERCOT is taking manual actions for an unsolved contingency in the [geographical area].

WHEN:

· Constraint solves and the contingency comes into RTCA

· Activate constraint, and

· Release manual override after SCED runs

· Cancel ERCOT Website posting.

	Log
	Log all action taken including the following:

· Reason for unsolved contingency

· Actions taken to resolve

	Unresolvable Congestion with EMR Generation available  

	1
	IF:

· Post-contingent rating exceedance in excess of 115% of the Emergency Rating, 

· An unsolved contingency,

· Real-time exceedance, OR

· A CMP that does not maintain Reliability;

THEN:

· Verify the contingency definition associated with the constraint is accurate and appropriate given the current state of the grid

IF:

· EMR Generation is available to be dispatched to resolve the Reliability issue,

THEN:

· Issue a Transmission Emergency Notice

· Post message on the ERCOT Website
· Notify the Real-Time Desk Operator to make Hotline call to QSEs

· Notify the RUC Desk Operator to RUC commit the appropriate EMR resource(s)

Typical ERCOT Website Posting Script:
Transmission Emergency Notice has been issued for the [Geographical Area] due to [state issue used in Hotline call].
Edit script as needed to fit situation.

WHEN:

· Contingency or Constraint solves and is no longer a Reliability concern

· Release the EMR Generation

· Cancel the Transmission Emergency Notice

· Cancel ERCOT Website posting.

	Log
	Log all action taken including the following:

· Reason for Transmission Emergency Notice

· Actions taken to resolve

	Model Inconsistencies/Updates

	1
	IF:

· Any inconsistencies in ratings, impedance changes, etc. are found;

THEN:

· Notify Operations Support Engineer so that they can work with the TO to confirm the correct information and if required, correct it through the NOMCR process.

	2
	IF:

· There is a difference in an Emergency Facility rating or system voltage limit between ERCOT and a TO;

THEN:

· The most limiting rating will be used until the correct rating can be determined,

· Notify Operations Support Engineer so that they can work with the TO to confirm the correct information and if required correct it through the NOMCR process.

	Log
	Log all actions.

	QSE Requests to Decommit a Resource

	1
	IF:

· Notified by the Resource or RUC Desk Operator of a request to decommit a self-scheduled Resource;

THEN:

· Perform a Real-Time study (if necessary) to determine that no violation of security criteria exist with the Resource off-line and no additional active constraints for SCED will occur,
· Notify the Resource or RUC Desk Operator with determination.

	Phase Shifters

	1
	IF:

· A TO calls to requests that a Phase Shifter position be adjusted and there are no longer any known reliability issues in the area;

THEN:
· As time permits, run a study to re-evaluate the phase shifter position; 

· Coordinate with the TO and adjust the phase shifter as needed to an agreed upon position (preferably as close to neutral as possible).

	Log
	Log all actions.


4.2
Transmission/Capacity Issues within the CENACE Area

Procedure Purpose:  Providing assistance to CENACE.

	Protocol Reference
	4.4.4
	
	
	

	Guide Reference
	2.2.2
	
	
	

	NERC Stadard
	
	
	
	


	Version: 2 
	Revision: 0
	Effective Date:  December 5, 2025


	Step
	Action

	Note
	On the CENACE side of the Railroad DC-Tie, there is an automatic runback scheme that runs back the DC-Tie under CENACE contingency conditions.  

	1
	IF: 

· Notified by a DC-Tie Operator that CENACE is unable to maintain reliability and needs to curtail an E-Tag; 

THEN:

· Verify the MW amount, DC-Tie, and time of the curtailment,

· Notify ERCOT DC-Tie Desk Operator with information.



	2
	IF: 

· Notified by a DC-Tie Operator that CENACE is requesting emergency energy; 

THEN:

· Determine which DC-Tie(s) and amount being requested,

· Determine or have the Operations Support Engineer determine that sending emergency energy to CENACE would not put ERCOT in an emergency condition

IF: 

· ERCOT is able to send CENACE emergency energy; 

THEN:

· Notify the ERCOT DC-Tie Desk Operator with information for an electronic Dispatch Instruction to be issued.

	3
	WHEN:

· Notified by a DC-Tie Operator that CENACE no longer needs emergency energy;

THEN:

· Notify the ERCOT DC-Tie Desk Operator with information.

	Log
	Log all actions.


4.3
Closely Monitored SOLs

Procedure Purpose: To identify SOLs that should be closely monitored.
	Protocol Reference
	6.5.7.1.10
	6.5.9.2
	6.5.9.3.4(5)
	

	Guide Reference
	2.2.2
	4.5.2(2)(b)
	
	

	NERC Standard


	IRO-001-4

R1
	IRO-002-7

R5
	TOP-001-6

R1, R7, R10, R10.1, R10.3, R14
	


	Version: 2 
	Revision: 0
	Effective Date:  December 5, 2025


	Step
	Action

	Cascading

Outages
	Uncontrolled successive loss of system elements – widespread electric service interruption that cannot be restrained from sequentially spreading beyond an area predetermined by studies.  

	System Instability
	The inability of the Bulk Power System, for a given initial operating condition, to regain a state of operating equilibrium after being subjected to a Disturbance1.
1Refers to the remaining portion of the interconnected Bulk Power System, with the exception of the Elements disconnected as a result of the Disturbance.

	Relay Loadability Rating
	The MVA rating below which no load-responsive phase-protection relay tripping is expected.  The Relay Loadability Rating is calculated based on the trip points of protective devices at the equipment terminals of the affected Transmission Element under a set of operating criteria defined by the Transmission Element owner.

	Note
	Considerations for an IROL:

· System Instability
· Loss of load in the Cascading or voltage collapse, either through manual action or as a consequence of the event, including loss of load as a result of Under Voltage Load Shedding (UVLS) and Under Frequency Load Shed (UFLS)
· Loss of load (manual or auto) is greater than 2000 MW as a result of instability, cascading or uncontrolled separation used in the study

	Monitoring
	Monitor for any of the following conditions:

· Basecase Overload

· Post-contingent rating exceedance in excess of 125% of the Emergency Rating

· An unsolved contingency

· A divergent case in VSAT and/or TSAT

· Exceedance of a Relay Loadability Rating 

· Under-voltage condition characterized by bus voltages of less than 90% across three or more related BES facilities

· Over-voltage condition greater than 110% across three or more BES facilities

	SOL

Comms
	If validated off-line study shows a post-contingency cascading or system instability, make verbal communication within 15-minutes to impacted TOs. Refer to section 3.8, “SOL Exceedance Communication Threshold”, for criteria of verbally communicating the SOL exceedance as identified below.  

	1
	IF:

· Any of the above exists;

THEN:

· Confirm the appropriate transmission congestion procedures have been completed,

· Notify the Operations Support Engineer to perform cascading outage studies

	Studies
	If a facility approaches 125% of Emergency Rating, a study for the loss of the contingency element and the overloaded facility will be conducted.

· Manually remove the contingency in the study and run powerflow, and

· Manually remove the facility identified to be loaded above 125% of its Emergency Rating (Breaker to Breaker), and

· Run powerflow.

IF: 

· The study results indicate no additional facilities will be overloaded over 125% of their Emergency rating,

THEN:

· This is determined to be a localized event and no additional pre-contingency actions will be taken,

IF:
· The study results in an additional facility(s) over 125% of its Emergency rating, continue the analysis to also trip the additional facilities (Breaker to Breaker). This analysis will be performed tripping a maximum of 5 study iterations.  
THEN:

· If the study indicates either a non-converged case OR continues to show facilities exceeding 125% of their Emergency ratings, this will be considered a potential cascade condition.

	Localized

Event
	IF:

· It is determined to be a localized event;

THEN:

· A Mitigation Plan should be developed and reviewed with the affected TO(s)

	Cascading 

Condition
	IF:

· It is determined to be a cascading condition (not a local radial load pocket);

VERIFY (time permitting):

All relevant actions have been implemented:

· All available generation has been brought online

· All generation redispatch options have been utilized

· No switching action is available

· All available load resources have been deployed

· All available reactive devices have been deployed or adjusted without exceeding voltage limits

· *All available load management programs have been deployed by the ERCOT TO (if available)

· All DC-Tie transactions have been curtailed that negatively impacts

· Emergency Energy has been requested or is being imported

· Any distribution voltage reduction has been implemented

· All necessary public appeals have been made

* Only applies June through September or when available in EEA 2. EEA 2 and EEA3 implements any available Load management plan to reduce Customer Load.

THEN:

· Proceed to the next procedure “Pre-contingency Load Shedding to avoid Post-contingency cascading” AND,
· Make verbal communication to impacted TOs within 15 minutes of determination.

	Pre-contingency Load Shedding to avoid Post-contingency cascading

	1
	IF:

· Load shed is the only option to prevent a cascading condition;

THEN:

· Obtain the necessary information from the Operations Support Engineer and review with the affected TO

· The amount of load shed should be enough to remain below the load shed rating of the first overloaded facility

· Verify if load shed needed to be location specific

· Inform TO that a Transmission Emergency will be issued

· Issue Operating Instruction for load shed 

	2
	IF:

· Load shed is 100 MW or greater;

THEN:

· Notify the Operations Support Engineer and Shift Supervisor to initiate the NXT for load shed (SO Request for Firm Load)

	3
	Issue a Transmission Emergency:

· Make a Hotline call to TOs 

· Post message on the ERCOT Website.

· Notify the Real-Time Desk Operator to make Hotline call to QSEs

T#30 – Typical Hotline Script for Transmission Emergency for Cascading Condition

Typical ERCOT Website Posting Script:
“ERCOT issued a Transmission Emergency for an expected cascading condition in the [geographical area].”

	4


	WHEN:

· Load can be restored;

THEN:

· Issue Operating Instruction to restore the load

· Make Hotline call to end the Transmission Emergency

· Notify the Real-Time Desk Operator to make Hotline call to QSEs

· Cancel message on ERCOT Website
· Notify the Operations Support Engineer and Shift Supervisor to initiate the NXT for restoration of load shed (SO Requested Firm Load restoration)
· Make verbal communication to impacted TOs, the SOL exceedance has been mitigated.

	Log
	Log all actions.


4.4
Interconnection Reliability Operating Limit (IROL)

Procedure Purpose:  Maintain transmission Stability using a Generic Transmission Constraint (GTC). The actual flows should not exceed limits.  If necessary, the ERCOT System Operator has the authority to instruct load shedding or removing generation before this IROL has been exceeded.

	Protocol Reference
	6.5.9.1(1)(e)
	6.5.9.3.4
	
	

	Guide Reference
	4.2.4(1)
	4.5.2(2)(b)
	
	

	NERC Standard


	EOP-011-4

R1, R1.1, R1.2, R1.2.4
	IRO-001-4 R1
	IRO-002-7

R5
	IRO-008-3

R2, R3, R5, R6

	
	IRO-009-2

R1, R1.1, R1.2, R2, R3
	PER-005-2 R4
	TOP-001-6

R1, R7, R8, R10, R10.1,  R12, R14, R25
	TOP-002-4

R2, R3


	Version: 2 
	Revision: 0
	Effective Date:  December 5, 2025


	Step
	Action

	Note
	Although the steps within the procedure are numbered, the numbering is for indexing purposes and are not sequential in nature.  The System Operator will determine the sequence of steps, exclude steps, or take any additional actions required to ensure system security based on the information and situational awareness available during both normal and Emergency Conditions.

	IROL

Comms
	If ICCP links are down for a TO, or a TO reports bad data, refer to section 3.8, “SOL Exceedance Communications Thresholds”, above for criteria of manually communicating IROL exceedances identified below.  

	Note
	Utilize the Not to Exceed (%NTE) feature in the Transmission Constraint Manager (TCM) to maintain a more consistent control of the IROL. (see Trans/Sec desktop guide 2.21 for operational  guidance)

	North-Houston Import IROL

	IROL
	The North – Houston VSAT voltage stability limit is an IROL; the actual flow should not exceed its limit.  If necessary, the System Operator has the authority to instruct load shedding before this IROL has been exceeded.

	VSAT
	WHEN:

· VSAT runs and provides an updated limit for the North to Houston;
THEN:

· Update RTMONI.

WHEN:

· The North to Houston flow is approaching 85% of the limit;

THEN:

· Activate the North to Houston constraint at 85% of the limit.

· Match the Not to Exceed (NTE) percentage to the activated percent rating.

· Adjust the NTE percentage before the activated percent rating to maintain and control up to 93%.

	North-Houston

345kV Circuit Outage
	IF:

· Any of the 345kV lines going into the Houston area has a forced outage;

THEN:

· Manually run the entire sequence of RTNET, RTCA, and RTDCP (VSA) immediately and proceed to the Monitor step in this procedure.

	Monitor
	Monitor each of the following Reliability Margins: 

· N-H G

· N-H L

If any of these Reliability Margins fall below the following pre-defined limits, take the appropriate corrective action for each limit, and notify the Shift Supervisor.

	Reliability Margin
	· IF:

· Reliability Margin ≤500 MW

THEN:
· Instruct TOs in the affected Houston area to increase voltages by placing capacitor banks in-service and turning off reactors near the weak busses that are available without exceeding high voltage SOLs.

T#95 North – Houston Reliability Margin ≤500 MW

	≤400MW
	Activate the appropriate constraint(s) such as:

· Thermal constraint(s)

· North to Houston constraint  

· For an unsolved contingency scenario or the Reliability margin is approaching 400, activate the North to Houston (N_TO_H) constraint to get the contingency to solve.

· This may require setting the % Rating lower than 90% to get the constraint to bind.

	≤300MW
	Coordinate with the Resource Desk Operator to deploy Non-Spin using the N_TO_H constraint or the Coast Weather Zone (WZ_COAST) in the A/S Manager and remove any A/S from resources as needed to Increase Capacity available to SCED 

· Issue a Transmission Watch by making a Hotline call and posting on the ERCOT Website
· Coordinate with the Real-Time Desk Operator to make Hotline notification to QSEs 

T#31 – Typical Hotline Script for Watch for North to Houston Interface

	
	

	≤200MW
	VDI QSGR in the Houston area that were not bid in as Non-Spin.  Determine QSGR in the Coast Weather Zone (WZ_COAST)

· Request the RUC Desk Operator to issue electronic Dispatch Instruction to RUC commit

	≤100MW
	· Notify the Resource Desk Operator to deploy Load Resources providing ECRS or RRS in Houston. Prioritize NCLR’s providing ECRS only without UFR.

· Issue a Transmission Emergency Notice by making a Hotline call and posting on the ERCOT Website
· Notify the Real-Time Desk Operator to make Hotline notification to QSEs

T#32 – Typical Hotline Script for Emergency Notice for North to Houston Interface 

	<25MW


	· Instruct CenterPoint to drop firm load in 100 MW blocks.

· Continue Transmission Emergency Notice by making a Hotline call and posting on the ERCOT Website
· Notify Shift Supervisor to make NXT notification

Typical Script for CenterPoint:  

This is ERCOT Operator [first and last name].  At [xx:xx], ERCOT is issuing CenterPoint an Operating Instruction to drop [*** MW] of firm load for the North – Houston interface.  Notify ERCOT when this task is complete.  Please repeat this back to me.  That is correct, thank you.”

T#33 – Typical Hotline Script for Emergency Notice for North to Houston Interface, Firm Load Shed 

	Cancel
	Make appropriate cancellations when back to normal operations.

	Log
	Log all actions.


4.6
RAS, AMP, RAP, PCAP, MP, and TOAP

Procedure Purpose:  To verify and take corrective action for post-contingency overloads for various conditions.

	Protocol Reference
	6.5.7.1.10(3)
	6.5.9.3.3
	
	

	Guide Reference
	2.2.2(3)(b)
	4.2.3(3)
	4.3.1
	

	NERC Standard


	EOP-011-4

R1, R1.1, R1.2, R1.2.3
	IRO-001-4

R1
	IRO-002-7

R5
	IRO-008-3

R2, R3, R5, R6

	
	TOP-001-6
R1, R10, R10.1, R10.2, R10.5, R11, R14, R25
	TOP-002-4

R2, R3
	
	


	Version: 2 
	Revision: 0
	Effective Date:  December 5, 2025


	Step
	Action

	Note
	MPs and PCAPs information are included in the EMS, refer to Desktop Guide Transmission Desk section 2.7

Electronic copies for the RASs, RAPs, PCAPs, and MPs can be found on SharePoint.

ERCOT SharePoint > System Operations – Control Center > Quick Links > Post-Contingency Overloads and/or MP/PCAP/RAP 

	Note
	 Remedial Action Schemes (RAS) (identified as RAS in EMS) OR Remedial Action Plans (RAP)

· EXAMINE the results of RTCA,

· If the background has a color indicating a RAS or RAP,  

· Refer to Desktop Guide Transmission Desk Section 2.7 for explanation of colors and for actions to be taken based on the color of the background.

	SOL Comms
	If electronic communication of SOL exceedances is unavailable, refer to section 3.8, “SOL Exceedance Communications Thresholds”, for criteria of manually communicating SOL exceedances.  

	Log
	Log all actions.

	Remedial Action Schemes (RAS) 

	Note
	Real-time Contingency Analysis (RTCA) indicates a Post Contingent overload(s) on a Contingency in which the RAS will not mitigate all the overloaded elements automatically.  In this case, Congestion Management techniques will be utilized to return the system to the state in which the RAS was designed to automatically relieve the overload.

	Note
	Use caution when the tolerance setting is <100% in RTCA.  If the post-contingency loading on an element monitored by an RAS is above the tolerance threshold, but below the activation point of the RAS (100%), the contingency associated with the RAS will show in the Transmission Constraint Manager (TCM) display. When this occurs, the result will be a light blue highlighted background identifying the device ID on the TCM display.  In this scenario, congestion management is not needed until the criteria in Desktop Guide Transmission Desk Section 2.7, is met.

	Monitor
	Each RAS will be displayed on the “Real Time Values” spreadsheet, as the RAS activation threshold increases the display changes color as follows:

· Greater than 80% but less than 90% turns Orange
· Greater than 90% turns Red

	1
	Typically, RASs are to solve post-contingency overloads on the Transmission System.

IF:

· The Transmission system topology has temporarily changed due to outages (planned or forced) that affects an RAS;

THEN:

· Utilize congestion management techniques to prevent any known RAS from operating in a pre-contingent state.

	2
	IF:

· RTCA indicates a post-contingency overload(s) on a contingency in which the RAS will not mitigate all the overloaded elements automatically; Example: (Light blue or Salmon highlighted background and above 100% loading) 

THEN:

· As system conditions warrant, activate congestion management techniques to relieve the overload.

	3
	IF:

· No reliability issues will arise as a result of a RAS’s operation;

THEN:

· At the Operator’s discretion, allow the RAS to perform its function.

	4
	IF:

· An RAS operates;

THEN:

· Notify affected TO to reset RAS as system conditions warrant

	RAS

Posting
	All RASs are considered in-service unless otherwise notified by the TO. 

IF:

· An RAS is taken out of service and/or removed from RTCA; 

THEN:

· Post the information on the ERCOT Website
WHEN:

· The RAS is placed back in service, 

THEN:

· Cancel the message.

Typical ERCOT Website Posting:
The [name] RAS has been [taken out of service/removed from RTCA].

	Status

Change
	Monitor RAS Summary for status changes. 

Refer to Desktop Guide Transmission Desk Section 2.14,

WHEN:

· Status changes for any type;

THEN:

· Acknowledge alarm

If notified that a RAS has changed status (taken out or placed in service):

· Send e-mail for notification and have RTCA updated, 

· “OPS Support Engineering”

· “1 ERCOT System Operators”

· “DAMTeam”

	Basecase continuous RAS Triggering
	Continual triggering of a RAS during Basecase operations should be managed utilizing manual constraints created in TCM (only applies to manual reset of RAS controls causing a reliability issue).

IF:

· A RAS is continually triggered during Basecase operations; 

THEN:

· Verify that an associated manual constraint exists for this RAS in TCM and activate the manual constraint in SCED.

IF:

· A manual constraint does not exist for this RAS in TCM;

THEN:

· Coordinate with the Operations Support Engineer to build a manual constraint for the RAS action in TCM.

	Log
	Log all actions.

	Automatic Mitigation Plan (AMP)

	Note
	There is current no AMPs. 

	Remedial Action Plan (RAP)

	1
	IF:

· A RAP exists for the contingency;

THEN:

· Confirm that the relevant RAP is properly modeled,

· Review the RAP with the impacted TO,

· Notify the Shift Supervisor of the anticipated actions.

	2
	IF:

· A RAP is used to alleviate the identified problem regardless of the contingency listed on the RAP;

THEN:

· Make log entry.

	3
	IF:

· A RAP exists for the contingency AND does not solve the contingency OR the pre-RAP overload exceeds the 15 MN rating;

THEN:
· RTCA does not pass the 15MN (15 minute) rating to TCM, only the EMGY (2-hour emergency) rating.  To properly constrain for RAP-associated elements, the % Rating column in TCM may need to be increased so that the constraint limit matches the 15MN value.
· Increase the value in the % Rating column in TCM to loosen the constraint (maximum 100% of 15MN value).

	4
	IF:

· RTCA indicates a post-contingency overload(s) on a contingency in which the RAP will not mitigate all the overloaded elements automatically; Example: (Light blue or Yellow highlighted background and above 100% loading) 

THEN:

· Activate constraint if a 2% shift factor exists.

	5
	IF:

· The contingency anticipated by the RAP takes place;

THEN:

· Instruct the implementation of the RAP,

· Respond to requests made by the TO in accordance with the RAP,

· If necessary, continue to use additional congestion management methods,

· Notify the TO when the contingency clears.

	6
	IF:

· A RAP will not work as designed and needs to be disabled due to topology changes in the area;

THEN:

· Notify the affected TO of actions

	RAP

Posting
	All RAPs are considered in-service unless otherwise notified by ERCOT or the TO. 

IF:

· A RAP is taken out of service and/or removed from RTCA; 

THEN:

· Post the information on the ERCOT Website
WHEN:

· The RAP is placed back in service, 

THEN:

· Cancel the message.

Typical ERCOT Website Posting:
The [name] RAP has been [taken out of service/removed from RTCA] due to a [Planned/Forced Outage].

	Status

Change
	If the RAP has changed status (taken out or placed in service):

· Send e-mail for notification and have RTCA updated, 

· “OPS Support Engineering”

· “1 ERCOT System Operators”
· “DAMTeam”

	Log
	Log all actions.

	Pre-Contingency Action Plan (PCAP)

	Caution
	Pre-Contingency Action Plans (PCAPs) are designed to be enacted before the contingency occurs.  

	1
	WHEN:

· RTCA shows a post-contingency overload and a PCAP exists to resolve it;

THEN:

· Review the PCAP with the impacted TO,

· Notify the Shift Supervisor of the anticipated actions,

· Instruct the execution of the PCAP with the impacted TO.

Typical Script to appropriate TO:
“This is ERCOT Operator [first and last name].  At [xx:xx], ERCOT is giving an Operating Instruction [TO] to implement the ****PCAP and [open/close] [breaker(s)].  [TO] please repeat this back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

	Note
	If necessary, use congestion management methods for post contingency loading after initiating the PCAP.

	2
	WHEN:

A PCAP is no longer needed; THEN:

· Instruct the impacted TO to return the system to:

· Its normal status, OR

· Its status prior to implementation of the PCAP.

	3
	IF:

· A PCAP is used to alleviate the identified problem regardless of the contingency listed on the PCAP;

THEN:

· Make log entry.

	Log
	Log all actions.

	Mitigation Plan (MP)

	Note
	Mitigation Plans (MPs) are pre-determined actions to be taken associated with the occurrence of a specific contingency event if congestion management methods cannot resolve the post-contingency overload.  MPs are designed to be enacted Post-Contingency.  They are NOT pre-emptive congestion management actions.

· A MP is developed when SCED cannot fully resolve the constraint, OR

· A MP is developed when there are no generator shift factors greater than or equal to 2% as indicated in EMS,

· If a MP is used to alleviate the identified problem regardless of the contingency listed on the MP, make a log entry.

	SCED

unable to 

fully resolve

constraint
	IF:

· SCED is unable to resolve a constraint;

THEN:

· Keep constraint active in SCED,

· Verify a MP or TOAP exists for the contingency, and review the MP or TOAP with the impacted TO

 IF:

· No MP or TOAP exists for the constraint;

THEN:

· Keep constraint active in SCED,

· Coordinate with Operations Support Engineer to develop a MP 

· If constraint exists due to an outage, a TOAP should be developed (see TOAP procedure),

· Issue a Transmission Watch if the MP or TOAP has not been developed within 30 minutes and the constraint remains violated in SCED.

	< 2% 

Absolute 

Shift

Factors 
	IF:

· A constraint exists for which there are no generator shift factors greater than or equal to 2% as indicated in EMS;

THEN:

· DO NOT activate the constraint in SCED

· Verify a MP or TOAP exists for the contingency, and review the MP or TOAP with the impacted TO

IF:

· No MP or TOAP exists for the constraint;

THEN:

· Coordinate with the Operations Support Engineer to develop MP

· If contingency exists due to an outage, a TOAP should be developed (see TOAP procedure)

· Issue a Transmission Watch if the MP or TOAP has not been developed within 30 minutes.

	TO

Issue
	IF:

· Notified by a TO that it will take more time to implement the MP than is identified on the MP;

THEN:

· Notify the Operations Support Engineer to restudy and modify MP,

· Log actions taken

	Issue

Watch
	When issuing a Transmission Watch for an unsolved post-contingency overload (and waiting on MP or TOAP to be developed:

· Make Hotline call to TOs

· Coordinate with the Real-Time Desk Operator to call QSEs 

· Post message on the ERCOT Website
T#34 – Typical Hotline Script for Transmission Watch for Post-Contingency Overload 

Typical ERCOT Website Posting Script: 

At [xx:xx] a Transmission Watch was issued due to the post-contingency overload in the [geographical area], [ manual actions are being performed to reduce the post-contingency overload] a [mitigation plan/temporary outage action plan] is being developed.

	Cancel

Watch
	When the MP or TOAP has been developed, cancel the Watch:

· Make Hotline call to TOs

· Coordinate with the Real-Time Desk Operator to call QSEs

· Cancel message on ERCOT Website
T#35 – Typical Hotline Script to Cancel Transmission Watch for Post-Contingency Overload

	Contingency

Occurs
	IF:

· The anticipated contingency takes place;

THEN:

· Instruct (if necessary) the implementation of the MP or TOAP to the impacted TO,

· Respond as quickly as possible to requests made by the TO in accordance with the MP,

· If necessary, continue to use congestion management methods for post-contingency loading after initiating the MP.

· Notify the TO when the system can be returned to normal.

	Log
	Log all actions.

	Temporary Outage Action Plan (TOAP)

	Note
	TOAPs are temporary since they are outage related  

· A TOAP is developed when there is no generation shift factors greater than or equal to 2% as indicated in EMS, OR

· A TOAP is developed when SCED cannot fully resolve the constraint

	Planned

Outage
	IF:

· A post-contingency overload is due to a planned outage on a transmission line(s) or a transmission facility;

THEN:

· Locate the TOAP in the Outage Notes,

· Follow the same process as a MP outlined above.

	Forced

Outage
	IF:

· A post-contingency overload is due to a forced outage or planned outage not recognized by Outage Coordination on a transmission line(s) or a transmission facility;

THEN:

· Follow the same process as a MP outlined above.

	Log
	Log all actions.


4.7
Manual Dispatch of Resources

Procedure Purpose:  Manually Dispatch Resources as necessary to ensure system security.

	Protocol Reference
	6.5.7.8
	6.5.9(3)
	
	

	Guide Reference
	4.1.(1)
	
	
	

	NERC Standard
	
	
	
	


	Version: 2 
	Revision: 0
	Effective Date:  December 5, 2025


	Step
	Action

	Note
	ERCOT shall honor all Resource operating parameters in Dispatch Instructions / Operating Instructions under normal conditions and Emergency Condition.  During Emergency Conditions, ERCOT may verbally request QSE’s to operate its Resources outside normal operating parameters.  If such request is received by a QSE, the QSE shall discuss the request with ERCOT in good faith and may choose to comply with the request.

	Manual Dispatch to take a Unit Off-Line

	1
	IF:

· A manual Dispatch Instruction / Operating Instruction will result in the unit being dispatched off-line (i.e., less than the minimum operating limit for that Resource);

THEN:

· Post message on the ERCOT Website anytime manual action is taken

· Request the RUC Desk Operator to issue the VDI and electronic Dispatch Instruction.

	Manual RUC Commit of a Resource

	1
	IF:

· It has been determined that a Resource is needed in real-time for a transmission condition;

THEN:

· Post message on the ERCOT Website anytime manual action is taken

· Request the RUC Desk Operator to RUC commit the Resource

	Log
	Log all actions.


4.8
Responding to Diminishing Reserves

Procedure Purpose: Monitor the Physical Responsive Capability (PRC) for issuing advance notice of diminishing Responsive Reserve.  Steps within this procedure are intended to keep ERCOT from progressing into EEA.

	Protocol Reference
	3.17.3(2)
	6.5.7.6.2.3
	6.5.9.4.1
	

	Guide Reference
	4.5.3.1(d)
	4.5.3.1(e)
	
	

	NERC Standard
	TOP-001-6

R8
	
	
	


	Version: 2 
	Revision: 0
	Effective Date:  December 5, 2025


	Step
	Action

	Media

Appeal
	An appeal through the public news media for voluntary energy conservation may be issued any time at ERCOT’s discretion.  Make Hotline call. 

T#39 Typical Hotline Script for Media Appeal

	TCEQ
	The Texas Commission on Environmental Quality (TCEQ) may exercise enforcement discretion for exceedances of emission limits and operational limits for Resources that exceed air permit limits in order to maximize generation when entering a capacity shortage. A Market Notice will be sent to Market Participants. Make Hotline call. 

T#87 Typical Hotline Script for TCEQ Notice of Enforcement Discretion

	Request Large Load Curtailment Program
	WHEN:

· Notified by the Shift Supervisor that the Large Load Voluntary Curtailment Program Participants were requested to curtail consumption;
THEN:
· Make Hotline call to notify TO’s that the Large Load Voluntary Curtailment Program Participants were requested to curtail consumption.
· Coordinate with the Resource Desk Operator for posting message.

T#63 Typical Hotline Script for ERCOT Large Load Voluntary Curtailment Program

	Large Load Curtailment Program Ended
	WHEN:

· Notified by the Shift Supervisor that the Large Load Voluntary Curtailment Program Participants requested to curtail consumption ended;

THEN:
· Make Hotline call to notify TO’s that the Large Load Voluntary Curtailment Program Participants requested to curtail consumption ended.
T#64 Typical Hotline Script for ERCOT Large Load Voluntary Curtailment Program Ended

	Log
	Log all actions.

	Watch

	Issue 

Watch
	IF:

· PRC < 3000 MW and not expected to return > 3000MW within 30 minutes
THEN:

· Using the Hotline, issue an Watch

· After the repeat, give TOs an update of system conditions, including chances of proceeding into an EEA.
· Reduce Customer Load by using Distribution voltage reduction measures, if deemed beneficial and EEA3 load shed is not anticipated
· If not already completed, coordinate with the Resource Desk Operator to post Distribution Voltage Reduction messages on the ERCOT Website.
 T#1 – Typical Hotline Script for Watch PRC <3000 MW

	Log
	Log all actions.

	Evaluate

Constraints
	IF:

· PRC is expected to continue to drop to the progression of an EEA 2; 

THEN:

· Proceed to section 7.2, Congestion Management during EEA Levels. 


	Cancel

Watch
	WHEN:

· PRC > 3000 MW;

THEN:

· Using the Hotline, cancel the Watch.

· If Distribution voltage reduction measures where requested, notify TOs to return Distribution Voltage Reduction back to normal  

· If not already completed, coordinate with the Resource Desk Operator to post “Transmission Operators have been requested to return Distribution Voltage Reduction to normal operation”.
T#2 – Typical Hotline Script to Cancel Watch for PRC<3000 MW

	Log
	Log all actions.


4.9
Creation of new GTC in Real-time

Procedure Purpose:  Unexpected change to system conditions that result in a new Generic Transmission Constraint or modified (GTC). 

	Protocol Reference
	3.10.7.6 (6)
	
	
	

	Guide Reference
	
	
	
	

	NERC Standard
	
	
	
	


	Version: 2 
	Revision: 0
	Effective Date:  December 5, 2025


	Step
	Action

	GTC
	If an unexpected change to system conditions occurs that result in a new or modified GTC (one that had not previously been defined and posted):

· Declare an OCN 

· Make Hotline call to TOs

· Notify the Real-Time Desk Operator to make Hotline call

· Post message on the ERCOT Website
T#36 – Typical Hotline Script for OCN for new Generic Transmission Constraint
Typical ERCOT Website Posting Script:
“An OCN has been issued due to ERCOT developing a [new/modified] Generic Transmission Constraint due to [reason].”

	Note
	If a OCN has been issued due to ERCOT developing a [new/modified] Generic Transmission Constraint

· Send e-mail for notification, 

· 1 ERCOT System Operators

· OPS Support Engineering

· OPS Outage Coordination

	Log
	Log all actions.


5.1
Outages

Procedure Purpose:  Monitor and respond to various types of equipment outages, both Transmission and Generation, to maintain reliability of the ERCOT Grid.

	Protocol Reference


	3.1.4.2
	3.1.4.4
	3.1.4.5
	3.1.4.6

	
	3.1.5.1
	3.1.5.5
	3.1.5.7

	3.1.5.11

	
	3.1.6.9
	3.1.6.11
	6.5.7.1.6
	6.5.9.3.1.1

	Guide Reference
	2.4
	
	
	

	NERC Standard


	EOP-011-4

R1, R1.1, R1.2, R1.2.2
	IRO-008-3

R2, R3
	TOP-002-4

R2, R3
	


	Version: 2 
	Revision: 0
	Effective Date:  December 5, 2025


	Step
	Action

	Note
	ERCOT Operators can only make the following changes in the Outage Scheduler:

· Remove actual start/end time if it is within 2 hours of the time the MP entered the outage,

· Change status,

· Add notes

If a MP needs assistance or is unable to enter their outages, direct them to Outage Coordination.  Outage Coordination has an “Impersonation” certification that will allow them to make the needed changes.

	Note
	Forced Outages should be verbally communicated to ERCOT and must be entered into the Outage Scheduler if it is to remain an Outage for longer than two hours.

	1
	IF:

· An Emergency Condition is declared;
THEN:

· Determine if Outages can be returned to service if causing negative impacts to reliability,

· Coordinate with the appropriate TO.

	Monitor Mode

	1
	IF:

· Any outages, either planned or forced, that may require additional monitoring;

THEN:

· Mark the outages in the Outage Scheduler OS Monitored Outage display as deemed necessary,

· Verify that the marked outages are in monitor mode,

· Continue to monitor the marked outages.

	Forced and Unavoidable Extensions

	1
	IF:

· A Forced or Unavoidable Extension is received, review the outage details;

THEN:
· Monitor congestion and make appropriate changes as necessary,
· Determine if it will have an effect on previously approved outages which may need to be withdrawn.

	Remedial Switching Action

	Definition
	“Remedial Switching Action” is a Forced Outage sub-type in the Outage Scheduler. ERCOT must approve all Remedial Switching Actions prior to implementation by TOs.

	< 3 Days in length
	Remedial Switching Actions are limited to a maximum of 3 days.

	> 3 Days in length
	If the Remedial Switching Action is required to remain active for longer than 3 days, a Planned Outage must be submitted to change the position of effected breakers and switches.

	Approve


	IF:

· No issues identified;

THEN:

· Approve the Outage as received.

	Reject
	IF:

· Reliability issues;

THEN:

· Notify Operations Support Engineer;

· Reject the outage to ensure system reliability.

	Restoration
	Breakers and switches in a Remedial Switching Action must be able to be returned to their normal position within 4 hours or less (this allows for drive time for remote switches w/o SCADA).

	Log
	Log all actions.

	Maintenance Outages

	Definition
	· Level 1- Equipment that must be removed from service within 24 hours to prevent a potential Forced Outage;

· Level 2 - Equipment that must be removed from service within 7 days to prevent a potential Forced Outage; and

· Level 3 - Equipment that must be removed from service within 30 days to prevent a potential Forced Outage.

	Maintenance Outage with start time ≤ 24 Hours
	IF:

· A Maintenance Outage is received, review the outage if the scheduled start time is within the next 24 hours;

THEN:
· Run a study to determine if the outage will cause any reliability issues.

	Approve

Maintenance Outage with start time ≤ 24 Hours 
	IF:

· No reliability issues identified;

THEN:

· Approve the Maintenance Outage.

	Coordinate Maintenance Outage with start time ≤ 24 Hours 
	IF:

· Reliability issues exist;

THEN:

· Coordinate the start of the outage with the TO to ensure system reliability if the outage is allowed to start within 24 hours, AND
· Approve the Maintenance Outage.

	Coordinate

Maintenance Level 2 and 3  Outage ≤ 24 Hours
	IF: 

· Maintenance Level 2 and 3 outages are received with a start time of less than the next 24 hours, AND

· Reliability issues exist;

THEN:

· Coordinate the start of the outage with the TO to ensure system reliability if the outage is within the allowed Maintenance Level 2 (7 Days) and 3 (30 Days) outage criteria,  

· ERCOT Outage Coordination group may help coordinate a new start time,
IF: 

· Reliability issues continue,
THEN:

· REQUEST the Operations Support Engineer investigate the development of a MP or TOAP (see section 4.7 Mitigation Plan),
· Approve the Maintenance Outage after coordination.

	Maintenance Level 2 and 3 Outages
	IF:

· Maintenance Level 2 and 3 outages are received with a start time of greater than the next 24 hours;

THEN:

· The ERCOT Outage Coordination group has a process to review all Maintenance Level 2 and 3 outages without further action.

	Log
	Log all actions.

	Consequential Outages

	1
	WHEN:

· A TO enters the breaker and switch statuses associated with an Electrical Bus;

THEN:

· A downstream topology processor will evaluate the breakers and switches associated with the applicable Electrical Bus to determine if the Electrical Bus is consequentially outaged, and to thereby designate the status of the Electrical Bus.

	Evaluate
	IF:

· The TO has submitted the outage in the Outage Scheduler;

THEN:

· As time permits, perform a study to determine the effects the outage has on the ERCOT system and evaluate the request and verify the Outage meets the applicable requirements.

	No

 Violations
	IF:

· NO, violations of applicable reliability standards exist; 

THEN:

· Approve the request in the Outage Scheduler.

	Yes 

Violations
	IF:

· YES, violations of applicable reliability standards exist; 

THEN:

· Reject the request in the Outage Scheduler.

	Log
	Log all actions.

	Returning from Planned Outage Early

	1
	Before an early return from an Outage, a Resource Entity or QSE may inquire of ERCOT whether the Resource is expected to be RUC decommitted by ERCOT upon its early return.  
IF:

·  A QSE is notified by ERCOT that the Resource will be RUC decommitted if it returns early and the Resource Entity or QSE starts the Resource within the previously accepted or approved Outage period; 

THEN:

· The QSE representing the Resource will not be paid any RUC decommitment compensation.

	Guidelines for Withdrawal of an Outage

	1
	IF:

· Security analysis and/or Operator experience indicates that an “Approved” or “Active” outage may have an adverse impact on system reliability;

THEN:

· Review the restoration time of the outage,
· Coordinate with the Entity,
· Withdraw the outage, if necessary, OR 
· Request assistance from ERCOT Outage Coordination.

	2
	WHEN:

· ERCOT withdraws an outage via the Outage Scheduler;

THEN:

· Enter an explanation in the “Reviewers Notes” listing the reliability concerns that caused the withdrawal,

· Notify the following, by e-mail, as soon as possible:

· OPS Outage Coordination

· OPS Support Engineering

· 1 ERCOT Shift Supervisors

· Include the following information:

· From Station – To Station (if applicable)

· The planned Start and End date of the outage.

	3
	IF:

· A TO or QSE reports that the outage in question has progressed to a point that withdrawal is not practicable within the outages designated restoration time;

THEN:

· Record this information in the “Outage Scheduler Reviewer’s Notes”,

· Log the outage in the Transmission Security Log,

· Inform the Shift Supervisor,

· Continue monitoring system security,

· Request Operations Support Engineer to develop Mitigation plan if necessary.

	Approval of an Outage on Transmission Devices of More than one hour duration

	1
	IF:

· A verbal request for permission to remove a transmission device from service for more than one hour is received;

THEN:

· Verify with the TO that the work being done will not prevent the device from being placed back in service immediately if needed,

· As time permits, determine that such operation will not affect the reliability of the Transmission System,

· If outage will cause reliability issues, go to Step 2

· If no impact to the system, go to 3.

	2
	IF:

· System reliability is impacted;

THEN:

· Discuss with the TO the possibility of postponing the outage to a later time OR deny the request.

	3
	IF:

· There is no reliability issue;

THEN:

· Verbally approve for the TO to remove a transmission device from service.

· Instruct TO to make notification when device is place back in service.

	Log
	Log all actions.

	Simple Transmission Outage

	Note
	A Simple Transmission Outage is a classification of outage that can be removed from service without effecting LMP prices or causing congestion.  The Outages are limited to the following 3 basic descriptions:

· Expanded Bus Outage

· Generator Breaker Maintenance

· Open-ended Lines
Refer to Desktop Guide Transmission Desk Section 2.2.

	1
	IF:

· The outage meets the requirements of a Simple Transmission Outage, which are:

· Has been submitted between 1 and 2 days in advance,

· Cannot exceed 12 hours in duration, AND
· Has a restoration time of 1 hour or less;

THEN:

· ERCOT will approve or reject within 8 business hours after receipt.

	Opportunity Outages 

	Definition
	An Outage that may be accepted by ERCOT when a specific Resource is Off-Line due to an Outage.

	1
	Opportunity Outages for Resources are a special category of Planned Outages that may be approved by ERCOT when a specific Resource has been forced Off-Line due to a Forced Outage and the Resource has been previously accepted for a Planned Outage during the next eight days.

	2
	When a Forced Outage occurs on a Resource that has an accepted or approved Outage scheduled within the following eight days, the Resource may remain Off-Line and start the accepted or approved Outage earlier than scheduled.  The QSE must give as much notice as practicable to ERCOT.

	3
	Opportunity Outages of Transmission Facilities may be approved by ERCOT when a specific Resource is Off-Line due to a Forced, Planned or Maintenance Outage.  A TO may request an Opportunity Outage at any time.  

	4
	When an Outage occurs on a Resource that has an approved Transmission Facilities Opportunity Outage request on file, the TO may start the approved Outage as soon as practical after receiving authorization to proceed by ERCOT.  ERCOT must give as much notice as practicable to the TO.

	Rescheduled High Impact Outage (RO)

	Definition
	An Outage on a High Impact Transmission Element (HITE) that was:

· Originally submitted and Approved as a Planned Outage with greater than 90 days’ notice 

· Being considered for rescheduling due to withdrawal of the original Planned Outage or subsequent Rescheduled Outage(s)

	1
	IF:

· The outage meets the requirements of a High Impact Outage (HIO) Outage

· The Outage interrupts flow on a High Impact Transmission element (HITE)

· The Outage was submitted with greater than 90 days’ notice

· The Outage needs to be Withdrawn or Rescheduled

· The Requesting TO wants to Reschedule the Outage

THEN:

· Go to the Outage Detail Page and select “Reschedule Outage”.  Select one element in the Group Outage converts the entire Group

	2
	IF:

· The requesting TO does NOT want to reschedule the Outage. 

THEN:

· Withdraw the outage

	Log
	Log all actions.


	Advance Action Notice (AAN)

	Definition
	Advance Action Notice (AAN)
Outage Adjustment Evaluation (OAE)

Outage Schedule Adjustment (OSA)
A type of Operating Condition Notice (OCN) that identifies a possible future Emergency Condition and describes future action ERCOT expects to take to address that condition unless the need for ERCOT action is alleviated by Qualified Scheduling Entity (QSE) and/or Transmission Service Provider (TSP) actions or by other system developments.

	Note
	ERCOT may issue an Advance Action Notice (AAN) in anticipation of a possible Emergency Condition.  Any AAN will identify actions ERCOT expects to take to address the possible Emergency Condition unless the need for ERCOT action is alleviated by QSE and/or TSP actions taken, or by other system developments that occur before a time stated in the AAN.

	Time Periods
	ERCOT shall issue the AAN a minimum of 24 hours prior to performing an OAE.  Additionally, unless impracticable, the OAE should not be performed until eight Business Hours have elapsed following issuance of the AAN.  ERCOT shall not issue an OSA under this Section unless it has first completed an OAE.

	1
	IF:

· ERCOT forecasts an inability to meet applicable transmission reliability standards and has exercised all other reasonable options AND;

· There are Resources with approved or accepted Resource Outages, whose approval or acceptance could be withdrawn to meet the applicable transmission reliability standards.

THEN:

· As instructed by the Shift Supervisor and in coordination with System Operations Management, Outage Coordination Management and Operations Support Management, issue an AAN.

	Hotline Issue AAN
	Notify TOs of an AAN Notice.

T#101 –Typical Hotline Script for an AAN

	Post
	Coordinate with the Resource Desk Operator for the posting of the notice on the ERCOT Website
Typical Posting Script:
ERCOT issued an AAN due to a possible future Emergency Condition of [reserve capacity deficiency or reliability problem] beginning [date HE XX] until [date HE XX].  [Summary of actions ERCOT may take].  ERCOT may seek [amount of capacity] from an OAE and then make the OSA.  On [date] at [xx:xx] ERCOT will execute an OAE if deemed necessary.

	2
	IF:

· Conditions change
THEN:

· Update the AAN

	Hotline Update AAN
	Notify TOs of an AAN Update Notice.

T#102 –Typical Hotline Script for an Update of an AAN

	Updated Post
	Coordinate with the Resource Desk Operator for the posting of the notice on the ERCOT Website
Typical Posting Script:
ERCOT has updated an AAN due to conditions changing and a possible future Emergency Condition of [reserve capacity deficiency or reliability problem] beginning [date HE XX] until [date HE XX].  [Summary of actions ERCOT may take].  ERCOT may seek [amount of capacity] from an OAE and then make the OSA.  On [date] at [xx:xx] ERCOT will execute an OAE if deemed necessary.

	OSA
	WHEN:

· Notified by the Shift Supervisor the OSA has executed.

THEN:

· Notify TOs of executing the OSA process.

T#88 Outage Scheduler Adjustment (OSA)

	Hotline Cancel AAN
	WHEN:
· ERCOT determines that the possible Emergency Condition has been alleviated by QSE or TSP action, by ERCOT action, or by other system developments;

THEN:

· Using the Hotline, cancel the  AAN

T#103 –Typical Hotline Script to cancel an AAN

	Cancel 

Posting
	WHEN:
· ERCOT determines that the possible Emergency Condition has been alleviated by QSE or TSP action, by ERCOT action, or by other system developments.
THEN:
· Coordinate with the Resource Desk Operator to cancel the ERCOT Website message(s).

	Log
	Log all actions.


5.2
Protective Relay Outages

Procedure Purpose:  Be aware and respond if needed to protective relay system failures when notified by a QSE or TO.

	Protocol Reference
	
	
	
	

	Guide Reference
	6.2.4
	
	
	

	NERC Standard
	
	
	
	


	Version: 2 
	Revision: 0
	Effective Date:  December 5, 2025


	Step
	Action

	Note
	· Protective relay maintenance that ERCOT ISO has been made aware of can be found on the Outage Calendar located on the System Operations SharePoint.

· Protective relay systems include relays, associated communications systems, voltage and current sensing devices, station batteries, and DC control circuitry.

	Planned

Outage
	IF:

· Notified that a relay is going to be removed from service (Planned);
THEN:

· Verify or enter information on the Outage Calendar located on the System Operations SharePoint Site,

· A relay can’t be removed from service unless there are secondary/back up relays that will be functional and no system degradation will occur;

IF:

· Secondary/back up relays in place;
THEN:

· Notify the TO they can proceed with work.

· 

	Protective

Relay

or

Equipment

Failure
	When notified by a QSE or TO that a protective relay or equipment failure reduces system reliability:

· Ask the QSE or TO how it reduces system reliability and what corrective actions have been taken,

· Ask the QSE or TO if notifications have been made to any other affected TOs,

· Notify the Operations Support Engineer to verify that system reliability has been affected.  If so, a corrective action must be taken within 30 minutes.  Corrective action could include re-dispatching as studies dictate, possible reconfiguration, or firm Load shed,

· Determine if other TOs are affected by this failure and make notification by phone.


	Forced

Outage
	IF:

· Notified that a primary relay has been removed from service (forced);
THEN:

· Ask if the secondary/back up relay is functional;

IF:

· There is no secondary/back up relay;
THEN:

· The equipment will need to be removed from service since it is no longer protected.

	Log
	Log all actions.


6.1
Voltage Control

Procedure Purpose:  Ensure adequate voltage levels are maintained throughout the ERCOT grid to prevent a potential voltage collapse.

	Protocol Reference


	3.15.1(3)
	6.5.7.1.10(3)(h)
	6.5.7.7(2) 
	6.5.7.7(6)

	Guide Reference
	2.2.5(1)
	2.2.6(2)
	2.2.10
	2.7.2

	
	2.7.3
	2.7.4
	
	

	NERC Standand


	IRO-001-4

R1
	IRO-002-7

R5
	IRO-008-3

R5, R6
	NUC-001-4

R4, R4.1, R4.2, R9, R9.2, R9.2.1, R9.4,  R9.4.2

	
	TOP-001-6

R1, R7, R10, R10.1, R10.3, R10.6, R14
	VAR-001-5

R2, R3 
	
	


	Version: 2 
	Revision: 0
	Effective Date:  December 5, 2025


	Step
	Action

	Note
	The intent of this procedure is to verify and take corrective action for voltage issues.  Although the steps within the procedure are numbered, the numbering is for indexing purposes and are not sequential in nature.  The System Operator will determine the sequence of steps, or any additional actions required to prevent voltage collapse.

	Note
	ERCOT posts the "Seasonal Voltage Profiles" desired voltage for each generation interconnection.  The current profiles for generators may be found in the 

ERCOT Market Information System (MIS) Secure site.

Select: Grid> Transmission>Voltage and Dynamic Ratings>Voltage Profiles

Select “Voltage Profiles” Open the current file>Open the xls file.

	Note
	All Operating Instructions shall be in a clear, concise, and definitive manner.  Ensure the recipient of the Operating Instruction repeats the information back correctly.  Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings.

	Voltage Issues at Nuclear Power Plants

	Note
	ERCOT and TOs shall maintain the switchyard voltage at each operating nuclear power plant at a value that does not violate its licensing basis with the Nuclear Regulatory Commission.

	Comanche

Peak

Voltage

Table
	For Comanche Peak:

System
345 kV

138kV

Nominal Voltage

352 kV

141 kV

Tolerance

+2.56% or -3.40%

+2.13% or -4.26%

Maximum Voltage

361 kV

144 kV

Minimum Voltage

340 kV

135 kV

Decordova and Wolf Hollow are points at which generation voltage adjustments can be expected to impact control of Comanche Peak voltage.

	STP

Voltage

Table
	For South Texas Project:

Plant Configuration
Maximum kV

Minimum kV

Normal line up

362.25 

339

Alternate line up

362.25

339

The STP Switchyard Facilities’ steady state voltage should be maintained within the ranges above.  This could become more difficult with both STP units off-line.

Calaveras (Spruce), Braunig (Von Rosenberg), DOW, and WAP are points at which generation voltage adjustments can be expected to impact control of STP voltage.

Note:  It is the STP QSEs responsibility to notify ERCOT when STP is in an alternate line up.

	1
	IF:

· Voltage levels exceed the limits as stated above in the voltage tables;

THEN:

· Notify the appropriate Nuclear Plant’s QSE

· Explain the event and an estimate of when voltage is expected to return to normal, to the extent possible

· Notify CenterPoint if related to STP

· Coordinate the appropriate voltage control action with the affected TO and QSE.

	2
	WHEN:

· Voltage is back to normal range;

THEN:

· Notify the appropriate Nuclear Plant QSE, and

· Notify the affected TO and CenterPoint (if related to STP)

	Real-Time Voltage Issues

	Note
	· Post-Contingency low voltage alarms beyond the emergency operating low voltage limit could trigger Automatic Under-Voltage Load Shedding if the contingency were to occur.  Detailed information on the amount of load on Automatic Under-Voltage Load Shedding Schemes (UVLS) can be found in Desktop Guide Transmission Section 2.9.

· ERCOT, shall instruct QSEs having Generation Resources or Energy Storage Resources (ESRs) required to provide Voltage Support Service (VSS), to adjust for voltage support within the Unit Reactive Limit (URL) provided by the QSE to ERCOT.

· Generation Resources or ESRs required to provide VSS may not reduce high reactive loading on individual units during abnormal conditions without the consent of ERCOT unless equipment damage is imminent.

· Major transmission lines shall be kept in service during Light Load as much as possible.  Lines should only be removed after all applicable reactive controls are implemented and studies are performed showing that reliability will not be degraded.

	Note
	ERCOT Nominal Voltage Levels are 345kV, 230kV, 138kV, 115kV and 69kV.

The general voltage guidelines are as follows (listed in kV):

Nominal Voltage

Normal Operating Limits

Emergency Operating Limits

Ideal Voltage Range

345

327.75 – 362.25

310.5 – 379.5

345 – 359

230

218.5 – 241.5

207 – 253

230 – 240

138

131.1 – 144.9

124.2 – 151.8

138 – 144

115

109.25 – 120.75

103.5 – 126.5

115 – 120

69

65.55 – 72.45

62.1 – 75.9

69 – 71.5

Some TOs utilize different Normal (Basecase) and Emergency (Post-Contingency) voltage operating limits than the general voltage guidelines.  These limits can be seen under the Network Limits display.



	SOL Comms
	If electronic communication of SOL exceedances is unavailable, refer to section 3.8, “SOL Exceedance Communications Thresholds”, for criteria of manually communicating SOL exceedances.  

	1
	Monitor the voltage contingency violations and Basecase voltage violation displays in RTCA

WHEN:

· Indicated by SCADA alarms, RTCA or by a TO of voltage concerns;

THEN:

· Determine if the SCADA is of similar magnitude to the pre-contingency value.  

· Example:  Review nearby kV measurements

· Review “Voltage Tracking Issues Spreadsheet” on SharePoint to ensure the Basecase/contingency is not listed

· If listed, no further action needed. 

IF:

· Inaccurate;

THEN:

· Notify the Shift Supervisor and Operations Support Engineer to investigate.

· Log in “Voltage Tracking Issues” on SharePoint

· Make log entry.

	2
	IF:

· Accurate;

THEN:

· Discuss the voltage concern with the appropriate TO
· Has the TO utilize all static reactive power resources? (capacitors, reactors, change transformer taps)
Typical Script to appropriate TO:

“This is ERCOT Operator [first and last name].  At [xx:xx], ERCOT is instructing [TO] to [Raise/Lower] voltage at [specify bus] by [Closing/Opening/Adjusting] [Cap/Reactor/Transformer Tap] to resolve a [Basecase Voltage Violation/RTCA Voltage Contingency Violation].  [TO] please repeat this instruction back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.
IF:

· Additional reactive support or coordination is needed to clear the violation;

THEN:

· Discuss with the appropriate TO and come to an agreement as to the proper action.  This could be transmission switching, adjusting voltage at a nearby Generation Resource or ESR, bringing on an additional Resource, returning a planned outage, or development of an CMP 

IF:

· The TO needs assistance from ERCOT to get voltage adjusted at a Resource;

THEN:

· Instruct the appropriate QSE to raise or lower bus voltage, 

· The QSE should complete the requested in no more than five minutes. 

Typical Script to appropriate QSE:

“This is ERCOT Operator [first and last name].  At [xx:xx], ERCOT is instructing [QSE] to [raise or lower] voltage at [specify bus] by [+1 or 2kV or -1 or 2kV] for a target of [target kV].  [QSE] please repeat this instruction back to me.”

If repeat back is CORRECT, “That is correct, thank you.”

If INCORRECT, repeat the process until the repeat back is correct.

	3
	When voltage issue has been resolved notify the impacted TO.

	East HVDC Tie Voltage Limits

	Note
	The East HVDC tie has voltage limits depending on the tie condition.

See Desktop Guide Transmission Desk 2.19

	1
	WHEN:

· Notified by AEP TOP that Reactors have been placed in/out of service on the East DC tie

THEN:

· Notify the DC tie Desk Operator 

	Log
	Log all actions.

	Future Voltage Studies or Issues

	NOTE
	Each hour run a STNET study for Two hours out (example it is 0100, run study for 0300) to review voltage violations. 

	
	WHEN:

· Notified by the Alternate Control Center or the RUC Desk Operator of future voltage violations;

THEN:

· Review the “Voltage Tracking Issues” on SharePoint.  If it is reoccurring, the solution may be listed on the “Resolutions” tab 

IF:

· Any capacitors or reactors are AVAILABLE that can address the violation;
THEN:

· Ensure the capacitor or reactor clears the violation
IF:

· Additional reactive support or coordination is needed to address the violation;
THEN:

· Discuss the identified future voltage violations with the appropriate TO and come to an agreement as to the proper action. This could be transmission switching, development of a CMP, making reactive devices available, or RUC commitment of additional generation
IF:

· An Off-Line Resource is needed to resolve the voltage violation;
THEN:

· Coordinate with the RUC Desk Operator to RUC commit the Resource

	Voltage Contingencies
	IF:

· Voltage contingencies exist;
THEN:

· Check “Voltage Tracking Issues” spreadsheet on SharePoint to ensure the contingency is not listed.

· If not listed, convey the voltage violations to the Transmission and Security Desk Operator with the potential resolution

· Validate the resolution

· Create a savecase, use naming convention “SC_TRAN (HE)_(DATE)

· Make at least one detailed log entry per shift that the studies are being executed.   If any new voltage violations are identified that do not have a solution, log the information and notify the Transmission and Security Desk Operator of the new violation(s)

· Update the “Voltage Tracking Issues” spreadsheet listing the new voltage violation with the contingency resolution.
IF:

· Unsolved contingencies exists;

THEN:

· Communicate any unsolved contingency to the Shift Engineer and Transmission and Security Desk Operator with potential solutions.

· Some potential solutions could be transmission switching, creation of a manual constraint, bringing on an additional Resource, returning a planned outage, or development of a CMP.

· Validate the resolution

· Update the “Voltage Tracking Issues” spreadsheet listing the new unsolved contingency with the contingency resolution.

	Violated 

Constraints
	REVIEW REFERENCE DISPLAYS:

Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP Binding Constraint Summary

Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP Constraint Summary

REVIEW:

· Violated constraints.  If needed, notify the Operations Support Engineer to determine the validity; 

IF:

· Invalid, no further action is required;

IF:

· Valid; AND

· Related to a phase shifter tap settings,

THEN:

· Notify Operations Support Engineer to determine and determine if adjusting a Phase Shifter would reduce the flow, 

· Create Suggestion Plan for Constraint,

· Manually RUC commit resources as needed 

	Phase Angles
	Monitor phase angles during the 2 hour ahead voltage studies

IF:

· Phase angle exceedances exists;

THEN:

· Communicate any phase angle exceedances to the Shift Engineer and Transmission and Security Desk Operator for potential solutions.

· Some potential solutions could be transmission switching, creation of a manual constraint, bringing on an additional Resource, returning a planned outage, or development of a CMP.

	Log
	Log all actions.

	ERCOT requesting Resource to operate beyond URL

	Exceeding

URL or

Reducing

Output
	If ERCOT determines that a Generation Resource or ESR should be instructed to provide additional MVAr beyond its URL or that a Generation Resource’s real power output should be decreased to allow the Generation Resource to provide additional Reactive Power beyond the URL, ERCOT shall issue a Resource-specific  Dispatch Instruction / Operating Instruction requiring any change in Reactive Power and/or real power output, except that ERCOT may not require a Generation Resource to exceed its excitation limits.

IF:

· A QSE communicates that an ERCOT or TO voltage instruction requires the Generation Resource or ESR to exceed its Unit Reactive Limit (URL) or the Resource must reduce MW;

THEN:

· Request the QSE to follow the instruction and inform them that Operations Analysis will make the verification and either an electronic Dispatch Instruction for settlements will be issued or a call with an explanation will be followed up on the next business day
· Send e-mail to Operations Analysis and shiftsupv with the following information:
· Resource name

· Specific voltage set point.  

· Start time

· End time



	QSE

Performance
	Maintain a log of QSEs acknowledgements of Dispatch Instructions / Operating Instructions concerning scheduled voltage or scheduled Reactive output requests.  QSEs responding in less than two minutes from the time of issuance shall be deemed satisfactory.

	Voltage Security Assessment Tool (VSAT)

	Note
	VSAT and RUC perform full AC analysis of all contingencies.  

	1
	IF:

· Any of the monitored VSAT scenario results approaches the Reliability margins listed in the table below;

THEN:

· Manually rerun the entire sequence of RTNET, RTCA, and RTDCP (VSA)

· Confirm VSAT indicates either “Normal” or “Pending”

Reliability Margin Table

Scenario Name

 Margin

LAREDO
25MW
N-H_G
200MW
N-H_L
200MW
PNHNDL
50MW
O-VAL_L
100MW
For N-H_G and N_H_L:

Refer to section 4.4 North-Houston Voltage Stability Limit of this procedure.

	2
	IF:

· VSAT indicates that a Reliability Margin may be exceeded;

THEN:

· Determine if the current Reliability Margin pre-contingency value is less than the Margin on the table in the previous step.

· If no, no further action is required.

· If yes, go to Step 3.

	3
	Determine the contingency status in RTCA (solved/unsolved).

IF:

· Solved,

· Have Operations Support Engineer verify if the problem is real,

· If real, request information on weak bus,

· Request the TO in the affected area turn on capacitor banks and turn off reactors near the weak busses.

· If not real, no further action is required.

· Unsolved,
· Notify Shift Supervisor and Operations Support Engineer

· Manually dispatch fast ramp generators to increase generation in weak bus area.

· If all online units are at maximum capacity

· Coordinate with the RUC Desk Operator to RUC commit additional resources in the weak bus area that are available.

	4
	WHEN:

· Capacitor banks are placed in service;

THEN:

· Rerun VSAT with new topology.

	5
	Determine if the current Reliability Margin pre-contingency value is greater than the Margin Value from the table above.

IF:
· The current Reliability Margin pre-contingency value is greater than the Margin;

THEN:

· No further action is required.

OR

IF:

· The current Reliability Margin pre-contingency value is less than the Margin;

THEN:

· Determine if there are more units available in the affected area, AND

· Repeat the process starting with Step 3.

If no additional generation is available, continue.

	6
	IF:

· No additional generation is available;

THEN:
· Notify Operations Support Engineer to create a Mitigation Plan.

	Power System Stabilizers (PSS) & Automatic Voltage Regulators (AVR)

	Note
	Each QSE’s Generation Resource or ESR providing VSS shall operate with the unit’s Automatic Voltage Regulator (AVR) in the voltage control mode unless specifically instructed to operate in manual mode by ERCOT.

	Note
	The status of each PSS and AVR can be viewed at EMP applications>SCADA>Unit AVR/PSS Summary EMS Display. 

	1
	Monitor each QSE’s Generation Resource or ESR AVR status.
WHEN:

· A discrepancy is identified;

THEN:

· Verify the discrepancy with the QSE or TO

IF:
· Determine if the AVR is in manual or in Power Factor Mode;

THEN:
· Instruct the QSE or TO to manually adjust VAR output as required to maintain voltage set-point until the AVR is back in service,

NOTIFY:

· The appropriate TO of the status, if not already done so by QSE,

· Enter the status change information into the ERCOT Logs,

· Log type of “AVR”.  

· Include the company name, the name of the person spoken with, and reason (if device is being placed in or taken out of service).

· Include that the TO has been notified of change in status

· Copy and paste the log entry into an e-mail and send to

· “Operations Analysis”

· “OPS Support Engineering”

· “OPS Advanced Network Applications”

· “1 ERCOT System Operators”

	2
	WHEN:

· Notified by a QSE or TO of a PSS or AVR in manual or in Power Factor Mode;

THEN:

· Instruct the QSE or TO to manually adjust VAR output as required to maintain voltage set-point until the AVR is back in service,

NOTIFY:

· The appropriate TO of the status, if not already done so by QSE,

· Enter the status change information into the ERCOT Logs,

· Log type of either “PSS” or “AVR”.  

· Include the company name, the name of the person spoken with, and reason (if device is being placed in or taken out of service).

· Include that the TO has been notified of change in status

· Copy and paste the log entry into an e-mail and send to

· “Operations Analysis”

· “OPS Support Engineering”

· “OPS Advanced Network Applications”

· “1 ERCOT System Operators”

	3
	WHEN:

· Notified by a QSE that the PSS or AVR is in Auto and back in service;

NOTIFY:

· The appropriate TO of the status, if not already done so by QSE,

· Enter the status change information into the ERCOT Logs,

· Log type of either “PSS” or “AVR”.  

· Include the company name, the name of the person spoken with, and reason (if device is being placed in or taken out of service).

· Include that the TO has been notified of change in status

· Copy and paste the log entry into an e-mail and send to

· “Operations Analysis”

· “OPS Support Engineering”

· “OPS Advanced Network Applications”

· “1 ERCOT System Operators”

	Log
	Log all actions.

	Generator Voltage Set Points

	Note
	TOs may change Voltage Set Points for Generators different than in the seasonal Voltage Profiles as necessary.  TOs are required to telemeter Voltage Set Point targets and measurements at the POI for each Generation Resource or ESR.  Generation Resources or ESR (greater than 20 MVA) are required to maintain the voltage at the POI within its KV based tolerance band of the target.

	Note
	The current status of each Voltage Set Point target and measurement can be viewed at EMP applications>SCADA> Voltage Set Point Display.   (ERCOT to QSE communication) Additionally, after going to Unit Voltage Set Point Display (Voltage Set Point tab), >Related Displays>Voltage Set Point Communication Display. (TO ERCOT communication)

	Note
	Generators have up to 5 minutes to respond (make adjustments) to a new Voltage Set Point Instruction even if the Generator is within the tolerance band of the new Voltage Set Point.  If a Generator cannot maintain the POI voltage within the tolerance band of the Voltage Set Point, it must notify it’s TO within 15 minutes of a new Voltage Set Point instruction OR within 30 minutes of an existing Voltage Set Point instruction OR notify ERCOT within 15 minutes of a VSS Dispatch Instruction from ERCOT. 

	Note
	When a Voltage Set Point target is entered outside of a reasonability range (.95 to 1.05 pu), the EMS will hold the last good target and identify the target as “Unreasonable”.  

	1
	IF:

· A Generation Resource or ESR is not maintaining voltage at the POI within its KV based tolerance band (checked as “Violated”).

· 345KV = +/- 4 KV of target

· 230KV = +/- 3 KV of target

· 138KV = +/- 2 KV of target

· 115KV = +/- 2 KV of target

·   69KV = +/- 1 KV of target

THEN:

· Instruct the TO to utilize available static reactive devices and if still necessary, coordinate with the resources to make adjustments to maintain the voltage at the POI at the Voltage Set Point target within its tolerance band.

	2
	IF:

· A Voltage Set Point Target is checked as “Unreasonable”;

THEN:

· Contact the appropriate TO,

· State that ERCOT has received an unreasonable Voltage Set Point target (outside of .95 to 1.05 pu),

· Instruct TO to enter the correct Voltage Set Point target.

	Log
	Log all actions.


7.1
Market Notifications

Procedure Purpose: Guidelines for issuing Emergency Conditions and the four possible levels: Operating Condition Notices (OCN), Advisories, Watches, and Emergency Notices.

	Protocol Reference


	3.1.4.6
	6.5.9.3

	6.5.9.3.1
	6.5.9.3.2

	
	6.5.9.3.3
	6.5.9.3.4
	
	

	Guide Reference
	4.2.1
	4.2.2
	4.2.3
	4.2.4

	NERC Standard
	
	
	
	


	Version: 2 
	Revision: 0
	Effective Date:  December 5, 2025


	Step
	Action

	Note
	· ERCOT is in an Emergency Condition whenever ERCOT Transmission Grid status is such that a violation of security criteria presents the threat of uncontrolled separation or cascading Outages and/or large-scale service disruption to Load (other than Load being served from a radial transmission line) and/or overload of a Transmission Element, and no timely solution is obtainable through SCED or CMPs.

· Consider the severity of the potential Emergency Condition prior to the issuance of a notification.  The severity of the Emergency Condition could be limited to an isolated local area, or the condition might cover large areas affecting several entities, or the condition might be an ERCOT-wide condition potentially affecting the entire ERCOT System.

· The sequence of notifications issued may vary due to changing system conditions or other operational issues and it may be necessary to skip certain notifications due to the severity of the situation.

	Operating Condition Notice (OCN)

	Note
	OCN’s are used to inform Market Participants of a possible future need for more Resources due to conditions that could affect ERCOT System reliability.  OCNs are for informational purposes only and may solicit additional information to determine whether the issuance of an Advisory, Watch, or Emergency Notice is warranted. OCNs serve as a reminder to QSEs and TSPs that some attention to the changing conditions may be warranted.

	1
	As instructed by the Shift Supervisor or when appropriate, issue an OCN.  The OCN can be issued for any of the following reasons:

· Insufficient Resources to meet forecasted conditions

· There is a projected reserve capacity shortage in DRUC that could affect reliability and may require more Resources

· When extreme cold weather is developing and forecasted to impact the ERCOT Region
· When extreme hot weather is forecasted to impact the ERCOT Region

· When a Hurricane or Tropical Storm is developing and forecasted to impact the ERCOT Region 

· Unplanned transmission Outages that may impact reliability

When anticipated adverse weather conditions are forecasted, ERCOT may confer with TOs and QSEs regarding the potential for adverse reliability impacts and contingency preparedness.

	Advance Action Notice (AAN)

	Note
	Outage Adjustment Evaluation (OAE)

Outage Schedule Adjustment (OSA)

An AAN is a type of OCN, ERCOT may issue an AAN in anticipation of a possible Emergency Condition.  An AAN will identify actions ERCOT expects to take to address the condition unless the need for ERCOT action is alleviated by QSE and/or TSP actions or by other system developments.

	1
	As instructed by the Shift Supervisor and in coordination with Outage Coordination and Operations Support, issue an AAN.  The AAN can be issued for any of the following reasons:

· Insufficient Resources to meet forecasted conditions

· There is a projected reserve capacity shortage in DRUC that could affect reliability and may require more Resources
· When extreme cold weather is developing and forecasted to impact the ERCOT Region
· When extreme hot weather is forecasted to impact the ERCOT Region

· When a Hurricane or Tropical Storm is developing and forecasted to impact the ERCOT Region 

· Unplanned transmission Outages that may impact reliability

When anticipated adverse weather conditions are forecasted, ERCOT may confer with TOs and QSEs regarding the potential for adverse reliability impacts and contingency preparedness.

	Advisory

	1
	As instructed by the Shift Supervisor or when appropriate, issue an Advisory.  The Advisory can be issued for any of the following reasons:

· When the probability of an approaching Hurricane or Tropical Storm impacting the ERCOT Region increases, and concerns exist to escalate awareness

· When the probability of extreme cold weather impacting the ERCOT Region increases, and concerns exist to escalate awareness
· When the probability of extreme hot weather impacting the ERCOT Region increases, and concerns exist to escalate awareness

· When conditions are developing or have changed and more Ancillary Services will be needed to maintain current or near-term reliability

· ERCOT exercises its authority to increase Ancillary Service requirements above the quantities originally specified in the Day-Ahead Market in accordance with ERCOT procedures

· When extreme weather or ERCOT System conditions require more lead-time than the normal Day-Ahead Market allows

· Transmission system conditions are such that operations within security criteria are not likely or possible due to Forced Outages or other conditions unless a CMP exists

· Loss of communications or control condition is anticipated or significantly limited

· ERCOT may require information from QSEs representing Resources regarding the Resources’ fuel capabilities. Requests for this type of information shall be for a time period of no more than seven days from the date of the request

	Watch

	1
	As instructed by the Shift Supervisor or when appropriate, issue a Watch.  The Watch can be issued for any of the following reasons:

· A reserve capacity shortage is projected with no market solution available that could affect reliability 

· When an approaching Hurricane or Tropical Storm is imminent and anticipated to have an adverse impact on the ERCOT Region

· When impacts from extreme cold weather is imminent and anticipated to have an adverse impact on the ERCOT Region
· When impacts from extreme hot weather is imminent and anticipated to have an adverse impact on the ERCOT Region

· Conditions have developed such that additional Ancillary Services are needed in the Operating Period

· 
· Market-based congestion management techniques embedded in SCED will not be adequate to resolve transmission security violations 

· Forced Outages or other abnormal operating conditions have occurred, or may occur that would require ERCOT to operate with active violations of security criteria as defined in the Operating Guides unless a CMP exists

· ERCOT varies from timing requirements or omits one or more Day-Ahead or Adjustment Period and Real-Time procedures.

· ERCOT varies from timing requirements or omits one or more scheduling procedures in the Real-Time process

· The SCED process fails to reach a solution, whether ERCOT is using one of the measures in Failure of the SCED Process. 

· The need to immediately procure Ancillary Services from existing offers

· ERCOT may instruct TOs to reconfigure transmission elements as necessary to improve the reliability of the system
· ERCOT may require information from QSEs representing Resources regarding the Resources’ fuel capabilities. Requests for this type of information shall be for a time period of no more than seven days from the date of the request

	Emergency Notice

	1
	As instructed by the Shift Supervisor or when appropriate, issue an Emergency Notice.  The Emergency Notice can be issued for any of the following reasons:

· Loss of Primary Control Center Functionality

· Load Resource deployment for North-Houston voltage stability

· Load Resource deployment for South Texas IROL’s.

· ERCOT cannot maintain minimum reliability standards (for reasons including fuel shortages) during the Operating Period using every Resource practically obtainable from the market

· Immediate action cannot be taken to avoid or relieve a Transmission Element operating above its Emergency Rating

· ERCOT forecasts an inability to meet applicable Reliability Standards and it has exercised all other reasonable options

· A transmission condition has been identified that requires emergency energy from any of the DC-Ties or curtailment of schedules

· The Transmission Grid is such that a violation of security criteria as defined in the Operating Guides presents the threat of uncontrolled separation or cascading outages, large-scale service disruption to load (other than Load being served from a radial transmission line) and/or overload of Transmission Elements, and no timely solution is obtainable through SCED or CMPs

· When extreme cold weather is beginning to have an adverse impact on the ERCOT System
· When extreme hot weather is beginning to have an adverse impact on the ERCOT System
· When a Hurricane or Tropical Storm is beginning to have an adverse impact on the System

	Operating Condition Scripts

	Hotline
	Communications must specify the severity of the situation, the area affected, the areas potentially affected, and the anticipated duration of the Emergency Condition.

T#37 – Typical Hotline Script for Operating Condition [OCN/Advisory/Watch/Emergency]

	Post
	All notices must be posted on the ERCOT Website using Grid Conditions Communications (GCC) Notices.

· For “free form” messages, the “Notice priority” will be specified as follows:

· Operational Information/OCN type messages – low priority

· Advisory/Watch type messages – medium priority

· Emergency type messages – high priority

	Hotline Cancellation
	T#38 – Typical Hotline Script to Cancel Operating Condition [OCN/Advisory/Watch/Emergency]

	Log
	Log all actions.

	Specific Scripts for QSE’s

	Note
	At times, the Real-Time, Resource or RUC Desk Operators takes the lead on the issuance of Hotline calls for specific procedures they have.  The following scripts are to help guide you when specific procedures don’t exist for the Transmission and Security Desk Operator.

	Deployment of Load Resources
	T#40 - Deployment of Load Resources to Maintain a Minimum 500MW of Generation RRS

	SCED

Or 

RLC

Failure
	Note: RLC can fail independently of AGC; this same script will also be used for a RLC failure.  If RLC is failed, SCED will have invalid results.

T#41 - Typical Hotline Script for Watch for SCED/RLC Failure
T#42 - Typical Hotline Script to Cancel Watch for SCED/RLC Failure


	EMMS

(LFC and RLC/SCED)

Failure
	T#43 - Typical Hotline Script for Emergency Notice for LFC/EMS and SCED Failure

T#44 - Typical Hotline Script to Cancel Emergency Notice for LFC/EMS Functioning, SCED valid

	
	


	

	


	

	


	

	


	DAM Timeline

Deviation
	T#53 - Typical Hotline Script for Advisory for DAM Timeline Deviation 

T#54 - Typical Hotline Script to Cancel Advisory for DAM Timeline Deviation

	DAM Failure
	T#55 - Typical Hotline Script for Watch for DAM Failure 

T#56 - Typical Hotline Script to Cancel Watch for DAM Failure 

	DRUC Delay or Timeline Deviation
	T#57 - Typical Hotline Script for Advisory for DRUC Timeline Deviation 
T#58 - Typical Hotline Script to Cancel Advisory for DRUC Timeline Deviation

	DRUC  Timeline not Met
	T#59 - Typical Hotline Script for Watch for DRUC not completing by 18:00 

T#60 - Typical Hotline Script to Cancel Watch for DRUC not  completing by 18:00

	HRUC Failure or Timeline Deviation
	T#61 - Typical Hotline Script for Watch for HRUC Failure / Timeline Deviation 

T#62 - Typical Hotline Script to Cancel Watch for HRUC Failure/Timeline/Deviation

	DRUC

Committed 

For Capacity

Shortage
	T#63 - Typical Hotline Script for OCN for Projected Reserve Capacity Shortage 

T#64 - Typical Hotline Script to Cancel OCN for Projected Reserve Capacity Shortage


	Excess Generation
	T#65 - Typical Hotline Script for OCN for Projected Excess Reserve Capacity 

T#66 - Typical Hotline Script to Cancel OCN for Projected Excess Reserve Capacity

	Projected Reserve Capacity Shortage with no market solution
	T#67 - Typical Hotline Script for Watch for Projected Reserve Capacity Shortage with No Market Solution
T#68 - Typical Hotline Script to Cancel Watch for Projected Reserve Capacity Shortage with No Market Solution

	RMR Projected Reserve Capacity Shortage
	T#69 - Typical Hotline Script for Watch for Projected Reserve Capacity Shortage with No Market Solution, RMR recommended
T#70 - Typical Hotline Script to Cancel Watch for Projected Reserve Capacity Shortage with No Market Solution, RMR recommended

	
	

	BAAL Firm Load Shed
	 T#8 EEA3 Firm Load Shed

T#10 EEA3/BAAL Restore All Firm Load


	Unannounced Constant Frequency Control Test
	T#99 QSE on Constant Frequency Control for Unannounced Constant Frequency Control Test
T#100 Cancel QSE on Constant Frequency Control for Unannounced Constant Frequency Control Test


7.3
Implement EEA Levels

Procedure Purpose:  To provide for maximum possible continuity of service while maintaining the integrity of the ERCOT system to reduce the chance of cascading outages.

	Protocol Reference
	6.5.9.3.4(6)
	6.5.9.4
	6.5.9.4.2
	

	Guide Reference


	4.5.3
	4.5.3.1
	4.5.3.2
	4.5.3.3

	
	4.5.3.4
	
	
	

	NERC Standard


	EOP-011-4

R2, R2.1, R2.2, R2.2.4, R2.2.7, R2.2.8
	IRO-001-4

R1
	TOP-001-6

R1, R8
	


	Version: 2 
	Revision: 0
	Effective Date:  December 5, 2025


	Step
	Action

	Note
	ERCOT MAY immediately implement EEA Level 2 when clock-minute average system frequency falls below 59.91 Hz for 15 consecutive minutes.  

ERCOT MAY immediately implement EEA Level 3 any time the clock-minute average system frequency falls below 59.91 Hz for 20 consecutive minutes OR when steady-state frequency falls below 59.8 Hz for any duration of time. 

ERCOT SHALL immediately implement EEA Level 3 any time the steady-state frequency is below 59.5 Hz for any duration.

	Note
	ERCOT will declare an EEA Level 1 when PRC falls below 2,500 MW and is not projected to be recovered above 2,500 MW within 30 minutes without the use of the following actions that are prescribed for EEA Level 1

	Note
	Confidentiality requirements regarding transmission operations and system capacity information will be lifted, as needed to restore reliability.

	ESR
	Energy Storage Resources (ESR) will be required to suspend charging during an Energy Emergency Alert (EEA) except in limited circumstances, including Security-Constrained Economic Dispatch (SCED), Load Frequency Control (LFC) Dispatch, or a manual instruction. An exception to this provision is if an ESR is co-located with onsite generation that would be incapable of exporting additional power to the ERCOT System. 

	Media

Appeal
	When an ERCOT-wide appeal through the public news media for voluntary energy conservation is made.  Notify the TOs by Hotline.

T#39 - Typical Hotline Script for Media Appeal

	TCEQ
	The Texas Commission on Environmental Quality (TCEQ) will exercise enforcement discretion for exceedances of emission limits and operational limits for Resources that exceed air permit limits in order to maximize generation for the duration of an EEA event.  A Market Notice will be sent to Market Participants. Make Hotline call.

T#87 Typical Hotline Script for TCEQ Notice of Enforcement Discretion

	Implement EEA Level 1

	1


	IF:

· PRC < 2500 MW and is not projected to be recovered above 2500 MW within 30 minutes without the use of EEA Level 1; 

THEN:

· Using the Hotline, notify the TOs to implement EEA 1. 

T#5 - Typical Hotline Script for EEA1 
After the repeat, give TOs an update of system conditions, including chances of proceeding into an EEA 2.

	Log
	Log all actions.

	Implement EEA Level 2

	Note
	ERCOT MAY immediately implement EEA Level 2 when the clock-minute average system frequency falls below 59.91 Hz for 15 consecutive minutes.

	1


	IF:

· PRC < 2000 MW or unable to maintain system frequency at 59.91 Hz and is not projected to be recovered above 2000 MW within 30 minutes without the use of EEA Level 2;

THEN:

· Using the Hotline, notify the TOs to implement EEA 2 and any measures associated with EEA 1, if not already implemented. 

· If the energy conservation call has not been made previously, it can be combined with this call.

· Reduce Customer Load by using distribution voltage reduction measures, if deemed beneficial. If not requested from previous steps.

· When available implement any available Load management plans to reduce Customer Load if not already implemented.

T#7 - Typical Hotline Script for EEA2 Media Appeal/Voltage Reduction 
After the repeat, give TOs an update of system conditions, including chances of proceeding into an EEA 3. Notify TO’s which load shed table will be used in the event of EEA 3 load shed. [winter/summer] Firm Load Shed.

	Log
	Log all actions.


	Implement EEA Level 3

	Note
	ERCOT may declare an EEA Level 3 when the clock-minute average system frequency falls below 59.91 Hz for 20 consecutive minutes OR when steady-state frequency falls below 59.8 Hz for any duration of time.

	1


	ERCOT will declare an EEA Level 3 when PRC cannot be maintained above 1,500 MW or when the clock-minute average system frequency falls below 59.91 for 25 consecutive minutes.

Using the Hotline, notify the TOs to implement any measures associated with EEA 1 and 2, if not already implemented.

	2
	IF:

· PRC < 1500 MW and is not projected to be recovered above 1,500 MW within 30 minutes, or when the clock-minute average frequency falls below 59.91 Hz for 25 consecutive minutes;

THEN:

· Using the Hotline, notify the TOs to implement EEA 3 [winter/summer] Firm Load Shed and any measures associated with EEA 1 and 2, if not already implemented
· *Request deployment of Load Management Programs
* When available in EEA 2 if not already deployed, EEA 2 and EEA3 implements any available Load management plan to reduce Customer Load.

T#8 - Typical Hotline Script for EEA3 Firm Load Shed

	Log
	Log all actions.


7.4
Restore EEA Levels

Procedure Purpose:  To restore the ERCOT grid to normal state as system conditions warrant while recovering from an EEA event.

	Protocol Reference
	6.5.9.4(3)(g)
	6.5.9.4.3
	
	

	Guide Reference
	4.5.3.5
	
	
	

	NERC Standard
	
	
	
	


	Version: 2 
	Revision: 0
	Effective Date:  December 5, 2025


	Step
	Action

	Restore Firm Load

	RESERVES
	1500 MW of PRC must be restored within 90 minutes.

	1
	IF:

· Sufficient Regulation Service exist to control to 60 Hz, AND
· PRC – Regulation Up Responsibility is ≥ 1500 MW for the last 15 minutes;

THEN:

· Using the Hotline, notify the TOs of firm load restoration.

T#9 - Typical Hotline Script EEA3 Restore a Portion of the Firm Load 
OR

T#10 - Typical Hotline Script EEA3/BAAL Restore All Firm Load 

	Log
	Log all actions.

	Move from EEA Level 3 to EEA Level 2

	1
	IF:

· Sufficient Regulation Service exist to control to 60 Hz, AND
· PRC is ≥ 2000 MW, AND

· All firm load has been instructed to be restored;

THEN:

· Using the Hotline, notify the TOs of the reduction from EEA 3 to EEA 2:
· Notify the TOs that Load Resources are being restored 

T#11 - Typical Hotline Script to move from EEA3 to EEA2 

	Log
	Log all actions.

	Move from EEA Level 2 to EEA Level 1

	1
	IF:

· The System can maintain PRC ≥ 2500 MW AND
· All Load Resources have been instructed to be restored;

THEN:

· Using the Hotline, notify the TOs of the reduction from EEA 2 to EEA 1,

· If BLTs were implemented, restore

T#12 - Typical Hotline Script to move from EEA2 to EEA1

	Move from EEA Level 1 to EEA 0

	1
	IF:

· The System can maintain PRC ≥ 3000 MW, AND
· All RUC committed units secured in EEA can be released, AND
· Emergency energy from the DC Ties is no longer needed; 

THEN:

· Using the Hotline, notify the TOs of the termination of EEA.

T#13 - Typical Hotline Script Terminate EEA1

	Cancel Watch

	1
	WHEN:

· Requested by the Real-Time Desk Operator;
THEN:

· Cancel Watch
T#2 - Typical Hotline Script to cancel Watch for PRC <3000 MW


7.6
Hold
Procedure Purpose:  
	Protocol Reference
	
	
	
	

	Guide Reference
	
	
	
	

	NERC Standard
	
	
	
	


	Version: 2
	Revision:  0
	None


	Step
	Action


8.1
Hurricane or Tropical Storm

Procedure Purpose: To ensure TOs are prepared for an approaching 

Hurricane or Tropical Storm that could impact system reliability.

	Protocol Reference
	3.1.4.6
	6.3.2(3)(a)(ii)
	6.5.9.3.1
	6.5.9.3.2(3)

	
	6.5.9.3.4
	
	
	

	Guide Reference
	4.2.1
	4.2.2
	4.2.3
	4.2.4

	NERC Standard
	EOP-011-4

R1, R1.1, R1.2, R1.2.2, R1.2.6, R1.2.6.2, R2, R2.1, R2.2, R2.2.10, R2.2.10.2
	TOP-001-6

R8
	
	


	Version: 2 
	Revision: 0
	Effective Date:  December 5, 2025


	Step
	Action

	Note
	· Hurricane or Tropical Storm notifications can be called when there is a probability of landfall in the ERCOT Region (http://www.nhc.noaa.gov)

· The ERCOT Meteorologist may provide forecasts to supplement other Weather Service data information

· The sequence of actions taken, or notifications issued may vary due to system conditions or other operational issues and it may be necessary to skip actions due to the severity of the situation. To the extent possible, and when prudent, actions that were skipped may be implemented later

· Operations Support and Outage Coordination will analyze the situation and make recommendations as to Resource requirements and transmission topology 

	OCN
	When a Hurricane or Tropical Storm is developing and forecasted to impact the ERCOT Region, using the Hotline, issue an OCN to the TOs:

T#72 - Typical Hotline Script for OCN for Hurricane/Tropical Storm
Coordinate with Outage Coordination for the review of existing, planned, and future outages to be withdrawn/rejected and/or restored.

Coordinate with Operations Support as they may make recommendations on the situation based on the Resource requirements and transmission topology.

	Advisory
	When the probability of an approaching Hurricane or Tropical Storm impacting the ERCOT Region increases and concerns exist to escalate awareness, using the Hotline, issue an Advisory to the TOs:

T#73 - Typical Hotline Script for Advisory for Hurricane/Tropical Storm

	Watch
	When impacts from an approaching Hurricane or Tropical Storm is imminent and anticipated to have an adverse impact on the ERCOT Region, using the Hotline, issue a Watch to the TOs:

T#74 - Typical Script for Watch for Hurricane/Tropical Storm

	Emergency
	When a Hurricane or Tropical Storm is beginning to have an adverse impact on the ERCOT Region, using the Hotline, issue an Emergency Notice to the TOs:

T#75 - Typical Hotline Script for Emergency for Hurricane/Tropical Storm

	Post
	Coordinate with the Real-Time Desk and Resource Desk Operators for the posting of the notices on the ERCOT Website.

	Cancel

Posting
	Coordinate with the Real-Time Desk and Resource Desk Operators for the cancelation of the postings on the ERCOT Website.

	Log
	Log all actions.


8.2
Extreme Cold Weather

Procedure Purpose: To ensure TOs are prepared for extreme cold weather operations that could impact system reliability.

	Protocol Reference
	3.1.4.6
	6.3.2(3)(a)(ii)
	6.5.9.3.1
	6.5.9.3.2(4)

	
	6.5.9.3.4
	
	
	

	Guide Reference
	4.2.1
	4.2.2
	4.2.3
	4.2.4

	NERC Standard
	EOP-011-4

R1, R1.1, R1.2, R1.2.2, R1.2.6, R1.2.6.1, R1.2.6.2, R2, R2.1, R2.2, R2.2.10, R2.2.10.1, R2.2.10.2
	TOP-001-6

R8
	
	


	Version: 2 
	Revision: 0
	Effective Date:  December 5, 2025


	Step
	Action

	Note
	· Extreme cold weather notifications can be issued when temperatures are forecasted to be 25°F or below in the North Central and in the South-Central weather zones.  Wind chill also has an impact on how the temperature feels due to the flow of lower temperature air.  When the wind chill is forecasted to be 20°F or below in the North Central and in the South-Central weather zones, consider a notification.  This criterion has been developed for guidance when the temperature or wind chill are expected to be below freezing for several continuous hours which may abnormally impact load levels or generation availability

· For such events, additional reserves may be necessary

· The ERCOT Meteorologist may provide forecasts to supplement other Weather Service data information

· The sequence of actions taken, or notifications issued may vary due to system conditions or other operational issues and it may be necessary to skip actions due to the severity of the situation. To the extent possible, and when prudent, actions that were skipped may be implemented at a later time or date

	OCN
	When extreme cold weather is developing and forecasted to impact the ERCOT Region, using the Hotline issue an OCN to the TOs:

T#76 - Typical Hotline Script for OCN for Extreme Cold Weather
Coordinate with Outage Coordination for the review of existing, planned, and future outages to be withdrawn/rejected and/or restored.

Coordinate with Operations Support as they may make recommendations on the situation based on the Resource requirements and transmission topology.

	Advisory
	When the probability of extreme cold weather impacting the ERCOT Region increases and concerns exist to escalate awareness,  using the Hotline issue an Advisory to the TOs:

T#77 - Typical Hotline Script for Advisory for Extreme Cold Weather

	Watch
	When impacts from extreme cold weather is imminent and anticipated to have an adverse impact on the ERCOT Region,  using the Hotline issue a Watch to the TOs: 

T#78 - Typical Hotline Script for Watch for Extreme Cold Weather

	Emergency

Notice
	When extreme cold weather is beginning to have an adverse impact on the ERCOT Region, using the Hotline issue an Emergency Notice to the TOs:
T#79 - Typical Hotline Script for Emergency for Extreme Cold Weather

	Post
	Coordinate with the Real-Time Desk and the Resource Desk Operators for the posting of the notices on the ERCOT Website.

	Cancel

Posting
	Coordinate with the Real-Time Desk and the Resource Desk Operators for the cancelation of the postings on the ERCOT Website.

	Log
	Log all actions.


8.3
Extreme Hot Weather

Procedure Purpose: To ensure TOs are prepared for extreme hot weather operations that could impact system reliability.

	Protocol Reference
	3.1.4.6
	6.3.2(3)(a)(ii)
	6.5.9.3.1
	6.5.9.3.2(4)

	
	6.5.9.3.4
	
	
	

	Guide Reference
	4.2.1
	4.2.2
	4.2.3
	4.2.4

	NERC Standard
	EOP-011-4

R1, R1.1, R1.2, R1.2.2, R1.2.6, R1.2.6.2, R2, R2.1, R2.2, R2.2.10, R2.2.10.2
	TOP-001-6

R8
	
	


	Version: 2 
	Revision: 0
	Effective Date:  December 5, 2025


	Step
	Action

	Note
	· Extreme hot weather notifications can be issued when temperatures are forecasted to be 103°F or above in the North Central and South-Central weather zones. 

– OR – 

When temperatures are forecasted to be 94°F or above in the North Central and South-Central weather zones during the following months (October – May). 

· For such events, additional reserves may be necessary

· The ERCOT Meteorologist may provide forecasts to supplement other Weather Service data information.

· The sequence of actions taken, or notifications issued may vary due to system conditions or other operational issues and it may be necessary to skip actions due to the severity of the situation. To the extent possible, and when prudent, actions that were skipped may be implemented at a later time or date. 

	OCN
	When extreme hot weather is forecasted to impact the ERCOT Region,  using the Hotline issue an OCN to the TOs:

T#80 - Typical Hotline Script for OCN for Extreme Hot Weather

Coordinate with Outage Coordination for the review of existing, planned, and future outages to be withdrawn/rejected and/or restored.

Coordinate with Operations Support as they may make recommendations on the situation based on the Resource requirements and transmission topology.

	Advisory
	When the probability of extreme hot weather impacting the ERCOT Region increases and concerns exist to escalate awareness, using the Hotline issue an Advisory to the TOs:

T#81 - Typical Hotline Script for Advisory for Extreme Hot Weather

	Watch
	When impacts from extreme hot weather are imminent and anticipated to have an adverse impact on the ERCOT Region, using the Hotline issue a Watch to the TOs: 

T#82 - Typical Hotline Script for Watch Extreme Hot Weather


	Emergency

Notice
	When extreme hot weather is beginning to have an adverse impact on the ERCOT Region, using the Hotline issue an Emergency Notice to the TOs:
T#83 - Typical Hotline Script for Emergency for Extreme Hot Weather

	Post
	Coordinate with the Real-Time Desk and the Resource Desk Operators for the posting of the notices on the ERCOT Website.

	Cancel

Posting
	Coordinate with the Real-Time Desk and the Resource Desk Operators for the cancelation of the postings on the ERCOT Website.

	Log
	Log all actions.


8.4
Significant Weather Events

Procedure Purpose:  Monitor severe weather conditions for the ERCOT Region and regions outside of ERCOT which can arise with little or no warning that could potentially impact system reliability.
	Protocol Reference
	3.1.4.6
	6.3.2(3)(a)(ii)
	6.5.9.3.1
	6.5.9.3.2(4)

	
	6.5.9.3.4
	
	
	

	Guide Reference
	4.2.1
	4.2.2
	4.2.3
	4.2.4

	NERC Standard
	EOP-011-4

R1, R1.1, R1.2, R1.2.2, R1.2.6, R1.2.6.2, R2, R2.1, R2.2, R2.2.10, R2.2.10.1, R2.2.10.2
	TOP-001-6

R8
	
	


	Version: 2 
	Revision: 0
	Effective Date:  December 5, 2025


	Step
	Action

	Note
	· Significant weather events are those that do not meet the criteria of the extreme hot, extreme cold, hurricane, or tropical storm procedures

· Significant weather events can consist of, but are not limited to the following:

· Tornados

· Strong straight-line winds

· Flooding

· Freezing precipitation

· Wild Fires

· The ERCOT Meteorologist may provide forecasts to supplement other Weather Service data information.

· The sequence of actions taken, or notifications issued may vary due to system conditions or other operational issues and it may be necessary to skip actions due to the severity of the situation. To the extent possible, and when prudent, actions that were skipped may be implemented at a later time or date.

	OCN/

Advisory/

Watch
	When a significant weather event arises that could or does impact the ERCOT Region, using the Hotline, issue a notification to the TOs:

T#84 - Typical Hotline Script for OCN/Advisory/Watch for other Weather Events

	Note
	Coordinate with Outage Coordination, as needed, for the review of existing and planned outages to be withdrawn/rejected and/or restored.

Coordinate with Operations Support, as needed, as recommendations may be needed on the situation based on the Resource requirements and transmission topology.

	Post
	Coordinate with the Real-Time Desk and the Resource Desk Operators for the posting of the notices on the ERCOT Website.

	Cancel

Posting
	Coordinate with the Real-Time Desk and the Resource Desk Operators for the cancelation of the postings on the ERCOT Website.  

	Log
	Log all actions.


11.1
Loss of Primary Control Center Functionality

        Procedure Purpose: Provide instructions for responding to conditions that cause the primary control center to become inoperable or uninhabitable while continuing to meet its obligations with regard to the reliable operations of the ERCOT system and ensuring the safety of control center personnel.
	Protocol Reference
	
	
	
	

	Guide Reference
	
	
	
	

	NERC Standard
	EOP-008-2

R1, R1.2, R1.2.1, R1.4 R1.6, R1.6.1, R1.6.2, 1.6.3, R4
	TOP-001-5

R9
	
	


	Version: 2 
	Revision: 0
	Effective Date:  December 5, 2025


	Step
	Action

	Contact Security
	IF:

· Unable to reach any Operator at the PCC (also trying Alternative Interpersonal Communication capability);

THEN:

· Check the control center video camera to determine the status of the PCC and personnel,

· Contact Security at the ACC

· Notify them of the situation AND
· Have them attempt to make contact with Security at PCC.

· Have them contact you with information acquired OR
IF:

· Notified by the PCC that they are evacuating and/or transferring sites OR
· control center video and Security confirms evacuation;

THEN:

· Continue with procedure.  


	Step
	Action

	IROL
	Monitor and take actions on all IROL’s; the actual flow MUST NOT exceed its limit.  If necessary, the System Operator has the authority to direct load shedding before the IROL has been exceeded

	3-Part


	When issuing an Operating Instruction, follow three-part communication:

· Issue the Operating Instruction

· Receive a correct repeat back

· Give an acknowledgement

	Systems are Functional

	Call in Additional Operators
	Coordinate with the DC-Tie Desk Operator and activate the NXT scenario to call in additional shift personnel, which includes a Shift Supervisor. 

 SELECT:

· SO Loss of Control Room at Taylor, OR;

· SO Loss of Control Room at Bastrop.

An email will be received after 10 minutes with a report of who has responded along with their estimated time of arrival.

	TO

Hotline

Call
	T#91 - Typical Hotline Script Emergency Notice Loss of Primary Control Center (Systems are Functional)


	Additional Notifications
	The Director Control Room Operations and/or Designee will notify the following:

· Help Desk (to notify GMS Support and IT Infrastructure (Telecommunications and Data Center)

· Engineering Support

These phone numbers are also programmed into the control room cell phone.

	ERCOT Website
Posting
	As time permits, post the Emergency Notice on the ERCOT Website.

Typical Posting Script:
ERCOT has issued an Emergency Notice for the loss of the primary control center, all systems are functioning.

	Respond to TO’s
	Monitor frequency and re-run SCED/use (manual offset) as needed.

IF:

· TO’s call in with questions about operational timelines or non real-time issues;

THEN:

· Notify the TO’s that timelines and non real-time issues will be addressed when additional staff arrive,

· Document TO’s calls to pass along to the appropriate Operators as they arrive.

	Real-time Contingency Analysis (RTCA)
	Operations Support will assist in monitoring the RTCA functionality including results and may communicate suggested actions as needed.

	Respond to TOs Thermal/ Voltage Limits Reached (SOL)
	IF:

· Thermal limits have reached their continuous rating, OR

· Notified by Operations Support or a TO that thermal limits have reached their continuous rating; 

THEN:

· Activate associated constraint, OR

· Seek a recommendation from Operations Support or the appropriate TO as to what actions will alleviate the situation,

· Issue unit specific Operating Instructions as necessary to QSE.  (Follow-up with electronic Dispatch Instruction confirmation as time permits),

· Continue to monitor to determine the effect of the plan.
ERCOT Nominal Voltage Levels are 345kV, 230kV, 138kV, 115kV and 69kV.

The general voltage guidelines are as follows (listed in kV):

Nominal Voltage

Normal Operating Limits

Emergency Operating Limits

Ideal Voltage Range

345

327.75 – 362.25

310.5 – 379.5

345 – 359

230

218.5 – 241.5

207 – 253

230 – 240

138

131.1 – 144.9

124.2 – 151.8

138 – 144

115

109.25 – 120.75

103.5 – 126.5

115 – 120

69

65.55 – 72.45

62.1 – 75.9

69 – 71.5

Some TOs utilize different Normal (Basecase) and Emergency (Post-Contingency) voltage operating limits than the general voltage guidelines.  These limits can be seen under the Network Limits display.

WHEN:

· Indicated by SCADA alarms, OR

· Notified by Operations Support or a TO of voltage concerns;

THEN:

· Initiate a solution in collaboration with Operations Support and the appropriate TO and QSE in the area.

WHEN:

· TOs have utilized all Static Reactive Power Resources (capacitors, reactors, change in transformer taps) and a voltage issue still remains;

THEN:

· Instruct a QSE to raise or lower bus voltage, 

· The QSE should complete the requested in no more than five minutes. 

Typical Script:

“This is ERCOT Operator [first and last name].  At [xx:xx], ERCOT is instructing [QSE] to [raise or lower] voltage at [specify bus] by [+1 or 2kV or -1 or 2kV] for a target of [target kV].  [QSE] please repeat this instruction back to me.  That is correct, thank you.”

	GTCs
	IF:

· Any of the GTCs is approaching 85%, OR

·  Notified by Operations Support or a TO that a GTC (this includes the IROL) is approaching 85%;

THEN:

· Activate the associated “BASECASE” constraint in TCM

· Update RTMONI with new limit each time it changes

	Log
	Make log entry of events.

	Systems are not Functional

	NOTE
	Market Participants must be notified of unplanned outages of 30 minutes or more, of telemetering, monitoring and assessment capabilities, and associated communication channels between affected entities.

	Monitor Frequency
	The ability to view an adequate Frequency source may be limited during a site-failover, database load, or if AGC is temporarily unavailable.  To view the System Frequency during these conditions you may monitor the following sources.

· ERCOT control room digital wall frequency displays

· PI ProcessBook → ERCOT → TrueTime Frequency (Taylor) and/or

· PI ProcessBook → ERCOT → TrueTime Frequency (Bastrop)
It may be necessary to reload the PI ProcessBook “ERCOT Main Summary” display to show the historical data.

	Call in Additional Operators
	Coordinate with the DC-Tie Desk Operator and activate the activate the NXT scenario to call in additional shift personnel, which includes a Shift Supervisor. 

 SELECT:

· SO Loss of Control Room at Taylor, OR;

· SO Loss of Control Room at Bastrop.

An email will be received after 10 minutes with a report of who has responded along with their estimated time of arrival.

	TO

Hotline

Call
	· T#92 - Typical Hotline Script Emergency Notice Loss of Primary Control Center (Systems are NOT Functional)
· If either Hotlines are inoperable, phone numbers can be found on SharePoint under OPX & LD Numbers.

	ERCOT Website
Posting
	As time permits, post the Emergency Notice on the ERCOT Website.

· Typical Posting Script:
ERCOT has issued an Emergency Notice for the loss of the primary control center, systems are not functioning.

	Additional Notifications
	· The Director Control Room Operations and/or Designee will notify the following:

· Help Desk (to notify GMS Support and IT Infrastructure (Telecommunications and Data Center)

· Engineering Support

These phone numbers are also programmed into the control room cell phone.

	Real-time Contingency Analysis (RTCA)
	Operations Support will be responsible for the State Estimator and RTCA functionality and ensuring an RTA is performed at least every 30 minutes.  They will communicate results and any suggested actions as needed.

	Respond to TOs Thermal/ Voltage Limits Reached (SOL)
	IF:

· Notified by Operations Support or a TO that thermal limits have reached their continuous rating; 

THEN:

· Seek a recommendation from Operations Support or the appropriate TO as to what actions will alleviate the situation, and issue unit specific Operating Instructions to appropriate QSE. 

· Continue to monitor to determine the effect of the plan.

ERCOT Nominal Voltage Levels are 345kV, 230kV, 138kV, 115kV and 69kV.

The general voltage guidelines are as follows (listed in kV):

Nominal Voltage

Normal Operating Limits

Emergency Operating Limits

Ideal Voltage Range

345

327.75 – 362.25

310.5 – 379.5

345 – 359

230

218.5 – 241.5

207 – 253

230 – 240

138

131.1 – 144.9

124.2 – 151.8

138 – 144

115

109.25 – 120.75

103.5 – 126.5

115 – 120

69

65.55 – 72.45

62.1 – 75.9

69 – 71.5

Some TOs utilize different Normal (Basecase) and Emergency (Post-Contingency) voltage operating limits than the general voltage guidelines.  These limits can be seen under the Network Limits display.
WHEN:

· Notified by Operations Support or a TO of voltage concerns;

THEN:

· Initiate a solution in collaboration with Operations Support and the appropriate TO and QSE in the area.

WHEN:

· TOs have utilized all Static Reactive Power Resources (capacitors, reactors, change in transformer taps) and a voltage issue still remains;

THEN:

· Instruct the appropriate QSE to raise or lower bus voltage, 

· The QSE should complete the requested in no more than five minutes. 

Typical Script:

“This is ERCOT Operator [first and last name].  At [xx:xx], ERCOT is instructing [QSE] to [raise or lower] voltage at [specify bus] by [+1 or 2kV or -1 or 2kV] for a target of [target kV].  [QSE] please repeat this instruction back to me.  That is correct, thank you.”

	GTCs
	IF:

· Notified by Operations Support or a TO that a GTCs (which includes the IROL) is approaching 85% and is continuing to trend upward;

THEN:

· Seek a recommendation from Operations Support or the appropriate TO as to what actions will alleviate the situation,

· Issue unit specific Operating Instructions as necessary to QSE, (Follow-up with electronic Dispatch Instructions as time permits).

· Continue to monitor to determine the effect of the plan.

	Thermal Limits Reached (SOL)
	IF:

· Notified by Operations Support or a TO that thermal limits have reached their emergency rating and are continuing to trend upward, 

THEN:

· Seek a recommendation from Operations Support or the appropriate TO as to what actions will alleviate the situation, and issue unit specific Operating Instructions as necessary (Follow-up with electronic Dispatch Instruction as time permits)

· Continue to monitor to determine the effect of the plan.

	Electronic

Dispatch 

Instruction
	When issuing a VDI or confirmation, ensure the use of three-part communication:

· Issue the Operating Instruction

· Receive a correct repeat back

· Give an acknowledgement



	Log
	Log all actions.


Document Control

Manual Change History

	Procedure
	Ver/

Rev
	Reason for Issue
	Effective Date

	All Sections
	2.0 / 0
	RTC+B Implementation 

All procedures in this manual have been reviewed
	December 5, 2025


