	ERCOT Operating Procedure Manual

	Resource Desk


	ERCOT Operating Procedure Manual

	Resource Desk



Power Operations Bulletin # 2018
ERCOT has posted/revised the Resource Desk manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html
3.11
Unannounced ESR Non-Spin Capability Testing

Procedure Purpose: This procedure provides direction and guidelines for conducting unannounced ESR testing.

	Protocol Reference
	8.1.1.2(19)
	
	
	

	Guide Reference
	
	
	
	

	NERC Standard
	
	
	
	


	Version: 2 
	Revision: 1
	Effective Date:  February 27, 2026


	Step
	Action

	Unannounced ESR Non-Spin Capability Test

	Note
	If an Energy Storage Resource (ESR) is telemetering a non-zero Non-Spin Ancillary Service Resource Responsibility, to verify that the Ancillary Service Resource Responsibility reported by telemetry is achievable based on the state of charge the Resource is maintaining in Real-Time, ERCOT may, at its discretion, conduct an unannounced Non-Spin capability test. At a time determined solely by ERCOT.

	1
	WHEN:

· ESR has a Non-Spin Responsibly and has a negative Status of Charge (SOC) Deviation: AND

· At the Operators discretion

THEN:
· Perform an Unannounced ESR Non-Spin Capability Test

	2
	ISSUE an instruction to the QSE for the ESR being tested.  

Q#132 - Typical script to Perform Unannounced ESR Non-Spin Capability Test:
Q#133 - Typical script to End Unannounced ESR Non-Spin Capability Test:
COMPLETE the ERCOT values on the Unannounced ESR  Non-Spin Capability Test via the NDCRC application on the ERCOT Website in a reasonable timeframe.

ERCOT Website>Applications>NDCRC>Unannounced Seasonal>Unannounced ESR AS Capability

	Electronic

Dispatch

Instruction

Confirmation
	ISSUE: 

· Electronic Dispatch Instruction confirmation to QSE (see Desktop Guide Common to Multiple Desks Section 2.3)

· Choose “OTHER FOR RESOURCE” as the Instruction Type from Resource level

· Choose “Other” as Reason

· Initiation Time and Completion Time should be correct times

· In Other Information, state “Unannounced ERS Non-Spin Capability Test ” 

· Confirm with Market Participant electronic Dispatch Instruction received.

When issuing a VDI or confirmation, ensure the use of three-part communication:

· Issue the Operating Instruction

· Receive a correct repeat back

· Give an acknowledgement

	Retest
	· The QSE can have the opportunity to request another test as quickly as possible (at a time determined by ERCOT) and may request a retest up to two times per month

·  QSEs should submit retest requests to shiftsupv@ercot.com.  

· Any requested retest must take place within three Business Days after the request for retest

· Any VDI issued as a result of a QSE-requested retest will be considered as an instructed deviation only for compliance purposes
ISSUE: 

· Electronic Dispatch Instruction confirmation to QSE (see Desktop Guide Common to Multiple Desks Section 2.3)

· Choose “OTHER FOR RESOURCE” as the Instruction Type from Resource level

· Choose “Other” as Reason

· Initiation Time and Completion Time should be correct times

· In Other Information, state “Unannounced ERS Non-Spin Capability RETEST ” 

· Confirm with Market Participant electronic Dispatch Instruction received.

When issuing a VDI or confirmation, ensure the use of three-part communication:

· Issue the Operating Instruction

· Receive a correct repeat back

Give an acknowledgement

	Notify
	When test is complete, include the following information:

· Resource(s) 

· Date

· Notification Time

· Completion Time

Send an e-mail to:

· Operations Analysis

· Shift Supervisor

	Log
	Log all actions.


Document Control

Manual Change History

	Procedure
	Ver/Rev
	Reason for Issue
	Effective Date

	All Sections
	2.0 / 0
	RTC+B Implementation 

All procedures in this manual have been reviewed
	December 5, 2025

	3.6
	2.0 / 1
	Added Transmission Constraint Deployment
	January 30, 2026

	3.11
	2.0 / 1
	Updated the Procedure Purpose
	February 27, 2026



