	ERCOT Operating Procedure Manual

	Shift Supervisor Desk



Power Operations Bulletin # 2019
ERCOT has posted/revised the Shift Supervisor Desk manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html
3.2
Capacity and Reserve Monitoring

Procedure Purpose:  To monitor capacity for SCED dispatch and total system capacity for providing Ancillary Services.

	Protocol Reference
	3.1.6.9(8)
	6.5.9.1(1)(a)
	6.5.7.6.2.3(1)
	

	Guide Reference
	2.2.1(3)(a)
	
	
	

	NERC Standard
	EOP-011-4 R2, R2.1
	
	
	


	Version: 2 
	Revision: 1
	Effective Date:  February 27, 2026


	Step
	Action

	Capacity Monitoring

	1
	Monitor the PUCT lookahead Margin:

IF:

· Load forecast is reasonable AND “Committed Capacity Margin” shows < 6,500MW Committed Capacity Margin;

THEN:

· Verify that HRUC has identified the insufficient capacity situation. 

	2
	Monitor the 7-Day Load and Capacity Outlook:

IF:

· Load forecast is reasonable AND Load Forecast exceeds Committed Capacity;

THEN:

· Verify that HRUC has identified the insufficient capacity situation.

	3
	IF:

· HRUC has not identified the insufficient capacity;

THEN:

· Discuss with the RUC Desk Operator and verify that HRUC is using a reasonable forecast AND update if necessary,

· Ensure Resource commitments are being made, if needed. 

	4
	Triggers to deploy Non-Spin

MONITOR:

The Generation Area Status Page and the Non-Spin Deployment Trigger display

WHEN:

· PRC < 3200 MW and not expected to recover within 30 minutes without deploying reserves

THEN:

· Verify that the Resource Desk Operator has deployed a group(s) or all of the available Non-Spin capacity.
IF:

· Projected Ramp Available in 30min < -300; 

THEN:

· Verify that the Resource Desk Operator has deployed half of the available groups of Non-Spin.

IF:

· Projected Ramp Available in 30min < -600, OR

· PRC is < 3000 MW; 

THEN:

· Verify that the Resource Operator has deployed the available groups of Non-Spin, as needed.

IF:

· Additional capacity is required, 

THEN:
· Verify the RUC Desk Operator is aware of the requirement to RUC commit additional Resources for the next hour.

	5
	During periods of low load and excess generation:

PERIODICALLY REVIEW:

· Splunk Dashboard Viewer under the MOS_Dev folder:

· “Last Approved HRUC Capacity” which is based on the last ran HRUC solution

IF:

· Load forecast is reasonable AND the decision needs to be made in the near future,

THEN:

· Decommit generation from the HRUC next study,

· Priority should be on Resources that resolve congestion;

IF:

· The decision needs to be made immediately,

THEN:

· Request RUC Desk Operator to issue electronic Dispatch Instruction confirmation.

	Log
	Log all actions.

	Large Load Curtailment Program

	ERCOT Large Load Curtailment Requested
	WHEN:

· PRC < 3200 MW and not expected to recover within 30 minutes without deploying reserves AND;

· All Non-Spin has been deployed AND;

· Available ERCOT Large Load Voluntary Curtailment Program Participants
THEN:
· Initiate X-Matters notification to all ERCOT Large Load Voluntary Curtailment Program Participants ERCOT is requesting to curtail consumption OR:
· Request Director Control Room Operations and/or Designee to make notification.
· Ensure Real Time Desk, Resource Desk, and Transmission & Security Desk make postings and Hotline Call Notifications.

	ERCOT Large Load Curtailment Request Ended
	WHEN:

· ERCOT Large Load Voluntary Curtailment Program Participants are no longer needed
THEN:
· Initiate X-Matters notification to all ERCOT Large Load Voluntary Curtailment Program Participants that request to curtail consumption ended OR:
· Request Director Control Room Operations and/or Designee to make notification.
· Ensure Real Time Desk, Resource Desk, and Transmission & Security Desk make postings and Hotline Call Notifications.

	Log
	Log all actions.

	Advance Action Notice (AAN)

	Definition
	An Advance Action Notice (AAN) is a type of Operating Condition Notice (OCN) that identifies a possible future Emergency Condition and describes future action ERCOT expects to take to address that condition unless the need for ERCOT action is alleviated by Qualified Scheduling Entity (QSE) and/or Transmission Service Provider (TSP) actions or by other system developments

	Note
	ERCOT may issue an (AAN) in anticipation of a possible Emergency Condition.  Any AAN will identify actions ERCOT expects to take to address the possible Emergency Condition unless the need for ERCOT action is alleviated by QSE and/or TSP actions taken, or by other system developments that occur, before a time stated in the AAN.

	Time Periods
	ERCOT shall issue the AAN a minimum of 24 hours prior to performing an Outage Adjustment Evaluation (OAE).  Additionally, unless impracticable, the OAE should not be performed until eight Business Hours have elapsed following issuance of the AAN.  ERCOT shall not issue an Outage Scheduler Adjustment (OSA) under this section unless it has first completed an OAE.

	1
	IF:

· While reviewing the 7-Day Load and Capacity Outlook or when notified by System Operations Management, Outage Coordination Management or Operations Support Management, ERCOT forecasts an inability to meet applicable transmission reliability standards and has exercised all other reasonable options AND;

· There are Resources with approved or accepted Resource Outages, whose approval or acceptance could be withdrawn to meet the applicable transmission reliability standards

THEN:

· In coordination with System Operations Management, Outage Coordination Management and Operations Support Management, issue an Advance Action Notice (AAN)

	2
	As conditions change, ERCOT shall, to the extent practicable, update the AAN in order to provide simultaneous notice to Market Participants.
IF:

· Conditions change;

THEN:

· In coordination with System Operations Management, Outage Coordination Management and Operations Support Management. Update the AAN.

	3
	IF:
· Planned Resource Outages which can feasibly be returned to service;

THEN:

· In coordination with System Operations Management, Outage Coordination Management and Operations Support Management. Instruct QSEs to restore Planned Resource Outages which can feasibly be returned to service.

	4
	IF:
· In coordination with System Operations Management, Outage Coordination Management and Operations Support Management, the OSA process has executed.  

THEN:

· Notify QSEs of executing the OSA process

	5
	WHEN:
· ERCOT determines that the possible Emergency Condition has been alleviated by QSE or TSP action, by ERCOT action, or by other system developments;
THEN:

· In coordination with System Operations Management, Outage Coordination Management and Operations Support Management, cancel the Advance Action Notice (AAN) AND;

· Cancel ERCOT Website message(s).

	Log
	Log all actions.


Manual Change History

	Procedure
	Ver/Rev
	Reason for Issue
	Effective Date

	All Sections
	2.0 / 0
	RTC+B Implementation

All procedures in this manual have been reviewed
	December 5, 2025

	3.6
	2.0 / 1
	Updated Log Instructions for IROLs 
	January 30, 2026

	3.2
	2.0 / 1
	Updated Non-Spin deployment trigger
	February 27, 2026


