	ERCOT Operating Procedure Manual

	Real Time Desk



Power Operations Bulletin # 2021
ERCOT has posted/revised the Real Time manual.

The Various Changes are shown below.
A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html
3.1
Frequency Control Operating Procedure

Procedure Purpose: To control frequency within defined limits.
	Protocol Reference
	6.5.7.6.2.2(7),

(16)
	6.5.9.1(1)(b)
	
	

	Guide Reference
	2.2.4
	2.2.8
	2.3.1.2
	4.8.1

	NERC Standard
	BAL-001-2

R2
	BAL-002-3

R1, R1.1, R1.3, R3
	IRO-001-4

R1
	NUC-001-4

R4, R4.1, R4.2, R9, R9.2, R9.2.1, R9.4, R9.4.1, R9.4.2

	
	TOP-001-5 R2, R11
	
	
	


	Version: 2 
	Revision: 1
	Effective Date: April 1, 2026


	Step
	Action

	Maintain System Frequency

	Objective
	· Frequency should be maintained within +/- 0.03 Hz of schedule

· Attempt to maintain CPS1 scores over 100

· Operate within the BAAL 

· Frequency Bias Setting set to 895 MW/0.1Hz

	CPS1 less than 100
	IF:

· Performance drops below 100 for over three consecutive hours;
THEN:

· LOG the event and the possible cause of the poor performance.

	BAAL
	Corrective action shall be taken whenever the clock-minute average ACE is outside its clock-minute average Balancing Authority ACE Limit (BAAL). This is to ensure that the Balancing Authority ACE does not remain outside the BAAL for more than 30 consecutive clock-minutes.  

	Caution
	NEVER (unless directed by GMS Support or Support Engineer): 

· Change other tuning parameters (including QSE Ramp Rates, dead bands, thresholds, gains, time constraints)

	Base Point

Deviation
	REVIEW REFERENCE DISPLAY:

EMP Applications>Generation Area Status>Related Displays>Expected Generation and Load Details

Not-Tracking Units tab

IF:

· A QSE has a Resource with a large Set Point deviation (not tracking unit flag), AND

· Their generation is not moving in the proper direction to correct their Set Point Deviation;

THEN:

· Notify the QSE of the issue.

	Frequency Deviations


	IF:

· Frequency deviations are equal to or greater than +/- 0.10 Hz, OR

· Sudden loss of generation greater than 450 MW;

THEN:

· Ensure frequency recovers to pre-disturbance within 15 minutes

· Manually run SCED or use offset as needed.
LOG:

· Log the following information:

· Possible reasons, if known (Set Point deviation, large schedule change, unit trip, DC-Tie trip, etc.)

· If unit trip:

· Time of unit trip or DC-Tie,

· Name of unit or DC-Tie,

· Approximate net MW,

· Approximate lowest TrueTime frequency (use 3 decimals), AND

· Approximate ERCOT load.

	Hydro
Generation Operating in Synchronous Condenser Fast Response Mode
	IF:
· Hydro Resources operating in synchronous condenser fast-response mode who provide MW to the System in response to a frequency event without ONSC deployment trigger;

THEN:

· QSE will request an electronic Dispatch Instruction confirmation 

· Choose Resource tab

· Choose requesting QSE for Participant Name 

· Choose Resource name

· Enter MW amount deployed in Current Operating Level

· Choose Other For Resource for Instruction Type

· State Hydro deployed in response to frequency in Other Information

· Initiation Time, and 

· Completion Time

When issuing a VDI or the confirmation, ensure the use of three-part communication:

· Issue the Operating Instruction

· Receive a correct repeat back

· Give an acknowledgement

· An electronic Dispatch Instruction confirmation will be needed for each Resource. 

IF:

· QSE contacts ERCOT to determine if it is allowed to recall and reset;

THEN:

· ERCOT grants approval to come off-line once the frequency recovers to pre-disturbance level or 60 Hz, whichever is lower, OR

· Request QSE to remain On-line

· May not exceed 30 minutes per release for each frequency deviation or event

· Shall not exceed two hours per a 12-hour period in aggregate unless an EEA is declared 

	Response to High Frequency

	BAAL

Sheet
	Located on the realtime drive in the _Operations Official Spreadsheets folder.  Open BAAL ERCOT Interconnection and select Control T simultaneously.

	Monitor
	IF:

· Frequency goes above 60.05 Hz and exceeds 60.05  Hz > 5 minutes AND

· Regulation Down service remains and is deploying;

THEN:

· Manually run SCED

· Call QSEs with Resources that have positive Set Point deviations and issue an Operating Instruction to bring their Set Point deviations to zero.

IF:

· Frequency goes above 60.05 Hz, AND

· Out of Down Regulation;

THEN:

· CHECK the GEN-LDL or Cap to decrease BP on the EMS to ensure there is adequate down room,

· Manually run SCED.

IF:

· There is no generation left for SCED to lower;
THEN:

· Coordinate with the Shift Supervisor and Transmission and Security Desk Operator to select a Resource to RUC decommit,

· Request the RUC Desk Operator to issue an Operating Instruction to RUC decommit Resource.

	10

Minutes
	REFERENCE DISPLAY: EMP Applications>Generation Unit Status>Related Displays>Expected Generation and Load Details>Top Ten button AND Market Operation>Real-Time Market>SCED Displays>DSI Displays>DSI Data Processes>DSI Generation Requirement Manual Adjustment

IF:

· 10 consecutive minutes of ACE above BAALHigh (60.09 Hz); 
THEN:

· Call QSEs with Resources that have positive Set Point deviations and issue an Operating Instruction to bring their Set Point deviations to zero,

· Verify SCEDs capacity to decrease Set Points GEN-LDL,

· Enter manual offset,

· Manually run SCED (do not run SCED more than once between SCED runs).

	Notify
	If it is recognized that Frequency is or expected to be outside +/- 0.1 Hz for a non-transient event and will not recover within 15 minutes, notify the Nuclear Power Plants QSEs.

	15

Minutes
	IF:

· 15 consecutive minutes of ACE above BAALHigh (60.09 Hz); 
THEN:

· Call QSEs with Resources that have positive Set Point deviations and issue an Operating Instruction to bring their Set Point deviations to zero,

· Verify SCEDs capacity to decrease Set Points GEN-LDL,

· Re-adjust manual offset,

· Manually run SCED,

· Log the event and notify Operations Support Engineer to send an event notification to OperationsAnalysis@ercot.com.

IF:

· There is no generation left for SCED to lower;
THEN:

· Coordinate with the Shift Supervisor and Transmission and Security Desk Operator to select a Resource to RUC decommit,

· Request the RUC Desk Operator to issue Operating Instruction to RUC decommit Resource.

	20

Minutes
	IF:

· 20 consecutive minutes of ACE above BAALHigh (60.09 Hz) and Frequency is above 60.10 Hz; 
THEN:

· Call QSEs with Resources that have positive Set Point deviations and issue an Operating Instruction to bring their Set Point deviations to zero

· Curtail appropriate amount of DC-Tie imports (issue an Emergency),

· Coordinate with the Shift Supervisor and Transmission and Security Desk Operator to select an additional Resource to RUC decommit,

· Request the RUC Desk Operator to issue Operating Instruction to RUC decommit Resource.

	25

Minutes
	IF:

· 25 consecutive minutes of ACE above BAALHigh (60.09 Hz) and Frequency is above 60.10 Hz; 
THEN:

· Call QSEs with Resources with positive Set Point deviations and issue an Operating Instruction to take their Resource off-line.

· Coordinate with Shift Supervisor and Transmission and Security Desk Operator to select an additional Resource to RUC decommit,

· Request the RUC Desk Operator to issue Operating Instruction to RUC decommit Resource.

	Stable
	IF:

· A manual offset was used; 

THEN:

· Ensure that it has been removed.

	Log
	Log all actions. 

	Response to Low Frequency 

	BAAL

Sheet
	Located on the realtime drive in the _Operations Official Spreadsheets folder.  Open BAAL ERCOT Interconnection and select Control T simultaneously.

	Note
	Responsive Reserve Service

· Primary Frequency Response (RRS-PFR)

· Fast Frequency Response (RRS-FFR)
· Units (ESRs)

· Controllable Load Resource (CLR)

· Non-Controllable Load Resource (NCLR)
· Under Frequency Response (RRS-UFR)

	Note
	The minimum capacity required from Gen Resources providing RRS using Primary Frequency Response shall not be less than 1,150 MW.

	Note
	UFRs will deploy as follows:

· Fast Frequency Response (FFR) – 59.85 Hz

· Hydro Resources in Synchronous Condenser mode (ONSC) providing RRS and ECRS  - 59.80 Hz

· Load Resource providing RRS, Load Resources providing ECRS with relay armed – 59.70 Hz

	Note
	Manually deploy Load Resources other than Controllable Load Resources providing ECRS or RRS before entering an Energy Emergency Alert (EEA), to maintain a minimum 500 MWs of Physical Responsive Capability (PRC) reserves on dispatchable Resources. Deployments will be made per Resource Desk Operating Procedure section 3.8 order starts with Group 0 Resources, and then next higher order group.

	Monitor/ Release
	IF:

· Frequency drops below 59.95 Hz, AND
· Regulation Up service remains and is deploying;
THEN:

· Manually run SCED (do not run SCED more than once between SCED runs)

· Call QSEs with Resources with negative Set Point deviations and issue an Operating Instruction to bring their Set Point deviations to zero.

IF:

· Frequency drops below 59.95 Hz, AND

· Out of Up Regulation;

THEN:

· Check the HDL-Gen on the EMS and enter appropriate manual offset (the offset will continue until removed).  Do not commit a manual offset while SCED is running.

· In EMS, do not enter an offset > than HDL-Gen

· Repeat as needed to recover the frequency

· 

	10

Minutes
	REFERENCE DISPLAY:

EMP Applications>Generation Unit Status>Related Displays>Expected Generation and Load Details>Top Ten button AND

Market Operation>Real-Time Market>SCED Displays>DSI Displays>DSI Data Processes>DSI Generation Requirement Manual Adjustment 

IF:

· 10 consecutive minutes of ACE is less than BAALLow (59.91 Hz);
THEN:

· Call QSEs with Resources with negative Set Point deviations and issue an Operating Instruction to bring their Set Point deviations to zero,

· Verify SCEDs capacity to increase Set Points,

· Enter manual offset 

· If room is available

· Manually run SCED

IF:

· There is no generation left for SCED to increase;
THEN:

· Coordinate with the Shift Supervisor and Resource Desk Operator to deploy any available Non-Spin,

· Manually release ONSC ECRS and ONSC RRS from Hydro Resources operating in Synchronous Condenser Fast Response Mode using the ERCOT Nodal Summary display on the EMS

· Check the box labeled “Activate Manual ONSC-ECRS” to activate, 

· Check the box labeled “Activate Manual ONSC-RRS” to activate

· Remember to remove the manual ONSC-ECRS and ONSC-RRS amount when frequency has recovered.

· Notify the Shift Supervisor of the need to possibly RUC commit additional Resources.

	Note
	ERCOT may declare an EEA Level 2 when the clock-minute average system frequency falls below 59.91 Hz for 15 consecutive minutes.

	Notify
	If it is recognized that the Frequency is or expected to be outside +/- 0.1 Hz for a non-transient event and will not recover within 15 minutes, notify the Nuclear Power Plants QSEs.

	15

Minutes
	IF:

· 15 consecutive minutes of ACE less than BAALLow (59.91 Hz ); 
THEN:

· ERCOT MAY immediately implement EEA Level 2 when clock-minute average system frequency falls below 59.91 Hz for 15 consecutive minutes
· Curtail appropriate amount of DC-Tie export (issue an Emergency)

· Coordinate with the Resource Desk Operator to manually deploy Load Resources providing ECRS or RRS. 

· Coordinate with the Resource Desk Operator to manually deploy RRS-FFR (NCLR), if available

· Call QSEs with Resources that have negative Set Point deviations and issue an Operating Instruction to bring their Set Point deviations to zero

· Verify SCEDs capacity to increase Set Points (HDL-GEN),

· Re-adjust manual offset

·  If room is available

· Manually run SCED

· Monitor ECRS and RRS Load Resource deployments

· Log the event and notify Operations Support Engineer to send notification of the event to OperationsAnalysis@ercot.com.

	Note:
	Coordinate with Resource desk to deploy ERS Resources.

	Load

Resources
	Q#8 - Typical Hotline Script for EEA2

	20

Minutes
	IF:

· 20 consecutive minutes of ACE less than BAALLow (59.91 Hz);
THEN:

· ERCOT MAY immediately implement EEA Level 3 any time the clock-minute average system frequency falls below 59.91 Hz for 20 consecutive minutes OR when steady-state frequency falls below 59.8 Hz for any duration of time.  
· Call QSEs with Resources that have negative Set Point deviations and issue an Operating Instruction to bring their Set Point deviations to zero,

· Verify SCEDs capacity to increase Set Points (HDL-GEN),

· If room is available, re-adjust manual offset,

· Manually run SCED,

· Monitor ECRS and RRS Load Resource deployments.

· Consider manually releasing RRS-FFR from SCED dispatchable Resources, if available using the ERCOT Nodal Summary display on the EMS. Note RRS-FFR from SCED dispatchable Resources should be preserved for 59.85 event to the extent possible.

· Check the box labeled “Activate Manual FFR” to activate, 

· Remember to remove the manual FFR amount when frequency has recovered.

· Make Hotline call to QSE’s

RRS-FFR released MW to Resources is allocated based on the RRS-FFR Awards from both units and CLR’s.

	25

Minutes
	IF:

· 25 consecutive minutes of ACE less than BAALLow (59.91 Hz ); 
THEN:

· Implement EEA Level 3

· EEA3 Unable to Maintain 59.91 Hz or PRC <1500 MW
· Verify SCEDs capacity to increase Set Points,

· Re-adjusted manual offset,

· Do Not enter an offset > than (HDL-GEN)

· Manually run SCED as needed,

· Monitor ECRS and RRS Load Resource deployments,

· Monitor DC-tie curtailments,

· Coordinate with the Transmission and Security Desk Operator to shed an appropriate amount of firm load.

· Make Hotline call to QSE’s

Q#11 EEA3 With Firm Load Shed

	Stable
	IF:

· Firm load was shed;
THEN:

· Coordinate with the Transmission and Security Desk Operator to restore firm load.

· Make Hotline call to QSE’s

Q#13 Restoring Firm Load

IF:

· ONSC-ECRS and ONSC-RRS was manually released; 

THEN:

· Uncheck the Activate Manual ONSC-ECRS,

· Uncheck the Activate Manual ONSC-RRS 

IF:

· RRS-FFR was manually released; 

THEN:

· Uncheck the Activate Manual FFR Responsive Reserve,

· Notify the Resource Desk Operator to recall FFR NCLR, if deployed.

IF:

· Load Resources providing ECRS or RRS were manually deployed; 

THEN:
· Recall Load Resources providing ECRS or RRS.

IF:

· A manual offset was used; 

THEN:

· Ensure that it has been removed.
IF:

· Non-Spin was deployed; 

THEN:

· Recall the Non-Spin.

	Log
	Log all actions.

	Monitor Frequency for the Loss of EMS or Site Failover

	
	The ability to view an adequate Frequency source may be limited during a site-failover, database load, or if AGC is temporarily unavailable.  To view the System Frequency during these conditions you may monitor the following sources.

· ERCOT Control Room VORNE digital wall frequency displays

· PI Process Book → ERCOT → TrueTime Frequency (Taylor) and/or

· PI ProcessBook → ERCOT → TrueTime Frequency (Bastrop)
It may be necessary to reload the PI ProcessBook “ERCOT Main Summary” display to show the historical data.

	Actions When Frequency Telemetry is Incorrect

	
	REVIEW REFERENCE DISPLAY:

EMP Applications>Generation Control>Generation Area Status>Current Frequency Deviation from Nominal

IF:

· Frequency is believed to be incorrect;

THEN:

· Check the current Frequency and switch to a different source,

·  Select Skip on the incorrect Frequency device,

· Contact the Service Desk.


4.1
Managing SCED

Procedure Purpose: To ensure that a SCED solution has solved, and that the solution is reasonable.  
	Protocol Reference
	3.8.3
	3.9.1(10)
	3.10.7.5.1(5)
	8.1.1.2(16)

	Guide Reference
	7.3.3
	
	
	

	NERC Standard
	TOP-003-5

R5, R5.2
	TOP-010-1(i) 

R1, R1.3, R2, R2.3
	
	


	Version: 2 
	Revision: 1
	Effective Date: April 1, 2026


	Step
	Action

	Workflow Controller Messages

	Note
	The SCED Workflow Controller provides three color coded messages as indicated in the following:

· GREEN – Informational (i) and Success (s)

· BLUE – Warning (w)

· RED – Error (e) and Fatal Error (f)

	1
	REVIEW REFERENCE DISPLAY:

Market Operation>Real-Time Market>SCED Displays>Workflow>SCED Workflow Messages

Monitor SCED Workflow Controller logs for “Warning” and “Error” messages.

	2
	IF:

· The log indicates an “Error” or “Fatal Error”;

THEN:

· Contact the Service Desk and notify the Control Room staff,

· Attempt to resolve the issue, refer to Desktop Guide Real Time Desk Section 2.5,

· Refer to Section 3.3 “Managing SCED Failures” in this procedure.

	SCED Solution Time Parameter 

	Note
	Typically, SCED should produce a solution within 20 seconds.  It is highly desirable to have at least 3 executions of SCED in any 15-minute period.

	Automatic

Trigger
	Verify that SCED is automatically triggered:

· Periodically every 5 minutes

· About 60 seconds after frequency declined below 59.91 Hz 

· About 60 seconds after Fast Responding Synchronous Condenser Resources providing ONSC-ECRS or ONSC-RRS and SCED dispatchable resources providing RRS-FFR have been deployed automatically or manually

· Frequency is < 59.955 Hz for > two consecutive minutes
IF:

· SCED is not automatically executed (but has not failed);

THEN:

· Manually execute SCED,

· Immediately notify the Shift Supervisor and Operations Support Engineer,

· Continue to manually execute SCED approximately every 5 minutes until the condition is corrected.

	Manual

Trigger
	SCED may be manually triggered when the following is identified:

· Frequency deviates  +/-0.05 Hz for more than 5 minutes

· Generation Resource trips and Frequency is > 59.91 Hz

· When approximately 50% of Regulation has been deployed

· Approximately 60 seconds after Fast Responding Resources providing ONSC-ECRS or ONSC-RRS and SCED dispatchable resources providing RRS-FFR have been deployed.

· After Load Resources providing ECRS or RRS have been deployed.

· As needed to recover frequency

	Log
	Log all actions.

	Quick Start Generation Resource

	QSGR
	A Generation Resource that in its cold-temperature state can come On-Line within ten minutes of receiving ERCOT notice and has passed an ERCOT Quick Start Generation Resource test that establishes an amount of capacity that can be deployed within a ten-minute period.  

· These Resources can be viewed in EMS: Generation Area Status > Analyst Displays > Quick Start Units

	COP
	The QSE for a QSGR that is available for deployment by SCED and awarding of ECRS and Non-Spin, if qualified and capable, shall set the COP Resource Status OFFQS, the COP LSL and HSL values to the expected sustainable LSL and HSL for the QSGR for the hour.  

	Telemeter
	The QSGR that is available to be released by SCED and awarded ECRS and Non-Spin, if qualified and capable, shall telemeter a Resource Status of OFFQS and an LSL of zero prior to receiving a release instruction from SCED.  This status is necessary for SCED to recognize that the Resource can be Dispatched and/or awarded ECRS and Non-Spin.  The status of the breaker shall be open, and the output of the Resource shall be zero in order for the State Estimator to correctly assess the state of the system.  After being released for energy by SCED, the Resource shall telemeter an LSL equal to or less than the Resource’s actual output until the Resource has Ramped to its physical LSL.  A QSGR with a telemeter breaker status of open and a telemeter Resource Status of OFFQS shall not provide Regulation or Responsive Reserve Service.

	QSGR

Decommitment
	Please refer to Desktop Guide Common to Multiple Desks for the QSGR decommitment process.

	QSGR

Qualification

Test
	WHEN:

· Conducting a QSGR qualification test for Operations Analysis;

THEN:

· Issue a VDI confirmation

· Choose “OTHER_RES” as the Instruction Type from Resource level

· Enter MW amount that the QSE is requesting to qualify its QSGR to provide.  

· Enter “QSGR Qualification Test” in “Other Information”

· . 

When issuing a VDI or the confirmation ensure the use of three-part communication:

· Issue the Operating Instruction

· Receive a correct repeat back

·  Give an acknowledgement

	Generation Resource Shut-down/Start-up Process

	Shutdown/

Startup
	Shut-down:

· A QSE representing a Generation Resource that is not actively providing A/S (except for Off-line Non-Spin) may only use a Resource Status of SHUTDOWN through telemetry that the Resource is operating in a shutdown sequence requiring manual control and is not available for Dispatch.

Start-up:

· A QSE representing a Generation Resource that is not actively providing A/S may only use a Resource Status of STARTUP through telemetry that the Resource is operating in a start-up sequence requiring manual control and is not available for Dispatch.

	Note
	QSEs can manage basepoint deviations by adjusting their telemetered Ramp Rate.

	Note
	When a Resource is carrying “Off-Line” Non-spin and that Non-Spin is being recalled, the QSE would continue to show the Non-Spin responsibility on the Resource that is shutting down.

	Combine Cycle Generation Resources

	Note
	WHEN:

· Combine Cycle Generation Resources are changing configuration creating basepoint deviations

THEN:
· QSEs will need to manage their telemetered HSL for proper basepoints.

	Real-Time Data Issues known by the QSE

	Note
	Manually replaced telemetry data is data entered by a QSE on their systems that is transmitted to ERCOT via ICCP in place of the normal points experiencing an issue.  If Reliability issues can’t be resolved in a timely manner, ERCOT reserves the right to order the Resource off-line until the problem is resolved.   

	Notification of Telemetry 

Data

Issue
	IF:

· Notified of a telemetry data issue (telemetry data will not be available or is unreliable for operational purposes;

THEN:
· The QSE should correct of the telemetry data as soon as practicable, or,

· Manually replace the data, if available.

	Cannot

Resolve
	IF:

· The QSE cannot resolve the telemetry data issue within two Business Day, fix the issue in a timely manner;

THEN:

· The QSE shall provide an estimated time of resolution.


Document Control

Manual Change History

	Procedure
	Ver/Rev
	Reason for Issue
	Effective Date

	All Sections
	2.0 / 0
	RTC+B Implementation 

All procedures in this manual have been reviewed
	December 5, 2025

	3.5
	2.0 / 1
	Adjusted formatting
	January 30, 2026

	3.1
4.1
	2.0 / 1
2.0 / 1
	Updated Base Points to Set Points
Updated navigation to QSRG
	April 1, 2026


PAGE  

