	ERCOT Operating Procedure Manual

DC Tie Desk
	



Power Operations Bulletin # 2025
ERCOT has posted/revised the DC Tie manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html 
2.3
Alert Media Notification Requirements 

Procedure Purpose:  To ensure the operator stays current using the system and to ensure system is tested.

	Protocol Reference
	
	
	
	

	Guide Reference
	
	
	
	

	NERC Standard
	
	
	
	


	Version: 2 
	Revision: 1
	Effective Date:  May 1, 2026


	Step
	Action

	Beginning

of each

Shift
	· Log into Alert Media at the beginning of each shift.
· 


· Refer to Desktop Guide Common to Multiple Desks Section 2.8, 

· Notify Service Desk immediately if unable to log into Alert Media and request immediate assistance.

	Alert Media
Test
	On the first weekend of each month, between the hours of 0800-2200:

· Coordinate the actual test time with the Shift Supervisor if he instructs you to proceed,

· Alert Media by activating the “SO ENS Test” scenario,  

· If any issues are found, open help ticket and cc: “shiftsupv”,

· Make log entry.


4.4
Loss of Primary Control Center Functionality
Procedure Purpose: Provide instructions for responding to conditions that cause the primary control center to become inoperable or uninhabitable while continuing to meet its obligations with regard to the reliable operations of the ERCOT system and ensuring the safety of control center personnel.

	Protocol Reference
	
	
	
	

	Guide Reference
	
	
	
	

	NERC Standard
	EOP-008-2

R1, R1.2, R1.2.1, R1.4 R1.6, R1.6.1, R1.6.2, 1.6.3, R4
	TOP-001-6

R9
	
	


	Version: 2 
	Revision: 1
	Effective Date:  May 1, 2026


	Step
	Action

	Contact Security
	IF:

· Unable to reach any Operator at the PCC (also trying Alternative Interpersonal Communication capability);

THEN:

· Check the control center video camera to determine the status of the PCC and personnel,

· Contact Security at the ACC

· Notify them of the situation AND
· Have them attempt to make contact with Security at PCC.

· Have them contact you with information acquired OR
IF:

· Notified by the PCC that they are evacuating and/or transferring sites OR
· control center video and Security confirms evacuation;

THEN:

· Continue with procedure.  

	3-Part


	When issuing an Operating Instruction, follow  three-part communication:

· Issue the Operating Instruction

· Receive a correct repeat back

· Give an acknowledgement

	Systems are Functional

	Call in Additional Operators
	Coordinate with the Transmission and Security Desk Operator and activate the Alert Media scenario to call in additional shift personnel, which includes a Shift Supervisor. 

 SELECT:

· SO Loss of Control Room at Taylor, OR;

· SO Loss of Control Room at Bastrop.

An email will be received after 10 minutes with a report of who has responded along with their estimated time of arrival.

	QSE

Hotline

Call
	Q#106 - Typical Hotline Script Emergency Notice Loss of Primary Control Center (Systems are Functional) 



	Additional Notifications
	The Director Control Room Operations and/or Designee will notify the following:

· Service Desk (to notify GMS Support and IT Infrastructure (Telecommunications and Data Center)

· Engineering Support

These phone numbers are also programmed into the control room cell phone.

	ERCOT Website
Posting
	As time permits, post the Emergency Notice on the ERCOT Website.

Typical Posting Script:
ERCOT has issued an Emergency Notice for the loss of the primary control center, all systems are functioning.

	Respond to QSEs
	Monitor frequency and re-run SCED/use (manual offset) as needed.

IF:

· QSEs call in with questions about operational timelines or non real-time issues;

THEN:

· Notify the QSE that timelines and non real-time issues will be addressed when additional staff arrive,

· Document QSE calls to pass along to the appropriate Operators as they arrive.

	Real-time Contingency Analysis (RTCA)
	Operations Support will assist in monitoring the RTCA functionality including results and may communicate suggested actions as needed.

	DC Tie E-Tags
	Make every attempt to handle all DC Tie E-Tags.

If the workload makes it impossible to keep up with, the E-Tags will be passively denied.

	Log
	Log all actions taken.

	Systems are not Functional

	NOTE
	Market Participants must be notified of unplanned outages of 30 minutes or more, of telemetering, monitoring and assessment capabilities, and associated communication channels between affected entities.

	Monitor Frequency
	The ability to view an adequate Frequency source may be limited during a site-failover, database load, or if AGC is temporarily unavailable.  To view the System Frequency during these conditions you may monitor the following sources.

· ERCOT control room digital wall frequency displays

· PI ProcessBook → ERCOT → TrueTime Frequency (Taylor) and/or

· PI ProcessBook → ERCOT → TrueTime Frequency (Bastrop)
It may be necessary to reload the PI ProcessBook “ERCOT Main Summary” display to show the historical data.

	Constant

Frequency
	IF:

· The loss of PCC involves the loss of EMS (LFC and RLC);

THEN:

· Instruct a QSE to go on Constant Frequency

· Q#114 – Typical Script to Instruct a QSE on Constant Frequency for LRC/SCED Failure

· Refer to Real-time desk procedure section 3.3, EMMS (LFC and RLC/SCED) Failure 



	Call in Additional Operators
	Coordinate with the Transmission and Security Desk Operator and activate the Alert Media scenario to call in additional shift personnel, which includes a Shift Supervisor. 

 SELECT:

· SO Loss of Control Room at Taylor, OR;

· SO Loss of Control Room at Bastrop.

An email will be received after 10 minutes with a report of who has responded along with their estimated time of arrival.

	QSE

Hotline

Call
	Q#107 - Typical Hotline Script Emergency Notice Loss of Primary Control Center (Systems are NOT Functional) 

If either Hotlines are inoperable, phone numbers can be found on SharePoint under OPX & LD Numbers.

	ERCOT Website
Posting
	As time permits, post the Emergency Notice on the ERCOT Website.

Typical Posting Script:
ERCOT has issued an Emergency Notice for the loss of the primary control center, systems are not functioning.

	Additional Notifications
	The Director Control Room Operations and/or Designee will notify the following:

· Service Desk (to notify GMS Support and IT Infrastructure (Telecommunications and Data Center)

· Engineering Support

These phone numbers are also programmed into the control room cell phone.

	Respond to QSEs
	IF:

· The QSE that is put on constant frequency needs assistance controlling frequency;

THEN:

· Issue a unit specific Operating Instruction to another QSE to help with Regulation.  (Follow-up with electronic Dispatch Instruction as time permits)

OR
· Put a different QSE on constant frequency (Remember to take the first QSE off constant frequency).

	Real-time Contingency Analysis (RTCA)
	Operations Support will be responsible for the State Estimator and RTCA functionality and ensuring an RTA is performed at least every 30 minutes.  They will communicate results and any suggested actions as needed.

	DC Tie Tags
	Make every attempt to handle all DC Tie E-Tags.

If the workload makes it impossible to keep up with, the E-Tags will be passively denied.

	Electronic

Dispatch 

Instruction
	Follow-up with electronic Dispatch Instructions where appropriate when systems are functional or as time permits (See Desktop Guide Common to Multiple Desks section 2.3).

When issuing a VDI or confirmation, ensure the use of three-part communication:

· Issue the Operating Instruction

· Receive a correct repeat back

· Give an acknowledgement



	Log
	Log all actions taken.


4.5
Restoration of Primary Control Center Functionality

Procedure Purpose: To be performed once additional staff has reported to the alternate Control Center and Grid can return to normal operations.

	Protocol Reference
	
	
	
	

	Guide Reference
	
	
	
	

	NERC Standard
	
	
	
	


	Version: 2 
	Revision: 1
	Effective Date:  May 1, 2026


	Step
	Action

	NOTE:
	As additional Operators arrive, communicate any pertinent information that will assist them in getting their specific functions ready for normal operation.

	Additional

Operators
	When a Real-Time Desk Operator has arrived, turn over frequency control to that Operator and assist with other needs such as approve any E-Tags waiting.

	Notification of Additional Operators
	WHEN:

· Fully staffed;

THEN:

· Coordinate with the Control room and make notification using  Alert Media - SO Loss of CC Operations Resumed.

	Help

Desk
	Make notification to Service Desk that the Control Room is now back to normal operations from the alternate.

	Contact Security
	Notify Security that the transition of Operations to the ACC has been completed.

	Log
	Make log entries as needed.


Document Control

Manual Change History

	Procedure
	Ver/Rev
	Reason for Issue
	Effective Date

	All Sections
	2.0 / 0
	RTC+B Implementation 

All procedures in this manual have been reviewed
	December 5, 2025

	3.3
	2.0 / 1
	Updated new CENACE BA to CEN1
	February 20, 2026

	2.3

4.4

4.5
	2.0 / 1

2.0 / 1

2.0 / 1
	Removed NXT and replaced with Alert Media
Removed NXT and replaced with Alert Media
Removed NXT and replaced with Alert Media
	May 1, 2026



