	ERCOT Operating Procedure Manual

	Shift Supervisor Desk



Power Operations Bulletin # 2026
ERCOT has posted/revised the Shift Supervisor Desk manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html
6.1
Reports

Procedure Purpose: Provide reporting criteria and instructions for the daily reports sent to the PUC, the process to report certain events to the Texas Reliability Entity, posting EEA notices to RCIS and the process for reporting system disturbances to NERC and DOE.

	Protocol Reference
	 22 (B)
	6.5.1.2 (4)
	
	

	Guide Reference
	3.2.3
	4.7
	
	

	NERC Standard
	EOP-004-4

R1, R2 


	EOP-010-1

R1, R1.1, R2


	EOP-011-4

R2, R2.1, R2.2, R2.2.3, R2.2.3.2, R2.2.3.3, R2.2.5
	


	Version: 2 
	Revision: 1
	Effective Date:  May 1, 2026


	Step
	Action

	PUCT Daily Report

	Note
	The PUCT Daily Report is automatically sent at 0530 and again at 1430 each day during the summer.  During the Fall, Winter and Spring the PUCT Daily Report is automatically sent at 0230 and again at 1430 each day.  Notify Grid Applications Development if the report fails to automatically send. 

	Prepare Report
	During the Summer prepare the PUCT Daily Report between 0530 – 0600 and again between 1430 – 1500 each day.  During the Fall, Winter and Spring prepare the PUCT Daily Report between 0230 – 0300 and again between 1430 – 1500 each day.  Management will coordinate the transition of reports so that everyone knows the appropriate times that the report should be sent.

	Review Report
	Open up the PUCT Report site and review at any time.  If required to send out the report manually, Refer to Desktop Guide Shift Supervisor section 2.7.

	E-Mail

Report
	E-mail the report to the distribution list entitled “PUC-Available Generating Resources.”

Subject line example: 0600 PUCT Report June 1, 2019 

	Unit Trip Posting

	Report
	Complete the Unit Trip posting for the previous day between 0000 – 0800 each day of the week.

	Analyze
	Review:

· Any unit trips from the previous day,

· Post an Operational Information message, low priority, on the ERCOT Website

	<450 MW
	IF:

· No trips are greater than 450 MW,
· Post the following message example on the ERCOT Website

	Post
	No sudden loss of generation greater than 450 MW occurred on <Date>. 

	≥450 MW
	IF:

· A trip was 450 MW or more,

· Post the following message example on the ERCOT Website

	Post
	On <Date>, a sudden loss of generation occurred at <Time> totaling *** MW. Frequency declined to **.*** Hz, ERCOT load was **,*** MW.

	Multiple Trip Example
	On <Date>, a sudden loss of generation occurred at <Time> totaling *** MW. Frequency declined to **.*** Hz, ERCOT load was **,*** MW. Another sudden loss of generation occurred at <Time> totaling *** MW. Frequency declined to **.*** Hz, ERCOT load was **,*** MW.

	Load Curtailment due to Transmission Problem Posting

	Note
	If the Emergency Condition is the result of a transmission problem, ERCOT shall act immediately to return the ERCOT System to a reliable condition, including instructing any QSE representing a Resource to change the Resource’s output, curtailing any remaining DC Tie Load, and instructing TSPs or DSPs to drop Load. In addition, ERCOT may instruct any QSE representing an ESR to suspend ESR charging if ERCOT determines that a Load reduction by the ESR is capable of mitigating the transmission problem.  An ESR co-located behind a POI with onsite generation that is incapable of exporting additional power to the ERCOT System may continue to charge as long as maximum output to the ERCOT System is maintained

	Analyze
	REVIEW:

· Any instructed Load Curtailment, Load Resource Deployment, ERS Resource Deployment, or DC Tie curtailments from the current day;

IF:
· An event occurred during the current day;
THEN:

· Complete the Load Curtailment due to Transmission Problem posting prior to midnight on the day of the event if Resources output is curtailed, any remaining DC Tie load is curtailed, TSPs and DSPs instructed load is curtailed, ESR has been instructed to suspend charging, or Load Resource(s) or ERS Resource(s) are deployed due to a transmission problem;

POST:

· An Operational Information message, low priority, on the ERCOT Website.

	ERCOT Website Posting Example
	Typical ERCOT Website posting:
On <Date>, at <Time>, ERCOT instructed a(n) <Load Curtailment/Load Resource Deployment/ERS Resource Deployment/DC Tie Curtailment> totaling *** MW in the <substation(s) or geographic area>. All < Load/Load Resources/ERS Resources/DC Tie Curtailments> were restored at <Time>.

	Event Analysis Reporting

	1
	WHEN an event occurs that is listed on the “event list” below, before shift is over:

· E-mail information to Director Control Room Operations and Designee

· The subject line of the e-mail should read “TRE Event.”

	Event

List
	For purposes of the event analysis program, brief reports must be completed with 10 days (Responsibility of Grid Analysis group).  Most events listed are either DOE-417 or EOP-004 reportable, those timelines and forms will be used in place of the EA brief report.  

Category 1 Events:

a. An outage, contrary to design, of three or more BES Facilities caused by an event:

i. The outage of a combination of three or more BES Facilities (excluding successful automatic reclosing)

ii. The outage of an entire generation station of three or more generators (aggregate generation of 500 MW to 1,999 MW); each combined cycle unit is counted as one generator

b. Retired on January 1, 2024
c. Failure or misoperation of a BES RAS

d. Retired on January 1, 2024
e. BES system separation contrary to design results in an island of 100 MW to 999 MW. This excludes BES radial connections, and non-BES (distribution) level islanding

f. Retired on January 1, 2016

g. The loss of generation of 1,400 MW to 1,999 MW

h. Loss of monitoring and/or control, at a Control Center, such that it degrades the entity’s ability to make Real-Time operating decisions that are necessary to maintain reliability of the BES in the entity’s footprint for 30 continuous minutes or more 

Some examples that should be considered include, but are not limited to the following: 

i. Loss of operator ability to remotely monitor or control BES elements 

ii. Loss of communications from SCADA RTU 

iii. Unavailability of ICCP links reducing BES visibility 

iv. Loss of the ability to remotely monitor and control generating units via AGC 

v. Unacceptable state estimator or contingency analysis solutions 

i. A non-consequential interruption of inverter type resources aggregated to 500 MW or more not caused by a fault on its inverters, or its AC terminal equipment

j. A non-consequential interruption of a DC tie, between two separate asynchronous systems, loaded at 500 MW or more, when the outage is not caused by a fault on the DC tie, its inverters, or its AC terminal equipment. 

Category 2 Events:

a. Complete loss of Interpersonal Communication and Alternative Interpersonal Communication capability affecting its staffed BES control center for 30 continuous minutes or more 

b. Retired on January 1, 2016 refer to Category 1h

c. BES Emergency resulting in a voltage  deviation of equal to or greater than 10% difference of nominal voltage sustained for 15 continuous minutes

d. Complete loss of off-site power (LOOP) to a nuclear generating station per the Nuclear Plant Interface Requirement

e. System separation contrary to design, that results in an island of 1,000 MW to 4,999 MW

f. Simultaneous loss of 300 MW or more of firm load due to a BES event, contrary to design, for more than 15 minutes

g. IROL exceedance for greater than 30 minutes.

Category 3 Events:

a. Loss of firm load, contrary to design, of 2,000 MW or more

b. System separation contrary to design, that results in an island of 5,000 MW or more

c.  Not applicable to ERCOT

d.  Loss of 2,000 MW or more provided by DC ties(s) connected to asynchronous resources

·  Loss of generation (including inverter-based resources) of 2,000 MW or more. This excludes RAS action that performed as designed.

	NERC and DOE Reporting Operating Plan

	Note
	· Send an email to “SysOpsMgrs” when a NERC or DOE reporting event occurs or if suspected to occur and verify it was received due to potential time constraints on report submissions 

· Within 72 hours of incident a Final Report must be filed unless an interim update has been provided

	DOE-417

Reporting

Events
	DOE-417 forms can be downloaded at: https://doe417.pnnl.gov/report
The events listed below must be reported within 1 hour of the incident:  

· Physical attack that causes major interruptions or impacts to critical infrastructure facilities or to operations
· Reportable Cyber Security Incident
· Cyber event that is not a Reportable Cyber Security Incident that causes interruptions of electrical system operations

· Complete operational failure or shut-down of the transmission and/or distribution electrical system

· Electrical System separation (Islanding) where part or parts of a power grid remain(s) operational in an otherwise blacked out area or within the partial failure of an integrated electrical system

· Uncontrolled loss of 300 MW or more of firm system loads for more than 15 minutes from a single incident

· Firm Load shedding of 100 MW or more implemented under emergency operational policy 

· System-wide voltage reduction of 3% or more

· Public appeal to reduce the use of electricity for purpose of maintaining the continuity of the electric power system 
The events listed below must be reported within 6 hours of the incident:

· Physical attack that could potentially impact electric power system adequacy or reliability; or vandalism which target components of any security systems

· Cyber event that could potentially impact electric power system adequacy or reliability

· Loss of electric service to more than 50,000 customers for 1 hour or more

· Fuel supply emergencies that could impact electric power system adequacy or reliability

The events listed below must be reported by the later of 24 hours of recognition of meeting an event threshold for reporting or by the end of the next business day (4 p.m. local time will be considered the end of the business day):

· Damage or destruction of a Facility that results in action(s) to avoid a Bulk Electric System Emergency

· Damage or destruction of its Facility that results from actual or suspected intentional human action
· Physical threat to its Facility excluding weather or natural disaster related threats, which has the potential to degrade the normal operation of the Facility. Or suspicious device or activity at its Facility

· Physical threat to its Bulk Electric System control center, excluding weather or natural disaster related threats, which has the potential to degrade the normal operation of the control center. Or suspicious device or activity at its Bulk Electric System control center

· Bulk Electric System Emergency resulting in voltage deviation on a Facility; A voltage deviation equal to or greater than 10% of nominal voltage sustained for greater than or equal to 15 continuous minutes

· Uncontrolled loss of 200 Megawatts or more of firm system loads for 15 minutes or more from a single incident for entities with previous year’s peak demand less than or equal to 3,000 Megawatts
· Total generation loss, within one minute of: greater than or equal to 1,400 Megawatts in the ERCOT Interconnection 

· Complete loss of off-site power (LOOP) affecting a nuclear generating station per the Nuclear Plant Interface Requirements

· Unexpected Transmission loss within its area, contrary to design, of three or more Bulk Electric System Facilities caused by a common disturbance (excluding successful automatic reclosing)

· Unplanned evacuation from its Bulk Electric System control center facility for 30 continuous minutes or more

· Complete loss of Interpersonal Communication and Alternative Interpersonal Communication capability affecting its staffed Bulk Electric System control center for 30 continuous minutes or more

· Complete loss of monitoring or control capability at its staffed Bulk Electric System control center for 30 continuous minutes or more

· Uncontrolled loss of a total of 500 MW or more from inverter-based resources(s) for greater than 30 minutes at a common point of interconnection to the bulk electric system

Attempted Cyber Compromise: Within 1 calendar day of determination of the attempted cyber compromise:

· Cyber Security Incident that was an attempt to compromise High or Medium Impact Bulk Electric System Cyber Systems or their associated Electronic Access Control or Monitoring Systems

	Event 

Reporting

EOP-004-4
	If an EOP-004 reportable event is also a reportable event under the DOE-417 requirements, the DOE-417 form can be used to report to NERC and DOE. 

The events listed below must be reported by the later of 24 hours of recognition of meeting an event threshold for reporting or by the end of the next business day (4 p.m. local time will be considered the end of the business day).

· Damage or destruction of a Facility that results in actions to avoid a BES Emergency

· Damage or destruction of a Facility that results from actual or suspected intentional human action

· Physical threats to a Facility excluding weather or natural disaster related threats, which has the potential to degrade the normal operation of the Facility or suspicious device or activity at a Facility

· Physical threats to its BES control center, excluding weather or natural disaster related threats, which has the potential to degrade the normal operation of the control center or suspicious device or activity at its BES control center

· Public appeal for load reduction to maintain continuity of the BES 

· System wide voltage reduction of 3% or more

· Firm load shedding ≥ 100 MW (manual or automatic)

· Voltage deviation of =/> 10% of nominal voltage sustained for ≥ 15 continuous minutes

· Uncontrolled loss of firm load for greater than 15 minutes from a single incident:

· ≥ 300 MW for entities with a previous year’s demand of ≥ 3,000 MW OR
· ≥ 200 MW for all other entities

· Each system separation resulting in an island ≥ 100 MW 

· Loss of generation of ≥ 1,400 MW 

· Complete loss of off-site power affecting a nuclear generating station per the Nuclear Plant Interface Requirement

· Unexpected loss within its area, contrary to design, of three or more BES Elements caused by a common disturbance (excluding successful automatic reclosing)

· Unplanned evacuation from BES control center facility for 30 continuous minutes or more

· Complete loss of Interpersonal Communication and Alternative Interpersonal Communication capability affecting its staffed BES control center for 30 continuous minutes or more

· Complete loss of monitoring or control capability at its staffed BES control center for 30 continuous minutes or more 

	Reporting

To

Entities
	When required to file or forward a report from other entities, the Director Control Room Operations or the Designee will be responsible.

File or forward the disturbance report to the following entities:

· NERC System Awareness (systemawareness@nerc.net)

· NERC (operations@eisac.com), requirement for cyber and courtesy copy for all other reports

· Fax (404) 446-9770, if internet down

· Phone (404) 446-9780 

· DOE when required above  (doehqeoc@hq.doe.gov)
· Fax (202) 586-8485, if internet down

· Phone (202) 586-8100

· NERC and DOE Disturbance Reporting distribution list

In the body of the e-mail, type the following:

· "Contains Privileged Information and/or Critical Energy Infrastructure Information - Do Not Release".

	Note
	· If adverse conditions prevent reporting the damage caused by an event and issuing a written Event Report within the timing of the Standard, notify NERC and Texas RE and provided as much information as is available at the time of the notification.
· Please be aware that for phone calls to NERC, you will be prompted by a computerized auto-attendant to press 1 for operational issues or 2 for cyber-security issues.

	RCIS Reporting

	EEA

Postings
	There are four levels of Emergency Energy Alert (EEA). As ERCOT enters each level, postings must be made on the RCIS under “Energy Emergency Alert”:

· “ERCOT is declaring EEA 1”

· “ERCOT is declaring EEA 2” 

· “ERCOT is declaring EEA 3”

· “ERCOT is in EEA 0 and back to normal operations.” 

	Alert Media Notification Requirements

	Beginning

of each

Shift
	Log into Alert Media at the beginning of each shift in order to make the required notification quickly. 

· If issues arise and you are unable to log into Alert Media, Verify whether the rest of the control room (Primary and Alternate) is having issues as well. Notify the helpdesk and request immediate assistance.

	Note
	Alert Media notification should be coordinated with the Shift Engineer.

	Watch
	IF:

· A Watch for Physical Responsive Capability is initiated,

THEN:

· Select the “SO Watch PRC below 3000” Scenario and activate notification,

WHEN:

· A Watch for Physical Responsive Capability has been cancelled,
THEN:

· Select the “SO Watch for PRC Cancelled” Scenario and activate notification.

	EEA

Implementation Levels
	IF:

· ERCOT initiates EEA Level 1,
THEN:

· Select the “SO EEA Level 1” Scenario and activate notification,
IF:

· ERCOT initiates EEA Level 2,
THEN:

· Select the “SO EEA Level 2” Scenario and activate notification,
IF:

· ERCOT initiates EEA Level 3 with Load Shed,
THEN:

· Select the “SO EEA Level 3, WITH Load Shed” Scenario and activate notification.

	EEA

Termination Levels
	WHEN:

· EEA Level 3 is terminated,
THEN:

· Select the “SO EEA Level 3 to EEA Level 2” Scenario and activate notification,
WHEN:

· EEA Level 2 is terminated,
THEN:

· Select the “SO EEA Level 2 to EEA Level 1” Scenario and activate notification,
WHEN:

· EEA Level 1 is terminated,
THEN:

· Select the “SO EEA Level 1 Cancellation” Scenario and activate notification.

	Loss of

Firm

Load
	IF:

· An Operator (ERCOT or TO) has issued a request for firm load shed of ≤ 100 MW,
THEN:

· Notify the Director Control Room Operations and/or Designee immediately.

WHEN:

· An Operator (ERCOT or TO) has issued a request for firm load shed of ≥ 100 MW,
THEN:

· Notify the Director Control Room Operations and/or Designee immediately,

· Select the “SO Request Firm Load Shed” Scenario and activate notification.

	Alert Media Testing
	WHEN:

· Performing Shift Supervisor Procedure 9.3 Monthly Testing of Non-Routinely used Telecommunications Facilities,
THEN:

· Select the “SO ENS Test” Scenario and activate notification.

	ERCOT Morning Report

	Note
	· This report is currently only required Monday – Friday.

· The Morning Report form is located on the _Operations Official Spreadsheets folder

	1
	Weather Information:

· The temperatures are automatically pulled from the EMS, however please verify temperatures from a National or Local Weather Service for each city listed and adjust as necessary.

· Enter the current day forecast conditions for each city listed.

	2
	Load Data:
· The All-Time Peak MW and Seasonal Peak MW will be provided as needed. 

· Verify the Projected Peak MW and peak hour for the current day.  Use the most reasonable forecast, which may not be the highest.

· Verify the Previous Day Actual MW.

	3
	Interchange: 

· Verify the net flow across the DC-Ties for the peak hour.  This can be obtained from the MOI under “DC Tie Scheduling” or from the Excel MAI.

	4
	Transmission Line Outages:

· Verify the number of 345 kV line segment outages for the peak hour.

	5
	Generation MW Totals:

· Verify the Generation scheduled outage MW total.

· Verify the Generation forced outage MW total.

	6
	Projected MW Reserves:

· Verify the Responsive Reserve requirement at the Project Peak.

· Verify the anticipated operating reserves available at time of peak.

· The anticipated operating reserves can be found by adding the “Max Cap. Room” and Responsive Reserve requirement.

	7
	Recent ERCOT Congestion Activity:

· No action needed

	8
	Comments:

· List any active OCNs, Advisories, Watches or Emergency notices.

	9
	Select:

· Create Report

	Email
	The file is transferred to P:\SYSTEM OPERATIONS drive in the NERC Morning Report Folder.   This report should be sent as an attachment by 0700 using the e-mail distribution list entitled “ERCOT Morning Report.”

The subject line of the e-mail should read “ERCOT Morning Report for <date>”

	RMR Unexcused Misconduct Events

	Note
	· For a RMR unit, a “Misconduct Event” means any hour or hours during which Participant is requested to, but does not; deliver the energy at a level of at least 98% on each hour of the level shown in the Availability Plan.

· For a Synchronous Condenser Unit, a “Misconduct Event” means any hour or hours during which Participant is requested to, but does not, synchronize the Unit to the ERCOT Transmission Grid during any hour in which the Unit is shown in the Availability Plan

	1
	IF:

· An RMR or Synchronous Condenser fail to deliver the energy when requested to;

THEN:

· Notify the Director Control Room Operations and/or Designee.

· The management will gather the detailed information and send an e-mail to “Nodal Settlements and Billing” with the subject line “Action Required – RMR Unexcused Misconduct Event”. 

	Shift Schedule

	Note
	· Operations Shift Schedules will be posted to the ERCOT Website under Data Products>Grid on the Transmission Page in the Reports & Extracts section.  

· The posting of the schedule will be current at all time to be compliant with the Protocols.

	Geomagnetic Disturbance (GMD)

	Note
	 Solar storms or Geomagnetic disturbances (GMDs) are caused by the interaction of coronal mass ejections (solar flares) with the Earth’s Ionosphere. This interaction produces ionospheric currents in the magnitude of millions of amperes which disturb Earth’s magnetic field. This disturbance induces voltage potential at Earth’s surface which results in geomagnetically induced currents (GICs) in conducting paths such as long transmission lines, pipelines, cables etc. GICs are low frequency or quasi-DC currents which enter and exit the power system at transformer groundings and grounded transmission lines. GICs of 100’s of amperes in magnitude have been recorded. Hence the GICs have the potential to disrupt the normal operation of power system and may damage transformers. GICs may also lead to the loss of reactive power support and hence may cause voltage instabilities.

	Monitor
	Monitor forecasted and current space weather:
Either via the Reliability Coordinator Information System (RCIS) at https://www.oatihub.oati.com/Hub/login, or NOAA’s Space Weather Prediction Center (SWPC) at http://www.swpc.noaa.gov/

	Warning

(Forecasted)
	WHEN:

· A forecasted GMD Warning is issued for K-7 and greater or G3 and greater;

THEN: 

· Post message on the ERCOT Website
· Notice Type: Operational Information

· Notice Priority: Low

Typical ERCOT Website Posting:
The Space Weather Prediction Center has issued a GMD Warning of [state level] until [date and time].

Notify Operations Support to run power flow studies to identify 345kV transformers loaded above 70% and develop a mitigation plan if needed.

	Extend
	IF:

· The Warning is extended or K level increases/decreases;

THEN: 

· Post new message on the ERCOT Website and
· Cancel the older message
Typical ERCOT Website Posting:
The Space Weather Prediction Center has extended the GMD Warning of [state level] until [date and time].

	Cancel
	WHEN:

· The Warning is no longer valid;

THEN: 

· Cancel the ERCOT Website posting.

	Alert

(Current)
	WHEN:

· An Alert for a GMD is issued for K-7 and greater or G3 and greater, or the K level increases/decreases;

THEN: 

· Instruct the Transmission and Security Desk and Real-Time Desk Operators to implement their GMD procedures to make additional postings and Hotline calls.

	Extend
	IF:

· The Alert is extended or the K level is increased/decreases;

THEN: 

· Instruct the Operators to extend the Alert and/or make notifications regarding storm severity.

	Cancel
	WHEN:

· K levels drop below K7 or when the Warning is no longer valid;

THEN: 

· Instruct the Operators to cancel the Advisory for the Alert.

	Issues
	IF:

· Any TO reports an issue due to the GMD event;

THEN: 

· Send e-mail to the following with the details
· Operations Analysis

· Operations Support

· Shiftsupv

	Gas Restrictions

	1
	Once notified by a QSE of gas restrictions

· Send an e-mail to “Gas Company Notifications”.  This will notify all appropriate ERCOT staff.

	2
	Determine:

· If the gas restriction could impact electric power system adequacy or reliability,

THEN:

· Proceed to “Reports” procedure for NERC/DOE reporting requirements, AND
· Consider discussing fuel switching with affected QSE for the generation that has this capability

This data can be viewed at ERCOT SharePoint > System Operations – Control Center > Quick Links > Fuel Oil Capability

	FFSSR Restocking Request

	Initial Request
	IF:

· During or following the deployment of FFSS, the QSE for an FFSSR may request an approval from ERCOT to restock their fuel reserve to restore their FFSS capability.

THEN:

· Request the QSE to submit a written request to the ERCOT Shift Supervisors email.

	Request Received
	IF:

· An email request is received;

THEN:

· Notify the Director Control Room Operations and/or Designee to help coordinate other departments with process.

	Review Request
	IF:

· A request has been received;

DETERMINE:

· If the entity can still meet their 48-hour FFSS capacity requirement,

· How long until the end of the Contract period,

· Risks of cold weather impacting the region, and
Any other conditions or impacts that need to be considered.

	Response

Provided
	THEN:

· Within 48 business hours an emailed response is required to the entity,
EXAMPLE:

· ERCOT confirms instructions have been made to [RESOURCE NAME(s)] to restore fuel reserves so [QSE] can meet their 48-hour obligation per the FFSS VDI dispatch instructions, OR

ERCOT denies the request to [RESOURCE NAME(s)] to restore fuel reserves.

	Log
	Log all actions.

	Remedial Action Schemes (RAS)

	1
	IF:
· A Monthly RAS report is received by e-mail;

THEN:

· Forward reports to:

· OPS Support Engineering
· Operations Analysis

· Shift Supervisors 


7.2
EEA Implementation Guideline

Procedure Purpose:  To provide general guidelines on the actions and sequence of steps required prior to and during an EEA event.

	Protocol Reference
	6.5.7.6.2.2(16)
	6.5.9.3.4(6)
	6.5.9.4
	6.5.9.4.2

	
	6.5.9.4.3
	
	
	

	Guide Reference
	4.5.3
	4.5.3.1
	4.5.3.2
	4.5.3.3

	
	4.5.3.4
	
	
	

	NERC Standard
	EOP-011-4

R1, R1.1, R1.2, R1.2.2, R1.2.6, R2, R2.1, R2.2 
	
	
	


	Version: 2 
	Revision: 1
	Effective Date:  May 1, 2026


	Note
	· ERCOT shall use the PRC and system frequency to determine the appropriate Emergency Notice and EEA levels.

· Manually deploy Load Resources other than Controllable Load Resources providing ECRS or RRS before entering into an Energy Emergency Alert (EEA), to maintain a minimum 500 MWs of Physical Responsive Capability (PRC) reserves on Generation Resources.
· ERCOT will declare an EEA Level 1 when PRC falls below 2,500 MW and is not projected to be recovered above 2,500 MW within 30 minutes without the use of the following actions that are prescribed for EEA Level 1
· ERCOT MAY immediately implement EEA Level 2 when clock-minute average system frequency falls below 59.91 Hz for 15 consecutive minutes.  

· ERCOT may immediately implement EEA Level 3 any time the clock-minute average system frequency falls below 59.91 Hz for 20 consecutive minutes OR when steady-state frequency falls below 59.8 Hz for any duration of time.

· ERCOT SHALL immediately implement EEA Level 3 any time the steady-state frequency is below 59.5 Hz for any duration.

	Note
	Energy Storage Resources (ESR) are instructed to suspend charging.  For ESRs, ERCOT shall issue the suspension instruction via a SCED Base Point instruction, or, if otherwise necessary, via a manual Dispatch Instruction.  An ESR shall suspend charging unless it is providing Primary Frequency Response, has received a charging instruction via SCED Base Point, or is carrying Reg-Down and has received a charging instruction from LFC.  However, an ESR co-located behind a POI with onsite generation that is incapable of exporting additional power to the ERCOT System may continue to charge as long as maximum output to the ERCOT System is maintained.


	Prior to entering EEA 

· To be considered when ERCOT anticipates entering an EEA Event or one is imminent

	Action

	· Media Appeal for voluntary energy conservation

	· Commit available Resources that can respond in the timeframe of the emergency, including RMR

	· Non-Spin deployed

	· Request Large Load Curtailment Program

	· 30 MIN & 10 MIN ERS deployed.  This includes Weather-Sensitive if available and Time Periods TP3 & TP4
· Ensure XML deployment made prior to QSE Hotline call

	· Distribution voltage reduction, if deemed beneficial when EEA2 and/or EEA3 load shed is not anticipated

	· TOs load management program deployed during June - September or when available during only in EEA 2 or EEA3 if not already self-deployed by TO

	· TCEQ exercising enforcement discretion for exceedance of generating plants environmental limits

	· ERCOT and the TO agree to use a 15-minute Rating
· Identify the appropriate double-circuit contingency and constrain on the single-circuit contingency to make more generation available

	· ERCOT notifies MISO or SPP to request one or more SWGRs be switched into ERCOT


	Administrative tasks applicable to each step:

	· Hotline calls made

	· Alert Media System activated

	· ERCOT Website message posted

	· SPP RC Notified

	· RCIS Posting

	· Ensure 3-part communication is used

	· Update EEA Dashboard, if EEA3 update Load Shed amounts each time it changes 

	· Ensure ERS XML deployments are made with time period changes


	EEA Level 1 Implementation 

	· PRC <2500 MW and is not projected to be recovered above 2500 MW within 30 minutes without the use of EEA Level 1

	· EMS EEA Flag activated

	· TCEQ exercising enforcement discretion for exceedance of generating plants environmental limits

	· Non-Spin deployed if not already deployed

	· SCED dispatchable ECRS released, if not already released

	· 30 MIN ERS deployed, if deploying in Level 1.  This includes Weather-Sensitive if available and Time Periods TP3 & TP4 if not already deployed

Ensure XML deployments are made

	· Resource testing suspended

	· Online RMRs loaded to full output

	· Emergency Energy procedures implemented across CENACE DC-Ties

	· EEA 1 Schedule requested across SPP DC-Ties

	· RUC VDI/electronic Dispatch Instruction confirmation, as appropriate/including EMR 

	· DOE-417 for public appeals

	· PRC <2000, Manually released RRS

	· If available, deploy the Resources providing ECRS using ONECRS Resource Status

	EEA Level 2 Implementation

	· Maintain steady state system frequency at a minimum of 59.91 Hz and maintain PRC above 1500 MW 

· ERCOT may immediately implement EEA Level 2 when the clock-minute average system frequency falls below 59.91 Hz for 15 consecutive minutes.  

· ERCOT will declare an EEA Level 2 when PRC <2000 MW or unable to maintain system frequency at a minimum of 59.91 Hz and is not projected to be recovered above 2000 MW within 30 minutes without the use of EEA Level 2

	· Media Appeal for voluntary energy conservation (if not already issued)

	· Load Resources deployed and/or ERS Resources (if not already deployed)

· Group 0/ Group 0+1a/ Group 0+1a+1b/ Group 0+1a+1b+1c/ Group 0+1a+1b+1c+2/ Group 0+1a+1b+1c+2+3 (<2000MW)
· All (<1500MW)

Ensure XML deployments are made

	· ERS deployed, if not already deployed.  This includes Weather-Sensitive

· Ensure XML deployment made prior to QSE Hotline call

	· ERCOT and the TO agree to use a 15-minute Rating
· De-activate the appropriate double-circuit contingency and constrain on the single-circuit contingency to make more generation available

	· TOs load management program deployed if not already deployed during June - September or when available 

	· Emergency Energy Procedures implemented across SPP DC-Ties

	· TOs notified of Load Resource deployment

	· Distribution voltage reduction, as appropriate if not already implemented.

	· RUC VDI/electronic Dispatch Instruction confirmation, as appropriate/including EMR

	EEA Level 3 Implemention FIRM LOAD SHED

	· ERCOT may immediately implement EEA Level 3 when the clock-minute average system frequency falls below 59.91 Hz for 20 consecutive minutes.  

· ERCOT will declare an EEA Level 3 when PRC cannot be maintained above 1500 MW
· PRC < 1500 MW and is not projected to be recovered above 1,500 MW within 30 minutes, or when the clock-minute average frequency falls below 59.91 Hz for 25 consecutive minutes OR when steady-state frequency falls below 59.8 Hz for any duration of time.  

	· Implement any measures associated with EEA Levels 1 and 2 that have not already been implemented

	· Verify all ERS and Load Resources deployed prior to firm load shed
Ensure XML deployments are made

	· Energy Storage Resources (ESR) are instructed to suspend charging.  For ESRs, ERCOT shall issue the suspension instruction via a SCED Base Point instruction, or, if otherwise necessary, via a manual Dispatch Instruction.  An ESR shall suspend charging unless it is providing Primary Frequency Response, has received a charging instruction via SCED Base Point, or is carrying Reg-Down and has received a charging instruction from LFC.  However, an ESR co-located behind a POI with onsite generation that is incapable of exporting additional power to the ERCOT System may continue to charge as long as maximum output to the ERCOT System is maintained.

	· Firm Load shed ordered (100 MW blocks)

	· QSEs notified of Firm Load shed

	· Load shed achieved


7.3
EEA Restoration Guideline

Procedure Purpose:  To provide general guidelines on the actions and sequence of steps required when recovering from an EEA event.

	Protocol Reference
	6.5.9.4.3
	
	
	

	Guide Reference
	
	
	
	

	NERC Standard
	
	
	
	


	Version: 2 
	Revision: 1
	Effective Date:  May 1, 2026


	Action

	Administrative tasks applicable to each step:

	· Hotline calls made

	· Alert Media System activated

	· ERCOT Website message updated

	· SPP RC Notified

	· RCIS Posted

	RESTORE FIRM LOAD 

	· Firm load restoration instructed

	· QSEs notified of Firm load restoration

	· Load shed recall achieved

	EEA LEVEL 3 TO EEA LEVEL 2 

	· All firm load must be restored prior to Load Resources being recalled

	· Begin recalling Load Resources 

	· TOs notified of Load Resources

	· TOs notified of Load Resource and ERS Resources recall

	EEA  Level 2 TO EEA LEVEL 1 

	· TOs load management program recalled

	· Instruct all deployed Load Resources that are not controllable to be restored

	EEA  Level 1 TO EEA 0 

	· End emergency energy across DC Ties

	· Release any RUC committed Resources

	· Manually deployed RRS recalled

	· Restore control to the post-contingency flow to within the Emergency Rating for those constraints that utilized the 15-Minute Rating
· Enforce double-circuit contingencies

	· See administrative tasks


9.3
Monthly Testing of Alternative Interpersonal Communication Device and other Communication Devices

Procedure Purpose: To test the multiple communication capabilities at least once each calendar month to ensure functionality.

	Protocol Reference
	
	
	
	

	Guide Reference
	
	
	
	

	NERC Standard
	COM-001-3

R9
	
	
	


	Version: 2 
	Revision: 1
	Effective Date:  May 1, 2026


	Step
	Action

	Primary Control Center

	1st 

Weekend

Of Every

Month
	On the first weekend of each month, between the hours of 0000 Saturday and 0500 Monday, test each communication device as listed in the steps below.  

	Testing

Form
	Complete the Monthly Communication Tests spreadsheet located on the System Operations – Control Center SharePoint site under Alternative Interpersonal Communication Testing (on left under Documents).

	Satellite Phone

(AIC) 
	The Satellite Phone is the Alternative Interpersonal Communication device.

Coordinate the test with the DC Tie Operator at the alternate control center. 

· Using the turret, call each programmed Satellite desk phone (RUC, RRD, REAL, RES, and TRANS) at the other control center,

· If any connection is unsuccessful, immediately open a helpdesk ticket and cc: “shiftsupv”, 

· Complete the testing form and make a log entry.

	PBX
	· Using the Cisco phone, make a call to an OPX extension

· Update the testing form and make a log entry listing the device tested, who the test call was made to, if it was successful or not, and actions taken if not successful.

	PBX

By-Pass
	· Using the PBX By-Pass phone, make a long distance call

· Update the testing form and make a log entry listing the device tested, who the test call was made to, if it was successful or not, and actions taken if not successful.

	Cell

Phone
	· Using the Control Room cell phone, make a call to the ERCOT 

Helpdesk.

· Update the testing form and make a log entry listing the device tested, who the test call was made to, if it was successful or not, and actions taken if not successful. 

	Stand

Alone

Satellite
	· Using the Standalone Satellite phone, make a call (not necessary to call a satellite number).  Refer to Desktop Guide Common to Multiple Desks section 2.7.5.

· Update the testing form and make a log entry listing the device tested, who the test call was made to, if it was successful or not, and actions taken if not successful.

	Alert Media
Test
	· Using Alert Media, activate the “SO ENS Test” scenario between the hours of 0800-2200.   

· Update the testing form and make a log entry if it was successful or not, and actions taken if not successful.

	Unsuccessful

Test
	IF:
· Any of the communication devices proved to be unsuccessful; 

THEN:

· Immediately open a helpdesk ticket and cc: “shiftsupv”, AND

· Make a log entry.

	Email
	Send the spreadsheet results by e-mail to “1 ERCOT Shift Supervisors”.

	Log
	Log all actions.  

	Alternate Control Center

	Once a 

Month
	When working out of the alternate Control Room during the monthly scheduled dates, test each Communication devices as listed in steps below.

	Testing

Form
	Complete the Monthly Communication Tests spreadsheet located on the System Operations – Control Center SharePoint site under Alternative Interpersonal Communication Testing (on left under Documents).

	Satellite Phone 
	The Satellite Phone is the Alternative Interpersonal Communication device.

Coordinate the test with the DC Tie Operator at the other control center. 

· Using the turret, call each programmed Satellite desk phone (RUC, RRD, REAL, RES, and TRANS) at the other control center,

· If any connection is unsuccessful, immediately open a helpdesk ticket and cc: “shiftsupv”, 

· Complete the testing form and make a log entry.

	PBX
	· Using the Cisco phone, make a call to an OPX extension

· Update the testing form and make a log entry listing the device tested, who the test call was made to, if it was successful or not, and actions taken if not successful.

	PBX

By-Pass
	· Using the PBX By-Pass phone, make a long distance call

· Update the testing form and make a log entry listing the device tested, who the test call was made to, if it was successful or not, and actions taken if not successful.

	Cell

Phone
	· Using the Control Room cell phone, make a call to the ERCOT Helpdesk.

· Update the testing form and make a log entry listing the device tested, who the test call was made to, if it was successful or not, and actions taken if not successful.

	Stand

Alone

Satellite
	· Using the Standalone Satellite phone, make a call (not necessary to call a satellite number).  Refer to Desktop Guide Common to Multiple Desks section 2.7.5.

· Update the testing form and make a log entry listing the device tested, who the test call was made to, if it was successful or not, and actions taken if not successful.

	Alert Media
Test
	· 
· Using Alert Media, activate the “SO ENS Test” scenario between the hours of 0800-2200.  

· Update the testing form and make a log entry if it was successful or not, and actions taken if not successful.

	Unsuccessful

Test
	IF:

· Any of the communication devices proved to be unsuccessful; 

THEN:

· Immediately open a helpdesk ticket and cc: “shiftsupv”, AND 

· Make a log entry.

	Form
	Complete the Alternative Interpersonal Communications Testing form located on the System Operations – Control Center SharePoint site

	Email


	Send the spreadsheet results by e-mail to “shiftsupv”.

	Log
	Log all actions.  


Manual Change History

	Procedure
	Ver/Rev
	Reason for Issue
	Effective Date

	All Sections
	2.0 / 0
	RTC+B Implementation

All procedures in this manual have been reviewed
	December 5, 2025

	3.6
	2.0 / 1
	Updated Log Instructions for IROLs 
	January 30, 2026

	3.2
	2.0 / 1
	Updated Non-Spin deployment trigger
	February 27, 2026

	6.1

7.2

7.3

9.3
	2.0 / 1

2.0 / 1

2.0 / 1

2.0 / 1
	Removed NXT and replaced with Alert Media
Removed NXT and replaced with Alert Media

Removed NXT and replaced with Alert Media

Removed NXT and replaced with Alert Media
	May 1, 2026


