	ERCOT Operating Procedure Manual

	Transmission and Security Desk



Power Operations Bulletin # 2029
ERCOT has posted/revised the Transmission and Security manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html
3.1
System Overview

Procedure Purpose: Review, monitor and analyze data to maintain system security.  
	Protocol Reference
	6.3.2(3)(a)(i)
	
	
	

	Guide Reference
	
	
	
	

	NERC Standard


	IRO-002-7 R5
	NUC-001-4

R4, R4.1, R4.2, R9, R9.2, R9.2.1, R9.2.2, R9.4, R9.4.1, R9.4.2
	TOP-001-6

R10, R10.1, R10.2, R10.4, R10.5, R10.6
	VAR-001-5

R2


	Version: 2 
	Revision: 1
	Effective Date: May 30, 2026


	Step
	Action

	Review
	REVIEW each of the following as necessary to confirm system reliability status:

· Alarms

· State Estimator (SE)

· Real Time Contingency Analysis (RTCA)

· Transmission Constraint Manager (TCM)

· Approved and Forced Outages

· Load Forecast

· Voltage and Transient Stability Limits

· Real Time Monitoring (RTMONI)

· Security Constrained Economic Dispatch (SCED)

· Real Time Reserve Monitoring

	Gap

Study
	Run a gap study for the next day’s peak hour to ensure all contingencies can be solved.  If necessary:

· Request the Operations Support Engineer to review results and create CMPs as needed  

· Coordinate with TOs 

· If both CPSES units are offline, the Auxiliary load will need to be manually adjusted to 45 MW at both units

· Refer to Desktop Guide Transmission Desk Section 2.5 Conducting Future Security Analysis

· Save study

· Log the following:

· Study name

· Any issues that could not be resolved and actions taken.



	STP

Lines
	A minimum of two transmission lines should be always in service.  The in-service lines should be from at least two of the groups in the table below: 

Independent Groups of STP Transmission Lines

Group 1

Group 2

Group 3

STP to Elm Creek 18 (STPELM18)

STP to Jones Creek 18 (JCKSTP18)

STP to New Hickory 27 and New Hickory to Elm Creek 27 (NHKSTP27 is G6_STP27 and ELMNHK27 is E5_G6)
STP to Refuge 27 and Refuge to Jones Creek 27 (REFSTP27 and JCKREF27)

STP to W.A. Parish 39 (STPWAP39)

Note: Group 1 – STP - Static (STATIC_STP1) to Static - Angstrom (ANGSTR_STATIC1), and Angstrom - White Point (ANGSTR_WHITE_1) are not included in this table because these circuits are currently not part of STP’s credited offsite sources.
Transmission lines, STP – Blessing 44 (BLESSING), STP – HILLJE 64 (HLJSTP64), and STP – HILLJE 44 (CKT_3124) (EMS naming convention) are not included in this table because these circuits are not part of STP’s credited offsite sources.

IF:

· A minimum of two lines are not in service; 

THEN:

· Notify the Nuclear Plant’s QSE.

· Explain the event, and an estimate of when expected to return to normal

	Dynamic

Transmission

Limits
	IF:

· Any changes in the system that could affect the security and dynamic transmission limits;

THEN:

· Post message on the ERCOT Website.


Document Control

Manual Change History

	Procedure
	Ver/

Rev
	Reason for Issue
	Effective Date

	All Sections
	2.0 / 0
	RTC+B Implementation 

All procedures in this manual have been reviewed
	December 5, 2025

	4.5
	2.0 / 1
	Updated KINNEY GTC with TSAT steps
	January 1, 2026

	Table of Contents

4.1

4.5


	2.0 / 1

2.0 / 2
	Removed Red Tap Stability and Bearkat Stability from the Table of Contents;

Add monitoring language before changing % rating in TCM;

Updated RV_RH, CULBSN, HMLTN, & KINNEY GTC’s with TSAT steps;
	January 30, 2026

	4.1
	2.0 / 2
	Updated Removal of A/S actions 
	February 27, 2026

	4.1
	2.0 / 3
	Updated navigation to SOL Exceedances

Quick Start Generation Resources
	April 1, 2026

	4.3

4.4

11.1

11.2
	2.0 / 1

2.0 / 1

2.0 / 1

2.0 / 1
	Removed NXT and replaced with Alert Media

Removed NXT and replaced with Alert Media

Removed NXT and replaced with Alert Media

Removed NXT and replaced with Alert Media
	May 1, 2026

	3.1
	2.0 / 1
	Updated STP Lines
	May 30, 2026


