	ERCOT Operating Procedure Manual

	Real Time Desk



Power Operations Bulletin # 2031
ERCOT has posted/revised the Real Time manual.

The Various Changes are shown below.
A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html
4.1
Managing SCED

Procedure Purpose: To ensure that a SCED solution has solved, and that the solution is reasonable.  
	Protocol Reference
	3.8.3
	3.9.1(10)
	3.10.7.5.1(5)
	8.1.1.2(16)

	Guide Reference
	7.3.3
	
	
	

	NERC Standard
	TOP-003-5

R5, R5.2
	TOP-010-1(i) 

R1, R1.3, R2, R2.3
	
	


	Version: 2 
	Revision: 3
	Effective Date: July 1, 2026


	Step
	Action

	Workflow Controller Messages

	Note
	The SCED Workflow Controller provides three color coded messages as indicated in the following:

· GREEN – Informational (i) and Success (s)

· BLUE – Warning (w)

· RED – Error (e) and Fatal Error (f)

	1
	REVIEW REFERENCE DISPLAY:

Market Operation>Real-Time Market>SCED Displays>Workflow>SCED Workflow Messages

Monitor SCED Workflow Controller logs for “Warning” and “Error” messages.

	2
	IF:

· The log indicates an “Error” or “Fatal Error”;

THEN:

· Contact the Service Desk and notify the Control Room staff,

· Attempt to resolve the issue, refer to Desktop Guide Real Time Desk Section 2.5,

· Refer to Section 3.3 “Managing SCED Failures” in this procedure.

	SCED Solution Time Parameter 

	Note
	Typically, SCED should produce a solution within 20 seconds.  It is highly desirable to have at least 3 executions of SCED in any 15-minute period.

	Automatic

Trigger
	Verify that SCED is automatically triggered:

· Periodically every 5 minutes

· After frequency has declined below 59.91 Hz or has risen above 60.09 Hz

· About 60 seconds after Fast Responding Synchronous Condenser Resources providing ONSC-ECRS or ONSC-RRS and SCED dispatchable resources providing RRS-FFR have been deployed automatically or manually

· Frequency is < 59.955 Hz or > 60.045 Hz for more than 60 seconds

IF:

· SCED is not automatically executed (but has not failed);

THEN:

· Manually execute SCED,

· Immediately notify the Shift Supervisor and Operations Support Engineer,

· Continue to manually execute SCED approximately every 5 minutes until the condition is corrected.

	Manual

Trigger
	SCED may be manually triggered when the following is identified:

· Frequency deviates  +/-0.05 Hz for more than 5 minutes

· Generation Resource trips and Frequency is > 59.91 Hz

· Load tripped and Frequency is < 60.09 Hz

· When approximately 50% of Regulation has been deployed

· Approximately 60 seconds after Fast Responding Resources providing ONSC-ECRS or ONSC-RRS and SCED dispatchable resources providing RRS-FFR have been deployed.

· After Load Resources providing ECRS or RRS have been deployed.

· As needed to recover frequency

	Log
	Log all actions.

	Quick Start Generation Resource

	QSGR
	A Generation Resource that in its cold-temperature state can come On-Line within ten minutes of receiving ERCOT notice and has passed an ERCOT Quick Start Generation Resource test that establishes an amount of capacity that can be deployed within a ten-minute period.  

· These Resources can be viewed in EMS: Generation Area Status > Analyst Displays > Quick Start Units

	COP
	The QSE for a QSGR that is available for deployment by SCED and awarding of ECRS and Non-Spin, if qualified and capable, shall set the COP Resource Status OFFQS, the COP LSL and HSL values to the expected sustainable LSL and HSL for the QSGR for the hour.  

	Telemeter
	The QSGR that is available to be released by SCED and awarded ECRS and Non-Spin, if qualified and capable, shall telemeter a Resource Status of OFFQS and an LSL of zero prior to receiving a release instruction from SCED.  This status is necessary for SCED to recognize that the Resource can be Dispatched and/or awarded ECRS and Non-Spin.  The status of the breaker shall be open, and the output of the Resource shall be zero in order for the State Estimator to correctly assess the state of the system.  After being released for energy by SCED, the Resource shall telemeter an LSL equal to or less than the Resource’s actual output until the Resource has Ramped to its physical LSL.  A QSGR with a telemeter breaker status of open and a telemeter Resource Status of OFFQS shall not provide Regulation or Responsive Reserve Service.

	QSGR

Decommitment
	Please refer to Desktop Guide Common to Multiple Desks for the QSGR decommitment process.

	QSGR

Qualification

Test
	WHEN:

· Conducting a QSGR qualification test for Operations Analysis;

THEN:

· Issue a VDI confirmation

· Choose “OTHER_RES” as the Instruction Type from Resource level

· Enter MW amount that the QSE is requesting to qualify its QSGR to provide.  

· Enter “QSGR Qualification Test” in “Other Information”

· . 

When issuing a VDI or the confirmation ensure the use of three-part communication:

· Issue the Operating Instruction

· Receive a correct repeat back

·  Give an acknowledgement

	Generation Resource Shut-down/Start-up Process

	Shutdown/

Startup
	Shut-down:

· A QSE representing a Generation Resource that is not actively providing A/S (except for Off-line Non-Spin) may only use a Resource Status of SHUTDOWN through telemetry that the Resource is operating in a shutdown sequence requiring manual control and is not available for Dispatch.

Start-up:

· A QSE representing a Generation Resource that is not actively providing A/S may only use a Resource Status of STARTUP through telemetry that the Resource is operating in a start-up sequence requiring manual control and is not available for Dispatch.

	Note
	QSEs can manage basepoint deviations by adjusting their telemetered Ramp Rate.

	Note
	When a Resource is carrying “Off-Line” Non-spin and that Non-Spin is being recalled, the QSE would continue to show the Non-Spin responsibility on the Resource that is shutting down.

	Combine Cycle Generation Resources

	Note
	WHEN:

· Combine Cycle Generation Resources are changing configuration creating basepoint deviations

THEN:
· QSEs will need to manage their telemetered HSL for proper basepoints.

	Real-Time Data Issues known by the QSE

	Note
	Manually replaced telemetry data is data entered by a QSE on their systems that is transmitted to ERCOT via ICCP in place of the normal points experiencing an issue.  If Reliability issues can’t be resolved in a timely manner, ERCOT reserves the right to order the Resource off-line until the problem is resolved.   

	Notification of Telemetry 

Data

Issue
	IF:

· Notified of a telemetry data issue (telemetry data will not be available or is unreliable for operational purposes;

THEN:
· The QSE should correct of the telemetry data as soon as practicable, or,

· Manually replace the data, if available.

	Cannot

Resolve
	IF:

· The QSE cannot resolve the telemetry data issue within two Business Day, fix the issue in a timely manner;

THEN:

· The QSE shall provide an estimated time of resolution.


Document Control

Manual Change History

	Procedure
	Ver/Rev
	Reason for Issue
	Effective Date

	All Sections
	2.0 / 0
	RTC+B Implementation 

All procedures in this manual have been reviewed
	December 5, 2025

	3.5
	2.0 / 1
	Adjusted formatting
	January 30, 2026

	3.1

4.1
	2.0 / 1

2.0 / 1
	Updated Base Points to Set Points

Updated navigation to QSRG
	April 1, 2026

	3.5

4.1
	2.0 / 2

2.0 / 2
	Updated Non-Spin Trigger to SOC Aware Trigger

Updated SCED Triggers
	May 30, 2026

	4.1
	2.0 / 3
	Updated wording on SCED Triggers
	July 1, 2026


PAGE  

